## 1. Overview
TR1 — Where does the PV energy go?
Prosumers vs. pure customers — every kWh traced from the raw model inputs
Purpose
This workbook accounts for every kWh of PV generated on transformer TR1 over one representative day, and it is fully auditable: nothing is hand-typed except the raw model outputs. Follow the data chain below — each step is a live formula, so changing any raw number updates everything.
The data chain (how each number is built)
Sheet 3 · Raw PV per load | The PV profile of every connection, 48 half-hours. Copied verbatim from TR1_load_PV_48periods.xlsx (sheet PV_generation_kW). Customers = 0.
Sheet 4 · Raw load per load | The load profile of every connection, 48 half-hours, tagged prosumer / customer. Copied from TR1_load_PV_48periods.xlsx (sheet Load_P_kW).
Sheet 5 · Raw batt charge | Charging power of every battery, 48 half-hours. Copied from the rolling dispatch TR1_analysis_data.xlsx (sheet Charge_kW).
Sheet 6 · Raw batt discharge | Discharging power of every battery. Copied from the same run (Discharge_kW).
Sheet 7 · PV allocation | Per half-hour: the five blue inputs are AGGREGATED from sheets 3–6 by SUM / SUMIF; the amber columns then split the PV by the priority rule.
Sheets 1 & 8 · Results | Daily totals (Σ×0.5 h) and shares. Every headline cell links to sheet 7.
The aggregation formulas (sheet 7, per half-hour)
PV (all)
prosumer load
customer load
battery charge
battery discharge
Headline results (all linked live to sheet 7)
Quantity | Value | Unit
Prosumers (PV + battery) | 77 | connections
Pure customers (load only) | 55 | connections
PV generated | 1796.988 | kWh/day
PV → prosumers' own load (direct) | 357.8252 | kWh/day
PV → battery storage | 258.7837 | kWh/day
PV → customers | 193.7687 | kWh/day
PV → export to grid | 986.6104 | kWh/day
PV share reaching customers | 10.78% | % of PV
Customer load covered by PV | 53.78% | % of customer load
Customer load covered by grid | 46.22% | % of customer load
Colour key & provenance
• LIGHT-BLUE cell = data belonging to a prosumer (its rooftop PV, load, or battery). WHITE = a pure customer (load only). On sheet 7: VIOLET = value aggregated live from the raw sheets (SUM/SUMIF); AMBER = allocation formula; GREEN = daily total (Σ × 0.5 h).
• Per-load PV & load profiles: results/tables/TR1_load_PV_48periods.xlsx (built from OpData.xls).
• Per-battery charge/discharge: TR1_analysis/01_DAILY_ROLLING_DISPATCH/TR1_analysis_data.xlsx (exact-QCP rolling dispatch, RunFOR_Rolling, CPLEX).
• Load classification (PV size > 0 = prosumer): sheet 'Customers' of the load/PV workbook.
• Method note: priority energy allocation per half-hour; downstream network + battery round-trip losses (~3–4% of PV) are not separated out in the per-period disposition.

## 2. Load classification
TR1 load classification — 132 connections
77 prosumers (PV + battery) · 55 pure customers (load only)
ID | Load name | Bus | Phase | PV size (kW) | Type
1 | Load_TR1_F1_1 | TR1_one38 | 2 | 0 | customer
2 | Load_TR1_F1_10 | TR1_one195 | 3 | 0 | customer
4 | Load_TR1_F1_12 | TR1_one235 | 1 | 0 | customer
5 | Load_TR1_F1_13 | TR1_one242 | 2 | 0 | customer
6 | Load_TR1_F1_14 | TR1_one252 | 3 | 0 | customer
7 | Load_TR1_F1_15 | TR1_one260 | 3 | 0 | customer
8 | Load_TR1_F1_16 | TR1_one280 | 1 | 0 | customer
9 | Load_TR1_F1_17 | TR1_one287 | 2 | 0 | customer
10 | Load_TR1_F1_18 | TR1_one299 | 2 | 0 | customer
12 | Load_TR1_F1_2 | TR1_one42 | 2 | 0 | customer
15 | Load_TR1_F1_22 | TR1_one328 | 1 | 0 | customer
16 | Load_TR1_F1_23 | TR1_one345 | 1 | 0 | customer
18 | Load_TR1_F1_25 | TR1_one363 | 3 | 0 | customer
20 | Load_TR1_F1_27 | TR1_one371 | 3 | 0 | customer
24 | Load_TR1_F1_30 | TR1_one416 | 3 | 0 | customer
26 | Load_TR1_F1_32 | TR1_one446 | 2 | 0 | customer
28 | Load_TR1_F1_34 | TR1_one477 | 1 | 0 | customer
39 | Load_TR1_F1_44 | TR1_one570 | 2 | 0 | customer
40 | Load_TR1_F1_45 | TR1_one585 | 1 | 0 | customer
41 | Load_TR1_F1_46 | TR1_one590 | 1 | 0 | customer
43 | Load_TR1_F1_48 | TR1_one614 | 2 | 0 | customer
47 | Load_TR1_F1_7 | TR1_one133 | 1 | 0 | customer
48 | Load_TR1_F1_8 | TR1_one137 | 1 | 0 | customer
49 | Load_TR1_F1_9 | TR1_one176 | 1 | 0 | customer
55 | Load_TR1_F6_14 | TR1_six203 | 1 | 0 | customer
56 | Load_TR1_F6_15 | TR1_six232 | 3 | 0 | customer
57 | Load_TR1_F6_16 | TR1_six238 | 1 | 0 | customer
69 | Load_TR1_F6_27 | TR1_six362 | 3 | 0 | customer
70 | Load_TR1_F6_28 | TR1_six365 | 3 | 0 | customer
75 | Load_TR1_F6_32 | TR1_six392 | 3 | 0 | customer
83 | Load_TR1_F6_4 | TR1_six82 | 1 | 0 | customer
84 | Load_TR1_F6_40 | TR1_six523 | 3 | 0 | customer
85 | Load_TR1_F6_41 | TR1_six534 | 2 | 0 | customer
86 | Load_TR1_F6_42 | TR1_six571 | 3 | 0 | customer
87 | Load_TR1_F6_43 | TR1_six583 | 1 | 0 | customer
88 | Load_TR1_F6_44 | TR1_six591 | 3 | 0 | customer
90 | Load_TR1_F6_46 | TR1_six625 | 1 | 0 | customer
91 | Load_TR1_F6_47 | TR1_six643 | 1 | 0 | customer
93 | Load_TR1_F6_49 | TR1_six651 | 3 | 0 | customer
94 | Load_TR1_F6_5 | TR1_six87 | 1 | 0 | customer
95 | Load_TR1_F6_50 | TR1_six652 | 1 | 0 | customer
96 | Load_TR1_F6_51 | TR1_six665 | 2 | 0 | customer
97 | Load_TR1_F6_52 | TR1_six667 | 1 | 0 | customer
102 | Load_TR1_F6_57 | TR1_six740 | 1 | 0 | customer
103 | Load_TR1_F6_58 | TR1_six758 | 2 | 0 | customer
106 | Load_TR1_F6_60 | TR1_six799 | 2 | 0 | customer
107 | Load_TR1_F6_61 | TR1_six801 | 3 | 0 | customer
109 | Load_TR1_F6_63 | TR1_six844 | 3 | 0 | customer
114 | Load_TR1_F6_68 | TR1_six894 | 2 | 0 | customer
118 | Load_TR1_F6_71 | TR1_six921 | 2 | 0 | customer
119 | Load_TR1_F6_72 | TR1_six929 | 1 | 0 | customer
120 | Load_TR1_F6_73 | TR1_six938 | 1 | 0 | customer
124 | Load_TR1_F6_77 | TR1_six974 | 3 | 0 | customer
125 | Load_TR1_F6_78 | TR1_six979 | 1 | 0 | customer
127 | Load_TR1_F6_8 | TR1_six111 | 3 | 0 | customer
3 | Load_TR1_F1_11 | TR1_one223 | 2 | 4 | prosumer
11 | Load_TR1_F1_19 | TR1_one313 | 1 | 4 | prosumer
13 | Load_TR1_F1_20 | TR1_one320 | 2 | 2 | prosumer
14 | Load_TR1_F1_21 | TR1_one321 | 3 | 4 | prosumer
17 | Load_TR1_F1_24 | TR1_one346 | 3 | 3 | prosumer
19 | Load_TR1_F1_26 | TR1_one366 | 2 | 2 | prosumer
21 | Load_TR1_F1_28 | TR1_one375 | 3 | 2.5 | prosumer
22 | Load_TR1_F1_29 | TR1_one410 | 2 | 2.5 | prosumer
23 | Load_TR1_F1_3 | TR1_one50 | 1 | 2 | prosumer
25 | Load_TR1_F1_31 | TR1_one423 | 2 | 2 | prosumer
27 | Load_TR1_F1_33 | TR1_one469 | 1 | 3 | prosumer
29 | Load_TR1_F1_35 | TR1_one480 | 1 | 2 | prosumer
30 | Load_TR1_F1_36 | TR1_one482 | 2 | 4 | prosumer
31 | Load_TR1_F1_37 | TR1_one521 | 3 | 2.5 | prosumer
32 | Load_TR1_F1_38 | TR1_one528 | 3 | 2.5 | prosumer
33 | Load_TR1_F1_39 | TR1_one537 | 1 | 2.5 | prosumer
34 | Load_TR1_F1_4 | TR1_one61 | 1 | 4 | prosumer
35 | Load_TR1_F1_40 | TR1_one544 | 1 | 4 | prosumer
36 | Load_TR1_F1_41 | TR1_one552 | 2 | 3.5 | prosumer
37 | Load_TR1_F1_42 | TR1_one559 | 3 | 2 | prosumer
38 | Load_TR1_F1_43 | TR1_one560 | 3 | 4 | prosumer
42 | Load_TR1_F1_47 | TR1_one605 | 1 | 2.5 | prosumer
44 | Load_TR1_F1_49 | TR1_one617 | 1 | 3 | prosumer
45 | Load_TR1_F1_5 | TR1_one73 | 1 | 3 | prosumer
46 | Load_TR1_F1_6 | TR1_one76 | 1 | 3.5 | prosumer
50 | Load_TR1_F6_1 | TR1_six64 | 1 | 2.5 | prosumer
51 | Load_TR1_F6_10 | TR1_six154 | 3 | 4 | prosumer
52 | Load_TR1_F6_11 | TR1_six173 | 3 | 4 | prosumer
53 | Load_TR1_F6_12 | TR1_six186 | 1 | 2 | prosumer
54 | Load_TR1_F6_13 | TR1_six191 | 2 | 4 | prosumer
58 | Load_TR1_F6_17 | TR1_six249 | 2 | 4 | prosumer
59 | Load_TR1_F6_18 | TR1_six254 | 2 | 2 | prosumer
60 | Load_TR1_F6_19 | TR1_six269 | 3 | 3 | prosumer
61 | Load_TR1_F6_2 | TR1_six68 | 3 | 1.5 | prosumer
62 | Load_TR1_F6_20 | TR1_six289 | 3 | 2 | prosumer
63 | Load_TR1_F6_21 | TR1_six317 | 3 | 2.5 | prosumer
64 | Load_TR1_F6_22 | TR1_six326 | 1 | 2.5 | prosumer
65 | Load_TR1_F6_23 | TR1_six329 | 1 | 2.5 | prosumer
66 | Load_TR1_F6_24 | TR1_six342 | 1 | 3 | prosumer
67 | Load_TR1_F6_25 | TR1_six349 | 1 | 2.5 | prosumer
68 | Load_TR1_F6_26 | TR1_six350 | 2 | 4 | prosumer
71 | Load_TR1_F6_29 | TR1_six378 | 1 | 4 | prosumer
72 | Load_TR1_F6_3 | TR1_six75 | 1 | 3 | prosumer
73 | Load_TR1_F6_30 | TR1_six385 | 2 | 1.5 | prosumer
74 | Load_TR1_F6_31 | TR1_six387 | 1 | 1.5 | prosumer
76 | Load_TR1_F6_33 | TR1_six410 | 1 | 2 | prosumer
77 | Load_TR1_F6_34 | TR1_six431 | 3 | 2.5 | prosumer
78 | Load_TR1_F6_35 | TR1_six441 | 1 | 4 | prosumer
79 | Load_TR1_F6_36 | TR1_six484 | 2 | 3 | prosumer
80 | Load_TR1_F6_37 | TR1_six501 | 1 | 3 | prosumer
81 | Load_TR1_F6_38 | TR1_six512 | 2 | 3.5 | prosumer
82 | Load_TR1_F6_39 | TR1_six518 | 2 | 4 | prosumer
89 | Load_TR1_F6_45 | TR1_six595 | 2 | 2.5 | prosumer
92 | Load_TR1_F6_48 | TR1_six646 | 2 | 2.5 | prosumer
98 | Load_TR1_F6_53 | TR1_six699 | 3 | 3.5 | prosumer
99 | Load_TR1_F6_54 | TR1_six718 | 3 | 1.5 | prosumer
100 | Load_TR1_F6_55 | TR1_six721 | 1 | 1.5 | prosumer
101 | Load_TR1_F6_56 | TR1_six723 | 2 | 4 | prosumer
104 | Load_TR1_F6_59 | TR1_six784 | 2 | 3 | prosumer
105 | Load_TR1_F6_6 | TR1_six90 | 2 | 2 | prosumer
108 | Load_TR1_F6_62 | TR1_six807 | 1 | 2 | prosumer
110 | Load_TR1_F6_64 | TR1_six852 | 2 | 4 | prosumer
111 | Load_TR1_F6_65 | TR1_six860 | 3 | 4 | prosumer
112 | Load_TR1_F6_66 | TR1_six869 | 3 | 4 | prosumer
113 | Load_TR1_F6_67 | TR1_six885 | 1 | 2 | prosumer
115 | Load_TR1_F6_69 | TR1_six909 | 3 | 2.5 | prosumer
116 | Load_TR1_F6_7 | TR1_six105 | 1 | 2.5 | prosumer
117 | Load_TR1_F6_70 | TR1_six914 | 1 | 3.5 | prosumer
121 | Load_TR1_F6_74 | TR1_six945 | 3 | 4 | prosumer
122 | Load_TR1_F6_75 | TR1_six952 | 1 | 2 | prosumer
123 | Load_TR1_F6_76 | TR1_six967 | 2 | 1 | prosumer
126 | Load_TR1_F6_79 | TR1_six990 | 2 | 4 | prosumer
128 | Load_TR1_F6_80 | TR1_six1006 | 3 | 3.5 | prosumer
129 | Load_TR1_F6_81 | TR1_six1020 | 1 | 4 | prosumer
130 | Load_TR1_F6_82 | TR1_six1025 | 2 | 3 | prosumer
131 | Load_TR1_F6_83 | TR1_six1064 | 3 | 1 | prosumer
132 | Load_TR1_F6_9 | TR1_six128 | 2 | 3 | prosumer

## 3. Raw PV per load
Raw PV per load
Verbatim copy of PV_generation_kW (TR1_load_PV_48periods.xlsx). One row per connection, 48 half-hours (kW).
Load name | Type | p1 | p2 | p3 | p4 | p5 | p6 | p7 | p8 | p9 | p10 | p11 | p12 | p13 | p14 | p15 | p16 | p17 | p18 | p19 | p20 | p21 | p22 | p23 | p24 | p25 | p26 | p27 | p28 | p29 | p30 | p31 | p32 | p33 | p34 | p35 | p36 | p37 | p38 | p39 | p40 | p41 | p42 | p43 | p44 | p45 | p46 | p47 | p48
Load_TR1_F1_1 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_10 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_11 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_12 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_13 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_14 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_15 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_16 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_17 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_18 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_19 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_2 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_20 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_21 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_22 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_23 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_24 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_25 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_26 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_27 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_28 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_29 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_3 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_30 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_31 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_32 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_33 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_34 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_35 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_36 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_37 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_38 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_39 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_4 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_40 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_41 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_42 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_43 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_44 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_45 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_46 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_47 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_48 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_49 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_5 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_6 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_7 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_8 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F1_9 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_1 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_10 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_11 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_12 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_13 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_14 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_15 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_16 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_17 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_18 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_19 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_2 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_20 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_21 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_22 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_23 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_24 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_25 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_26 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_27 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_28 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_29 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_3 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_30 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_31 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_32 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_33 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_34 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_35 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_36 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_37 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_38 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_39 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_4 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_40 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_41 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_42 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_43 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_44 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_45 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_46 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_47 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_48 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_49 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_5 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_50 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_51 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_52 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_53 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_54 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_55 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_56 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_57 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_58 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_59 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_6 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_60 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_61 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_62 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_63 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_64 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_65 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_66 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_67 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_68 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_69 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_7 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_70 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_71 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_72 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_73 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_74 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_75 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_76 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0009 | 0.0124 | 0.0581 | 0.1153 | 0.1855 | 0.262 | 0.3394 | 0.4165 | 0.4937 | 0.5661 | 0.6342 | 0.6921 | 0.7416 | 0.785 | 0.8208 | 0.8462 | 0.8574 | 0.8606 | 0.8546 | 0.8343 | 0.8033 | 0.7664 | 0.7195 | 0.6698 | 0.6099 | 0.5425 | 0.461 | 0.3848 | 0.3065 | 0.2307 | 0.1577 | 0.0921 | 0.0268 | 0.0049 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_77 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_78 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_79 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_8 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_80 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_81 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_82 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_83 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0009 | 0.0124 | 0.0581 | 0.1153 | 0.1855 | 0.262 | 0.3394 | 0.4165 | 0.4937 | 0.5661 | 0.6342 | 0.6921 | 0.7416 | 0.785 | 0.8208 | 0.8462 | 0.8574 | 0.8606 | 0.8546 | 0.8343 | 0.8033 | 0.7664 | 0.7195 | 0.6698 | 0.6099 | 0.5425 | 0.461 | 0.3848 | 0.3065 | 0.2307 | 0.1577 | 0.0921 | 0.0268 | 0.0049 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR1_F6_9 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 4. Raw load per load
Raw load per load
Verbatim copy of Load_P_kW (TR1_load_PV_48periods.xlsx), tagged by type. One row per connection, 48 half-hours (kW).
Load name | Type | p1 | p2 | p3 | p4 | p5 | p6 | p7 | p8 | p9 | p10 | p11 | p12 | p13 | p14 | p15 | p16 | p17 | p18 | p19 | p20 | p21 | p22 | p23 | p24 | p25 | p26 | p27 | p28 | p29 | p30 | p31 | p32 | p33 | p34 | p35 | p36 | p37 | p38 | p39 | p40 | p41 | p42 | p43 | p44 | p45 | p46 | p47 | p48
Load_TR1_F1_1 | customer | 0.1728 | 0.1488 | 0.1515 | 0.2622 | 0.1579 | 0.1852 | 0.1683 | 0.053 | 0.1215 | 0.1709 | 0.1807 | 0.1728 | 0.2473 | 0.053 | 0.3006 | 0.3354 | 1.2371 | 0.3016 | 0.3932 | 0.3972 | 0.3368 | 1.0621 | 0.6625 | 0.3886 | 0.0929 | 0.232 | 0.1743 | 0.3792 | 0.1691 | 0.3555 | 0.1618 | 0.2703 | 0.3229 | 0.2858 | 0.3273 | 0.1983 | 1.6876 | 0.2883 | 0.2392 | 0.7353 | 1.6555 | 2.2482 | 0.915 | 0.6569 | 1.542 | 0.7453 | 0.6293 | 0.6921
Load_TR1_F1_10 | customer | 0.2614 | 0.1504 | 0.0916 | 0.3191 | 0.0588 | 0.347 | 0.0685 | 0.2293 | 0.1861 | 0.124 | 0.2538 | 0.1279 | 0.1937 | 0.1854 | 0.2156 | 1.0153 | 0.3903 | 0.146 | 0.1504 | 0.054 | 0.1675 | 0.2953 | 0.1856 | 0.4612 | 0.119 | 0.1229 | 0.3951 | 0.054 | 0.2549 | 0.5166 | 0.6905 | 0.3861 | 0.7 | 0.6783 | 1.6196 | 4.291 | 2.5453 | 0.1406 | 0.4521 | 0.7723 | 0.5788 | 1.4949 | 0.5698 | 0.2831 | 0.1677 | 0.0948 | 0.3207 | 0.054
Load_TR1_F1_11 | prosumer | 0.1833 | 0.2404 | 0.1517 | 0.223 | 0.1409 | 0.1484 | 0.2789 | 0.046 | 0.1445 | 0.2129 | 0.0693 | 0.2821 | 0.1218 | 0.1522 | 0.2674 | 0.3476 | 0.4452 | 1.1229 | 0.3797 | 0.3114 | 0.4319 | 1.1413 | 0.4484 | 0.0771 | 0.2982 | 0.098 | 0.0536 | 0.3154 | 0.1042 | 0.1311 | 0.2961 | 0.046 | 0.4704 | 0.1786 | 0.1123 | 0.249 | 0.2829 | 0.1967 | 0.2577 | 0.4576 | 1.0054 | 0.7273 | 0.9693 | 0.5957 | 1.725 | 0.708 | 0.5263 | 0.5321
Load_TR1_F1_12 | customer | 0.1863 | 0.1472 | 0.1732 | 0.2747 | 0.052 | 0.0857 | 0.2497 | 0.0877 | 0.2684 | 0.1795 | 0.1597 | 0.1607 | 0.1795 | 0.2257 | 0.1568 | 0.1444 | 0.25 | 0.052 | 0.2001 | 0.0639 | 0.3198 | 0.1162 | 0.171 | 0.1866 | 0.1785 | 0.058 | 0.266 | 0.1819 | 0.052 | 0.3959 | 1.2573 | 0.6164 | 0.9556 | 1.5565 | 1.9744 | 1.5019 | 0.437 | 0.2018 | 0.1848 | 0.2093 | 0.1866 | 0.1966 | 0.2513 | 0.0904 | 0.2094 | 0.2262 | 0.1027 | 0.0563
Load_TR1_F1_13 | customer | 0.6131 | 0.2 | 0.047 | 0.2566 | 0.0612 | 0.115 | 0.047 | 0.1717 | 0.1461 | 0.1075 | 0.1395 | 0.1858 | 0.047 | 0.1929 | 0.1249 | 0.047 | 0.2304 | 0.3872 | 0.2434 | 0.2359 | 0.3124 | 0.2529 | 0.1873 | 0.1787 | 0.0966 | 0.2446 | 1.2986 | 0.2547 | 0.1046 | 0.2979 | 0.2664 | 0.047 | 0.1292 | 0.1886 | 0.0699 | 0.121 | 0.0651 | 0.349 | 0.1189 | 0.3787 | 0.2406 | 0.6588 | 0.3029 | 0.3207 | 0.1461 | 0.047 | 0.1075 | 0.0546
Load_TR1_F1_14 | customer | 0.0727 | 0.1196 | 0.0915 | 0.1683 | 0.1515 | 0.1383 | 0.204 | 0.1346 | 0.1702 | 0.1215 | 0.1065 | 0.1665 | 0.054 | 0.2115 | 0.0615 | 0.0727 | 0.2958 | 0.4877 | 0.2519 | 0.2744 | 0.3749 | 1.6141 | 0.3934 | 0.5864 | 1.4142 | 0.8744 | 0.4191 | 0.3119 | 0.2326 | 0.3471 | 0.1149 | 0.2377 | 0.2125 | 0.2375 | 0.19 | 0.1365 | 0.1149 | 0.2124 | 0.8871 | 0.4017 | 0.4929 | 0.4979 | 0.5161 | 0.4558 | 0.7765 | 2.1796 | 0.4599 | 0.1324
Load_TR1_F1_15 | customer | 0.1648 | 0.0568 | 0.026 | 0.2317 | 0.0672 | 0.026 | 0.026 | 0.2343 | 0.0646 | 0.026 | 0.026 | 0.1879 | 0.111 | 0.1262 | 0.4975 | 0.146 | 0.6465 | 0.5299 | 0.5584 | 0.7484 | 0.5453 | 0.4157 | 0.234 | 0.3272 | 0.2128 | 0.3512 | 1.7433 | 1.2534 | 0.1956 | 0.026 | 0.1872 | 0.1117 | 0.099 | 0.1999 | 0.026 | 0.122 | 0.1769 | 0.0475 | 0.2514 | 0.0732 | 0.056 | 0.2437 | 0.1697 | 0.2222 | 1.3685 | 0.6312 | 0.4549 | 0.142
Load_TR1_F1_16 | customer | 0.2336 | 0.1361 | 0.059 | 0.2004 | 0.059 | 0.1104 | 0.149 | 0.059 | 0.2004 | 0.059 | 0.1875 | 0.0719 | 0.059 | 0.059 | 0.2443 | 0.2996 | 0.2433 | 0.3589 | 0.2322 | 0.2923 | 0.9015 | 0.5465 | 0.1683 | 0.0911 | 0.1297 | 0.1297 | 0.059 | 0.059 | 0.2329 | 0.2898 | 0.0738 | 0.3493 | 0.3378 | 0.1805 | 0.2218 | 0.4635 | 0.4438 | 1.4101 | 0.5824 | 0.6825 | 0.4531 | 0.3283 | 0.6732 | 0.9685 | 0.1757 | 0.3037 | 0.0847 | 0.1747
Load_TR1_F1_17 | customer | 0.1091 | 0.1519 | 0.052 | 0.209 | 0.052 | 0.052 | 0.052 | 0.2019 | 0.0591 | 0.1519 | 0.1091 | 0.1091 | 0.1519 | 0.052 | 0.2068 | 0.3638 | 0.2762 | 0.1131 | 0.455 | 0.0882 | 0.2776 | 1.0528 | 1.5006 | 0.2141 | 0.4982 | 0.0597 | 0.5093 | 0.1108 | 0.2361 | 0.0892 | 0.236 | 0.0966 | 0.1608 | 0.3327 | 0.1347 | 0.3078 | 0.052 | 0.209 | 0.052 | 0.052 | 0.5694 | 0.4466 | 1.0521 | 1.1626 | 0.9625 | 0.6937 | 0.0591 | 0.2019
Load_TR1_F1_18 | customer | 0.05 | 0.2314 | 0.05 | 0.1489 | 0.1324 | 0.083 | 0.1984 | 0.05 | 0.2314 | 0.05 | 0.05 | 0.05 | 0.1902 | 0.0912 | 0.05 | 0.0747 | 0.4134 | 0.2076 | 0.2184 | 0.1162 | 0.1394 | 0.1823 | 0.2149 | 0.05 | 0.1984 | 0.083 | 0.1491 | 0.2584 | 0.4931 | 0.3075 | 0.3458 | 0.3415 | 0.3189 | 0.6418 | 0.2928 | 0.4345 | 0.2397 | 0.1353 | 0.4797 | 0.1718 | 0.3206 | 0.572 | 0.3459 | 0.6346 | 0.3421 | 0.4153 | 0.4146 | 0.5358
Load_TR1_F1_19 | prosumer | 0.0944 | 0.04 | 0.04 | 0.0944 | 0.1352 | 0.04 | 0.1897 | 0.04 | 0.1216 | 0.108 | 0.0468 | 0.1829 | 0.04 | 0.04 | 0.2704 | 0.2957 | 0.04 | 0.2431 | 0.27 | 0.2536 | 0.4267 | 0.2479 | 0.2079 | 0.4306 | 0.0902 | 0.1352 | 0.0944 | 0.074 | 0.1557 | 0.04 | 0.1625 | 0.0672 | 0.074 | 0.1557 | 0.04 | 0.04 | 0.04 | 0.1897 | 0.04 | 0.04 | 0.1897 | 0.04 | 0.04 | 0.0604 | 0.1693 | 0.04 | 0.1216 | 0.108
Load_TR1_F1_2 | customer | 0.2276 | 0.048 | 0.2272 | 0.1704 | 0.1701 | 0.2276 | 0.048 | 0.3089 | 0.0888 | 0.1133 | 0.2844 | 0.048 | 0.0643 | 0.315 | 0.0663 | 0.1906 | 0.2071 | 0.1029 | 0.2621 | 0.0807 | 2.9241 | 2.9344 | 0.4729 | 0.3192 | 0.0725 | 0.048 | 0.2276 | 0.1701 | 0.0888 | 0.1868 | 0.1701 | 0.2276 | 0.0602 | 0.3698 | 0.1464 | 0.1781 | 0.2289 | 0.1796 | 0.0863 | 0.445 | 0.586 | 0.3306 | 0.4188 | 0.696 | 0.2925 | 0.1051 | 0.048 | 0.1112
Load_TR1_F1_20 | prosumer | 0.05 | 0.1332 | 0.05 | 0.1332 | 0.05 | 0.0639 | 0.1193 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1332 | 0.05 | 0.05 | 0.0639 | 0.1193 | 0.05 | 0.05 | 0.1332 | 0.05 | 0.1332 | 0.1284 | 0.1332 | 0.05 | 0.2556 | 0.3439 | 0.516 | 0.2166 | 0.2529 | 0.1801 | 0.2704 | 0.4909 | 0.2861 | 0.1256 | 0.2225 | 0.0893 | 0.2708 | 0.2325 | 0.3736 | 1.3265 | 0.4714 | 0.5002 | 0.4069 | 0.4534 | 0.273 | 0.503 | 0.4559 | 0.311
Load_TR1_F1_21 | prosumer | 0.057 | 0.057 | 0.057 | 0.1755 | 0.057 | 0.1755 | 0.057 | 0.1636 | 0.0688 | 0.1636 | 0.0688 | 0.057 | 0.0985 | 0.134 | 0.057 | 0.0866 | 0.3122 | 0.7263 | 0.2819 | 0.3187 | 0.2665 | 0.2031 | 0.1201 | 0.2157 | 0.057 | 0.1755 | 0.1077 | 0.3644 | 0.3035 | 0.3673 | 0.3908 | 0.1453 | 0.1987 | 0.3021 | 0.057 | 0.2873 | 0.2249 | 0.0748 | 0.057 | 0.1636 | 0.0688 | 0.0925 | 0.1399 | 0.0925 | 0.1399 | 0.057 | 0.057 | 0.1399
Load_TR1_F1_22 | customer | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 1.4943 | 1.2897 | 0.0333 | 0.1516 | 0.321 | 0.3095 | 0.2275 | 0.2736 | 0.2683 | 0.1454 | 0.032 | 0.032 | 0.032 | 0.0789 | 0.032 | 0.1908 | 0.2482 | 0.0793 | 0.4764 | 0.4805 | 0.2702 | 0.3297 | 0.387 | 0.5936 | 0.1987 | 0.3812 | 0.3766 | 1.1606 | 0.4951 | 0.5389 | 0.0643 | 0.0452
Load_TR1_F1_23 | customer | 0.031 | 0.1267 | 0.0479 | 0.0816 | 0.0929 | 0.031 | 0.031 | 0.0816 | 0.0929 | 0.031 | 0.1435 | 0.031 | 0.1435 | 0.031 | 0.0985 | 0.076 | 0.031 | 0.031 | 0.1435 | 0.031 | 0.1041 | 0.0704 | 0.031 | 0.1223 | 0.0665 | 0.0873 | 0.0873 | 0.031 | 0.0929 | 0.0816 | 0.2816 | 0.185 | 0.031 | 0.1435 | 0.0395 | 0.3015 | 0.1736 | 0.1392 | 0.3241 | 0.4879 | 0.856 | 0.7266 | 0.6855 | 0.4137 | 0.1435 | 0.031 | 0.031 | 0.1435
Load_TR1_F1_24 | prosumer | 0.055 | 0.055 | 0.2143 | 0.055 | 0.1636 | 0.1057 | 0.0767 | 0.1925 | 0.055 | 0.055 | 0.055 | 0.1419 | 0.1274 | 0.0695 | 0.1998 | 0.055 | 0.1708 | 0.0984 | 0.055 | 0.055 | 0.2106 | 0.0622 | 0.055 | 0.0912 | 0.1781 | 0.055 | 0.055 | 0.1925 | 0.0767 | 0.055 | 0.055 | 0.2143 | 0.0655 | 0.207 | 0.0622 | 0.055 | 0.1636 | 0.1057 | 0.1057 | 0.1636 | 0.055 | 0.0622 | 0.207 | 0.055 | 0.2143 | 0.055 | 0.084 | 0.1853
Load_TR1_F1_25 | customer | 0.0643 | 0.1551 | 0.053 | 0.053 | 0.1664 | 0.053 | 0.104 | 0.1154 | 0.053 | 0.1664 | 0.053 | 0.1437 | 0.0757 | 0.156 | 0.9465 | 0.1374 | 0.087 | 0.0537 | 1.1198 | 0.1327 | 0.053 | 0.053 | 0.053 | 0.1381 | 0.3316 | 0.0828 | 0.1687 | 0.1296 | 0.0757 | 0.1437 | 0.053 | 0.1494 | 0.1054 | 0.0766 | 0.053 | 0.053 | 0.1505 | 0.1664 | 0.053 | 0.053 | 0.053 | 0.1267 | 0.0927 | 0.053 | 0.053 | 0.0927 | 0.1267 | 0.053
Load_TR1_F1_26 | prosumer | 0.1916 | 0.2179 | 0.0801 | 0.3056 | 0.1508 | 0.1487 | 0.3145 | 0.0946 | 0.2074 | 0.2153 | 0.054 | 0.2604 | 0.2028 | 0.1765 | 0.1379 | 0.2672 | 0.1637 | 0.2067 | 0.2951 | 0.1702 | 0.8387 | 0.2305 | 0.5731 | 0.3107 | 0.3269 | 0.5026 | 0.2903 | 0.4947 | 0.1534 | 0.3353 | 0.4569 | 0.3355 | 0.5833 | 0.4219 | 0.6359 | 0.7223 | 2.3691 | 0.4901 | 0.4187 | 0.7205 | 0.7747 | 1.2072 | 1.0811 | 0.8608 | 1.8941 | 0.7583 | 2.2278 | 0.2169
Load_TR1_F1_27 | customer | 0.1863 | 0.1271 | 0.05 | 0.1489 | 0.1043 | 0.172 | 0.1414 | 0.1102 | 0.186 | 0.1274 | 0.05 | 0.2387 | 0.0747 | 0.1167 | 0.1968 | 0.093 | 0.1091 | 0.1613 | 0.0738 | 0.6814 | 2.111 | 0.828 | 0.0586 | 0.186 | 0.1274 | 0.05 | 0.1831 | 0.6447 | 0.0751 | 0.1359 | 0.1228 | 0.1473 | 0.1489 | 0.05 | 0.2634 | 0.05 | 0.1299 | 0.388 | 0.3995 | 0.7943 | 0.7216 | 0.9126 | 0.3907 | 0.4241 | 0.4069 | 0.4719 | 0.5784 | 0.0586
Load_TR1_F1_28 | prosumer | 0.229 | 0.1078 | 0.111 | 0.2222 | 0.0749 | 0.147 | 0.1971 | 0.053 | 0.1783 | 0.1658 | 0.1 | 0.2441 | 0.053 | 0.1893 | 0.209 | 0.2233 | 0.4139 | 1.7158 | 0.2412 | 2.1624 | 0.053 | 0.1188 | 0.7776 | 1.7235 | 1.5585 | 1.6838 | 1.5139 | 0.2996 | 0.1104 | 0.1005 | 0.2018 | 0.1423 | 0.053 | 0.206 | 0.1381 | 0.1958 | 0.2714 | 0.3874 | 0.3959 | 0.7018 | 1.0668 | 0.5633 | 0.7202 | 0.5059 | 0.8987 | 0.6762 | 1.825 | 0.8563
Load_TR1_F1_29 | prosumer | 0.2562 | 0.0946 | 0.051 | 0.2998 | 0.051 | 0.1019 | 0.2489 | 0.0957 | 0.2302 | 0.1206 | 0.1492 | 0.157 | 0.3337 | 0.1627 | 0.051 | 0.1403 | 0.1606 | 0.1009 | 0.0809 | 0.7083 | 0.923 | 0.5828 | 1.402 | 0.2109 | 0.2184 | 0.0822 | 0.051 | 0.1882 | 0.1571 | 0.0566 | 0.051 | 0.1741 | 0.1767 | 0.0845 | 0.2638 | 0.3175 | 0.4132 | 0.2051 | 0.2845 | 0.051 | 0.2886 | 0.0622 | 0.1754 | 0.2769 | 0.0822 | 0.2686 | 0.051 | 0.2309
Load_TR1_F1_3 | prosumer | 0.56 | 0.5335 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.1352 | 1.1912 | 0.055 | 0.1017 | 0.2 | 0.2265 | 0.2265 | 0.2265 | 0.2265 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.2265 | 0.2265 | 0.3133 | 0.4017 | 0.4663 | 0.1461 | 0.225 | 0.4191 | 1.6851 | 0.6053 | 0.7386 | 0.7765 | 0.5454 | 0.2193 | 0.055
Load_TR1_F1_30 | customer | 0.221 | 0.05 | 0.2132 | 0.0578 | 0.0889 | 0.1821 | 0.05 | 0.221 | 0.3393 | 0.1821 | 0.0889 | 0.1277 | 0.1433 | 0.05 | 0.221 | 0.05 | 0.1433 | 0.1277 | 0.3109 | 0.339 | 0.05 | 0.2744 | 0.1912 | 0.1355 | 0.0811 | 0.4143 | 0.05 | 0.2054 | 0.0655 | 0.1122 | 0.1588 | 0.05 | 0.05 | 0.221 | 0.05 | 0.1821 | 0.0889 | 0.05 | 0.221 | 0.05 | 0.05 | 0.1199 | 0.151 | 0.05 | 0.221 | 0.05 | 0.1199 | 0.151
Load_TR1_F1_31 | prosumer | 0.3783 | 0.3821 | 0.061 | 0.2249 | 0.061 | 0.061 | 0.21 | 0.0759 | 0.061 | 0.2249 | 0.061 | 0.061 | 0.2249 | 0.061 | 0.1727 | 0.1437 | 0.061 | 0.2975 | 0.2002 | 0.4308 | 0.5055 | 0.1985 | 0.3219 | 0.5737 | 0.2965 | 0.3256 | 0.3271 | 0.2582 | 0.7951 | 1.1037 | 0.061 | 0.2249 | 0.2501 | 0.3045 | 0.2174 | 0.061 | 0.5171 | 0.3732 | 0.649 | 0.821 | 1.4332 | 0.98 | 0.6961 | 1.7437 | 0.99 | 0.6726 | 0.061 | 0.1653
Load_TR1_F1_32 | customer | 0.058 | 0.1373 | 0.0627 | 0.142 | 0.058 | 0.142 | 0.058 | 0.128 | 0.072 | 0.058 | 0.142 | 0.058 | 0.0627 | 0.1373 | 0.058 | 0.0908 | 0.142 | 0.2954 | 0.2156 | 0.0828 | 0.1999 | 0.534 | 0.0627 | 0.0641 | 0.072 | 0.1589 | 0.1227 | 0.1002 | 0.1837 | 0.1168 | 0.2441 | 0.3115 | 0.3599 | 0.3927 | 0.2807 | 0.4207 | 0.4138 | 0.2512 | 0.1233 | 0.0767 | 0.058 | 0.1233 | 0.0767 | 0.1187 | 0.4802 | 0.4405 | 0.447 | 0.5337
Load_TR1_F1_33 | prosumer | 0.4844 | 0.5063 | 0.3843 | 0.1669 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.05 | 0.217 | 0.7582 | 0.5696 | 0.1607 | 0.068 | 0.0463 | 0.046 | 0.1815 | 1.2744 | 0.0904 | 0.0759 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.0743 | 0.1226 | 0.3169 | 0.3093 | 0.4761 | 0.438 | 0.4878 | 0.4053 | 0.3227 | 0.5936 | 0.504
Load_TR1_F1_34 | customer | 0.0599 | 0.3026 | 0.1009 | 0.1257 | 0.2997 | 0.038 | 0.3011 | 0.0894 | 0.0729 | 0.2341 | 0.1913 | 0.1481 | 0.2773 | 0.0459 | 0.2792 | 0.1389 | 0.1895 | 0.2734 | 0.1974 | 0.1993 | 0.2561 | 1.2573 | 0.7009 | 0.2147 | 0.2619 | 0.2508 | 0.0404 | 0.1481 | 0.4124 | 0.483 | 0.2716 | 0.1062 | 0.4256 | 0.359 | 0.3033 | 0.3018 | 0.2261 | 0.4661 | 0.5064 | 0.5268 | 0.0903 | 0.1742 | 0.1623 | 0.0746 | 0.2007 | 0.5902 | 0.0511 | 0.3114
Load_TR1_F1_35 | prosumer | 0.3531 | 0.5032 | 0.7105 | 0.3688 | 0.2348 | 0.1389 | 0.048 | 0.1758 | 0.2312 | 0.0571 | 0.3332 | 0.0646 | 0.1367 | 0.2703 | 0.1463 | 0.1804 | 0.1927 | 0.5406 | 0.869 | 0.2208 | 0.1331 | 1.0974 | 1.0414 | 0.5972 | 0.5768 | 0.0863 | 0.2299 | 0.1771 | 0.048 | 0.1423 | 0.1374 | 0.3222 | 0.3079 | 0.357 | 0.3128 | 1.6821 | 0.3752 | 2.7472 | 0.6287 | 0.421 | 0.4839 | 0.6307 | 0.6996 | 0.3016 | 0.2208 | 0.1862 | 0.394 | 0.6263
Load_TR1_F1_36 | prosumer | 0.1833 | 0.051 | 0.0666 | 0.2066 | 0.051 | 0.2066 | 0.0666 | 0.051 | 0.2222 | 0.051 | 0.1755 | 0.0977 | 0.051 | 0.1444 | 0.1288 | 0.0703 | 0.2613 | 1.3614 | 0.8029 | 1.2913 | 0.191 | 0.051 | 0.2066 | 0.0666 | 0.0588 | 0.2144 | 0.051 | 0.0952 | 0.1134 | 0.0586 | 0.2198 | 0.0859 | 0.0987 | 0.2774 | 0.063 | 0.2991 | 0.3931 | 0.2102 | 0.1848 | 0.2935 | 0.4482 | 0.6293 | 0.568 | 0.4366 | 0.4674 | 0.7617 | 0.3167 | 0.4343
Load_TR1_F1_37 | prosumer | 0.2288 | 0.0841 | 0.3192 | 0.052 | 0.0643 | 0.3309 | 0.06 | 0.1749 | 0.052 | 0.2163 | 0.2152 | 0.0806 | 0.239 | 0.1642 | 0.1073 | 0.3734 | 0.097 | 0.2056 | 0.2023 | 0.2206 | 0.1528 | 0.6213 | 0.2216 | 0.2859 | 1.0427 | 0.6753 | 0.1857 | 0.1787 | 0.1183 | 0.2104 | 0.1955 | 0.2186 | 0.5026 | 0.1627 | 0.2203 | 0.202 | 0.2019 | 0.3742 | 0.4082 | 0.1081 | 0.2951 | 0.052 | 0.2283 | 0.052 | 0.1749 | 0.1321 | 0.2711 | 0.068
Load_TR1_F1_38 | prosumer | 0.1298 | 0.1298 | 0.1122 | 0.1075 | 0.1521 | 0.048 | 0.0629 | 0.1967 | 0.048 | 0.1967 | 0.0629 | 0.048 | 0.0563 | 0.2115 | 0.048 | 0.048 | 0.2115 | 0.048 | 0.3706 | 0.4651 | 0.6609 | 1.5417 | 0.4666 | 0.103 | 0.5811 | 1.3936 | 0.8968 | 0.1042 | 0.7368 | 0.7937 | 0.5859 | 0.1225 | 0.4432 | 1.1144 | 0.7606 | 0.1975 | 0.6037 | 0.1973 | 0.8636 | 0.9282 | 1.5454 | 0.8636 | 0.4927 | 1.5617 | 0.3854 | 0.4005 | 0.8143 | 0.048
Load_TR1_F1_39 | prosumer | 0.045 | 0.045 | 0.0601 | 0.1964 | 0.045 | 0.0753 | 0.1812 | 0.045 | 0.2115 | 0.045 | 0.045 | 0.2115 | 0.045 | 0.045 | 0.0526 | 0.439 | 0.0812 | 1.5282 | 0.3212 | 0.3967 | 0.181 | 0.045 | 0.2115 | 0.045 | 0.045 | 0.427 | 0.1062 | 0.1033 | 0.2647 | 0.2087 | 0.3437 | 0.4961 | 0.2324 | 0.7845 | 2.0419 | 0.8337 | 0.5623 | 0.7237 | 0.481 | 0.3564 | 0.4851 | 1.6572 | 1.1879 | 0.867 | 0.9004 | 0.8109 | 0.1888 | 0.045
Load_TR1_F1_4 | prosumer | 0.0788 | 0.2877 | 0.05 | 0.05 | 0.2949 | 0.0716 | 0.1271 | 0.225 | 0.0644 | 0.158 | 0.2086 | 0.0963 | 0.2342 | 0.086 | 0.2012 | 0.1653 | 0.1487 | 1.3683 | 0.5546 | 0.1868 | 0.1797 | 0.1495 | 0.3951 | 1.2829 | 0.1992 | 0.3631 | 0.3585 | 0.2841 | 0.6485 | 0.1822 | 0.1661 | 0.2623 | 0.1699 | 0.2649 | 0.1589 | 0.158 | 0.2866 | 0.3471 | 0.1678 | 0.4162 | 1.8851 | 0.6092 | 0.7627 | 0.9286 | 0.7314 | 0.5498 | 0.4424 | 0.616
Load_TR1_F1_40 | prosumer | 0.3784 | 0.2161 | 0.054 | 0.054 | 0.054 | 0.1203 | 0.2685 | 0.054 | 0.2611 | 0.1277 | 0.0908 | 0.2979 | 0.054 | 0.2088 | 0.0614 | 0.1203 | 0.657 | 0.1499 | 0.2425 | 0.1246 | 0.8356 | 1.4714 | 1.6979 | 0.3299 | 0.3102 | 0.7518 | 0.2934 | 0.4144 | 0.5074 | 0.3516 | 0.2895 | 0.7752 | 0.6343 | 0.6631 | 0.2795 | 0.2934 | 0.3239 | 0.4042 | 0.1919 | 0.6453 | 0.3285 | 0.4375 | 0.7376 | 0.7242 | 0.6538 | 0.825 | 0.8264 | 0.6471
Load_TR1_F1_41 | prosumer | 0.1071 | 0.047 | 0.1596 | 0.0996 | 0.0515 | 0.1938 | 0.1596 | 0.047 | 0.2122 | 0.047 | 0.0921 | 0.1671 | 0.047 | 0.2122 | 0.047 | 0.1596 | 0.0996 | 0.077 | 0.1822 | 0.047 | 0.1596 | 0.0996 | 0.1071 | 0.1521 | 0.047 | 0.1296 | 0.1296 | 0.047 | 0.077 | 0.1822 | 0.047 | 0.1972 | 0.062 | 0.047 | 0.0845 | 0.1747 | 0.047 | 0.047 | 0.047 | 0.2122 | 0.047 | 0.0713 | 0.2126 | 0.4777 | 0.3264 | 0.2662 | 0.3623 | 0.557
Load_TR1_F1_42 | prosumer | 0.2199 | 0.104 | 0.2894 | 0.074 | 0.1317 | 0.2227 | 0.108 | 0.2812 | 0.166 | 0.1031 | 0.3352 | 0.049 | 0.237 | 0.2013 | 0.049 | 0.2183 | 0.223 | 0.8454 | 1.3558 | 1.4402 | 1.481 | 0.247 | 0.0767 | 0.1799 | 0.1878 | 0.1883 | 0.2038 | 0.2095 | 0.7275 | 0.6003 | 0.3049 | 0.5278 | 0.7545 | 1.3441 | 0.7779 | 0.423 | 0.5186 | 0.7902 | 0.074 | 0.3516 | 0.3454 | 0.9935 | 0.2812 | 0.0569 | 0.9337 | 0.1367 | 0.1511 | 0.1869
Load_TR1_F1_43 | prosumer | 0.1002 | 0.331 | 0.0577 | 0.2261 | 0.155 | 0.1737 | 0.2093 | 0.2479 | 0.1833 | 0.1983 | 0.1608 | 0.1241 | 0.2233 | 0.1269 | 0.1473 | 0.3186 | 0.049 | 0.4075 | 0.3749 | 0.9513 | 0.248 | 0.6482 | 1.412 | 2.511 | 0.4583 | 0.1531 | 0.1269 | 0.2101 | 0.307 | 1.4659 | 0.2629 | 0.2307 | 0.924 | 0.4799 | 0.3499 | 0.2429 | 0.192 | 0.2422 | 0.1254 | 0.4449 | 0.6123 | 0.5052 | 0.2167 | 0.3606 | 0.0577 | 0.3065 | 0.1507 | 0.062
Load_TR1_F1_44 | customer | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.2941 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.086 | 0.2021 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 1.0159 | 0.746 | 0.1788 | 0.1436 | 0.0942 | 0.1671 | 0.2453 | 0.28 | 0.4356 | 0.046 | 0.046 | 0.8458 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046
Load_TR1_F1_45 | customer | 0.1288 | 0.053 | 0.1204 | 0.0614 | 0.0951 | 0.0867 | 0.053 | 0.1288 | 0.053 | 0.053 | 0.1288 | 0.053 | 0.1288 | 0.053 | 0.053 | 0.1288 | 0.053 | 0.1907 | 0.1832 | 0.1314 | 0.061 | 0.3172 | 0.0658 | 0.1548 | 0.8675 | 0.1209 | 0.302 | 0.4523 | 3.429 | 0.9708 | 2.2582 | 0.3005 | 0.2095 | 0.1879 | 0.2237 | 0.2416 | 0.1331 | 0.3905 | 0.16 | 0.4427 | 0.5969 | 1.8317 | 0.5245 | 0.3211 | 0.462 | 0.6858 | 0.6828 | 0.3379
Load_TR1_F1_46 | customer | 0.049 | 0.0702 | 0.1836 | 0.049 | 0.1765 | 0.0773 | 0.0915 | 0.1623 | 0.049 | 0.1906 | 0.0632 | 0.1269 | 0.1269 | 0.049 | 0.2048 | 0.049 | 0.049 | 0.0702 | 0.3895 | 0.9502 | 0.0905 | 0.3638 | 0.5259 | 0.3746 | 1.4734 | 0.3041 | 0.1307 | 0.2198 | 0.0734 | 0.222 | 0.5341 | 0.2198 | 1.0425 | 0.1402 | 0.1233 | 0.1774 | 1.6912 | 0.1602 | 0.3059 | 0.5453 | 0.3927 | 0.6126 | 0.424 | 0.6492 | 0.5537 | 0.5627 | 0.6544 | 0.5395
Load_TR1_F1_47 | prosumer | 0.051 | 0.1678 | 0.1083 | 0.051 | 0.1837 | 0.0924 | 0.051 | 0.0796 | 0.1906 | 0.1014 | 0.0637 | 0.1019 | 0.0574 | 0.0765 | 0.1996 | 0.0858 | 1.0118 | 0.1005 | 0.4102 | 0.2595 | 0.1848 | 0.3693 | 0.2498 | 0.2554 | 0.1544 | 0.0696 | 0.2511 | 0.2124 | 0.4901 | 0.3685 | 0.2373 | 0.1678 | 0.0924 | 0.2264 | 1.4147 | 0.8254 | 1.5978 | 0.3525 | 0.124 | 0.316 | 0.3162 | 0.1083 | 0.1099 | 0.1661 | 0.051 | 0.1083 | 0.1094 | 0.1666
Load_TR1_F1_48 | customer | 0.048 | 0.048 | 0.048 | 0.1304 | 0.048 | 0.048 | 0.0617 | 0.1167 | 0.0663 | 0.1121 | 0.048 | 0.048 | 0.048 | 0.0617 | 0.1167 | 0.048 | 0.048 | 0.0892 | 0.0892 | 0.048 | 0.048 | 0.08 | 0.0984 | 2.7837 | 1.6286 | 2.2629 | 0.8309 | 0.2277 | 0.201 | 0.048 | 0.048 | 0.1194 | 0.08 | 0.06 | 1.2096 | 0.633 | 1.6685 | 1.5145 | 1.3225 | 0.9576 | 0.1361 | 0.1075 | 0.0709 | 0.048 | 0.0873 | 0.0526 | 0.1258 | 0.048
Load_TR1_F1_49 | prosumer | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1745 | 0.0843 | 0.0917 | 0.0791 | 0.1006 | 0.0864 | 0.1473 | 0.1786 | 0.0782 | 1.1199 | 0.2884 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1455 | 0.4832 | 0.5063 | 0.6141 | 0.1239 | 0.7021 | 0.4141 | 0.3408
Load_TR1_F1_5 | prosumer | 2.4385 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.0971 | 0.1954 | 0.1038 | 0.055 | 0.055 | 0.3915 | 0.214 | 0.3906 | 0.7517 | 0.4945 | 2.1865 | 2.649 | 0.723 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.3056 | 0.364 | 0.2595 | 0.055 | 0.055
Load_TR1_F1_6 | prosumer | 0.0951 | 0.1044 | 0.058 | 0.1323 | 0.0673 | 0.0998 | 0.0998 | 0.058 | 0.1416 | 0.058 | 0.058 | 0.058 | 0.1416 | 0.058 | 0.058 | 0.1974 | 0.26 | 0.1416 | 0.058 | 0.058 | 0.2079 | 0.1916 | 0.058 | 0.058 | 0.058 | 0.2989 | 0.2154 | 0.3109 | 0.2546 | 0.1339 | 0.1229 | 0.2014 | 0.0879 | 1.8224 | 0.4318 | 0.058 | 0.1416 | 0.058 | 0.0859 | 0.1145 | 0.1893 | 1.7806 | 1.4758 | 1.019 | 0.5096 | 0.3194 | 0.1416 | 0.058
Load_TR1_F1_7 | customer | 0.055 | 0.055 | 0.055 | 0.1307 | 0.055 | 0.055 | 0.1222 | 0.0634 | 0.055 | 0.1138 | 0.0718 | 0.055 | 0.1012 | 0.0844 | 0.1222 | 0.0634 | 0.055 | 0.4823 | 0.055 | 0.055 | 0.0718 | 0.1138 | 0.055 | 0.0844 | 0.1012 | 0.055 | 0.1307 | 0.1088 | 0.0881 | 0.3059 | 0.1676 | 0.6045 | 0.4782 | 0.3045 | 0.1918 | 0.225 | 0.217 | 0.1849 | 0.1428 | 0.2637 | 0.4868 | 0.3705 | 0.251 | 0.2337 | 0.7334 | 0.4665 | 0.2199 | 0.1332
Load_TR1_F1_8 | customer | 0.046 | 0.167 | 0.2109 | 0.046 | 0.046 | 0.225 | 0.153 | 0.046 | 0.2277 | 0.1503 | 0.046 | 0.2354 | 0.153 | 0.0948 | 0.1991 | 0.13 | 0.1541 | 0.2302 | 0.1707 | 0.046 | 0.6024 | 0.0907 | 0.1036 | 0.3007 | 0.046 | 0.0867 | 0.2913 | 0.1295 | 0.4629 | 0.2241 | 0.1226 | 0.3687 | 0.0818 | 0.1957 | 0.2607 | 0.1802 | 0.4885 | 0.1421 | 0.046 | 0.3319 | 0.046 | 0.046 | 0.153 | 0.0785 | 0.1924 | 0.153 | 0.046 | 0.1315
Load_TR1_F1_9 | customer | 0.04 | 0.1087 | 0.1648 | 0.0629 | 0.117 | 0.1412 | 0.1198 | 0.1461 | 0.1084 | 0.1651 | 0.04 | 0.2335 | 0.04 | 0.2804 | 0.2538 | 0.1444 | 0.1925 | 0.2438 | 0.9031 | 0.4368 | 1.701 | 2.046 | 0.8597 | 0.22 | 1.6621 | 0.2289 | 0.2701 | 0.3648 | 0.2923 | 0.3134 | 0.3005 | 0.3302 | 1.4295 | 0.2358 | 0.6111 | 0.3569 | 0.3541 | 1.4979 | 0.1011 | 0.1648 | 0.1087 | 0.04 | 0.1024 | 0.1024 | 0.04 | 0.0744 | 0.0931 | 0.1728
Load_TR1_F6_1 | prosumer | 0.5223 | 0.0966 | 0.1305 | 0.057 | 0.057 | 0.0683 | 0.1588 | 0.057 | 0.1701 | 0.057 | 0.1305 | 0.0966 | 0.057 | 0.057 | 0.0796 | 0.1475 | 0.3055 | 1.1964 | 0.6177 | 0.3622 | 0.3146 | 0.9811 | 0.9254 | 0.5585 | 0.9342 | 1.5169 | 0.2146 | 0.4951 | 0.2596 | 0.1362 | 0.0909 | 0.057 | 0.1701 | 0.057 | 0.057 | 0.057 | 0.3893 | 0.0627 | 0.1007 | 0.5277 | 0.8284 | 0.7352 | 0.5455 | 0.5535 | 0.969 | 0.6903 | 1.1789 | 0.704
Load_TR1_F6_10 | prosumer | 0.1331 | 0.05 | 0.0863 | 0.1175 | 0.05 | 0.1538 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0656 | 0.1383 | 0.05 | 0.05 | 0.0959 | 0.1678 | 0.054 | 0.351 | 1.2517 | 0.2931 | 0.2516 | 0.3053 | 0.2595 | 1.0785 | 0.3139 | 0.2308 | 0.4022 | 0.3127 | 0.0716 | 0.1742 | 0.1147 | 0.1846 | 0.1332 | 0.281 | 0.1586 | 0.082 | 0.1279 | 0.0649 | 0.2023 | 0.1953 | 0.1666 | 0.05 | 0.05 | 0.05 | 0.1486 | 0.0552 | 0.0656 | 0.1383
Load_TR1_F6_11 | prosumer | 0.1966 | 0.055 | 0.3883 | 0.0699 | 0.1073 | 0.2337 | 0.0998 | 0.1667 | 0.1855 | 0.0662 | 0.1222 | 0.2188 | 0.1222 | 0.1592 | 0.1706 | 0.0662 | 0.2449 | 0.0961 | 0.0848 | 0.2562 | 0.055 | 0.1369 | 0.1705 | 0.1184 | 0.2375 | 0.0737 | 0.0624 | 0.23 | 0.1036 | 0.055 | 0.2673 | 0.055 | 0.1183 | 0.2227 | 0.055 | 0.2972 | 0.2683 | 0.5726 | 0.4401 | 0.3699 | 0.6699 | 1.3253 | 3.0703 | 2.9746 | 0.3962 | 0.6128 | 0.4064 | 0.4471
Load_TR1_F6_12 | prosumer | 0.6549 | 0.6932 | 0.4794 | 0.0913 | 0.1602 | 0.05 | 0.208 | 0.1731 | 0.1946 | 0.1087 | 0.1277 | 0.05 | 0.3311 | 0.05 | 0.276 | 0.2023 | 0.3137 | 0.36 | 0.3193 | 0.0889 | 0.4905 | 0.3539 | 0.2993 | 0.4061 | 0.2898 | 0.2978 | 0.1584 | 0.2761 | 0.152 | 1.2395 | 2.8772 | 2.6168 | 0.5086 | 0.0839 | 0.3391 | 0.3943 | 1.565 | 3.5466 | 4.5369 | 1.5188 | 0.6124 | 0.6124 | 0.5621 | 0.7989 | 0.4681 | 0.7646 | 0.4991 | 0.0579
Load_TR1_F6_13 | prosumer | 0.2451 | 0.3883 | 0.2691 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.07 | 0.9204 | 1.5653 | 0.0632 | 0.248 | 0.4712 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 2.2341 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.0657 | 0.1466 | 0.103 | 0.1083 | 0.2444 | 0.2409 | 0.2989 | 0.2986 | 0.5995 | 0.3201 | 0.6654 | 0.054 | 0.054
Load_TR1_F6_14 | customer | 0.116 | 0.041 | 0.116 | 0.041 | 0.116 | 0.041 | 0.041 | 0.091 | 0.066 | 0.041 | 0.116 | 0.041 | 0.116 | 0.041 | 0.0785 | 0.0785 | 0.041 | 0.0952 | 0.0618 | 0.0785 | 0.0785 | 0.0493 | 0.1077 | 0.041 | 0.116 | 0.041 | 0.041 | 0.116 | 0.041 | 0.116 | 0.041 | 0.041 | 0.041 | 0.116 | 0.041 | 0.041 | 0.2949 | 0.2699 | 0.084 | 0.5874 | 0.3596 | 0.488 | 0.5402 | 0.5938 | 0.5592 | 0.3521 | 0.041 | 0.041
Load_TR1_F6_15 | customer | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.1754 | 0.9091 | 0.128 | 0.1516 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.1249 | 0.1877 | 0.1877 | 0.1896 | 0.2169 | 0.2169 | 0.1984 | 0.305 | 0.2968 | 0.3704 | 0.5255 | 0.4402 | 0.4572 | 1.7427 | 1.5248 | 1.1027
Load_TR1_F6_16 | customer | 0.1649 | 0.057 | 0.057 | 0.057 | 0.1739 | 0.1287 | 0.1829 | 0.1197 | 0.1649 | 0.1377 | 0.057 | 0.197 | 0.1056 | 0.1056 | 0.1164 | 0.0794 | 0.1153 | 0.1326 | 0.1656 | 0.0615 | 0.1458 | 0.1568 | 0.057 | 0.2053 | 0.0973 | 0.1434 | 0.1592 | 0.057 | 0.296 | 0.2903 | 0.2261 | 0.2494 | 0.3714 | 0.2375 | 0.3928 | 0.2414 | 0.1571 | 0.1643 | 0.1049 | 0.2445 | 0.3398 | 0.3748 | 0.2764 | 0.4521 | 0.4801 | 0.4501 | 0.2557 | 0.0929
Load_TR1_F6_17 | prosumer | 0.059 | 0.1728 | 0.1659 | 0.1728 | 0.059 | 0.2684 | 0.0704 | 0.0818 | 0.1501 | 0.059 | 0.1659 | 0.059 | 0.1659 | 0.1728 | 0.059 | 0.3551 | 0.2754 | 0.2009 | 0.5482 | 0.4078 | 1.3054 | 0.3288 | 0.5177 | 0.3119 | 0.2798 | 0.1125 | 0.1125 | 0.1728 | 0.1971 | 0.059 | 0.1349 | 0.2038 | 0.0932 | 0.2456 | 0.059 | 0.1793 | 0.1659 | 0.0761 | 0.1707 | 0.248 | 0.5725 | 0.6361 | 0.4945 | 0.6053 | 0.855 | 0.605 | 0.1506 | 0.1653
Load_TR1_F6_18 | prosumer | 0.147 | 0.1978 | 0.0955 | 0.0955 | 0.044 | 0.175 | 0.1698 | 0.0514 | 0.2655 | 0.072 | 0.0734 | 0.2714 | 0.044 | 0.3011 | 0.2293 | 1.1455 | 0.2575 | 0.1386 | 0.3082 | 0.0661 | 0.1768 | 0.168 | 0.072 | 0.1698 | 0.1977 | 0.2767 | 0.2345 | 0.3105 | 0.098 | 0.147 | 0.1978 | 0.125 | 0.2129 | 0.051 | 0.044 | 0.264 | 0.1458 | 0.1349 | 0.2228 | 0.4252 | 0.5776 | 0.6167 | 0.2431 | 0.6529 | 0.4526 | 0.4093 | 0.3121 | 0.1176
Load_TR1_F6_19 | prosumer | 0.1675 | 0.1166 | 0.1612 | 0.1606 | 0.1354 | 0.1675 | 0.1606 | 0.1241 | 0.204 | 0.06 | 0.06 | 0.2681 | 0.06 | 0.1424 | 0.1857 | 0.1332 | 0.1949 | 0.1332 | 0.1823 | 0.0765 | 0.0675 | 0.4693 | 0.0817 | 0.2328 | 0.1156 | 0.1698 | 0.186 | 0.1449 | 0.1844 | 0.3886 | 0.3396 | 0.2294 | 0.1925 | 0.1864 | 0.354 | 0.4428 | 0.4942 | 0.2 | 0.476 | 0.4319 | 0.4336 | 0.2989 | 0.3073 | 0.3172 | 0.2973 | 0.4081 | 0.1409 | 0.1424
Load_TR1_F6_2 | prosumer | 0.0698 | 0.3721 | 0.161 | 0.05 | 0.2084 | 0.05 | 0.2084 | 0.05 | 0.1652 | 0.0932 | 0.122 | 0.1364 | 0.05 | 0.0716 | 0.1901 | 0.1194 | 0.3798 | 1.5499 | 2.0568 | 1.1561 | 0.1976 | 0.2065 | 0.4008 | 0.4445 | 1.0176 | 0.3877 | 0.0613 | 0.4306 | 1.2279 | 0.4963 | 0.831 | 0.1277 | 0.1724 | 0.086 | 0.2679 | 0.2942 | 0.504 | 0.265 | 1.6119 | 0.9776 | 1.1909 | 0.2126 | 0.3154 | 0.423 | 0.2701 | 0.2495 | 0.1791 | 0.102
Load_TR1_F6_20 | prosumer | 0.0734 | 0.2983 | 0.1502 | 0.1656 | 0.2557 | 0.1004 | 0.3186 | 0.1452 | 0.1656 | 0.058 | 0.2195 | 0.1907 | 0.1115 | 0.1584 | 0.1964 | 0.9831 | 0.5016 | 0.334 | 1.2747 | 1.2457 | 0.4786 | 0.4621 | 0.0625 | 0.2107 | 0.1977 | 0.1089 | 0.4407 | 0.2204 | 0.2103 | 0.5849 | 0.0941 | 0.9327 | 0.4058 | 0.058 | 0.2677 | 0.1961 | 0.3731 | 0.26 | 0.3051 | 0.6243 | 0.9207 | 1.5458 | 1.0172 | 0.9556 | 1.3587 | 0.5728 | 0.8204 | 0.2857
Load_TR1_F6_21 | prosumer | 0.2692 | 0.2254 | 0.1806 | 0.1315 | 0.1835 | 0.2571 | 0.2234 | 0.1539 | 0.1251 | 0.2234 | 0.2102 | 0.1029 | 0.2154 | 0.1726 | 0.3079 | 0.1867 | 0.5289 | 1.4367 | 0.1027 | 0.275 | 0.3742 | 0.3813 | 0.9852 | 0.9036 | 0.3431 | 0.1795 | 0.6086 | 0.2328 | 0.8895 | 0.378 | 0.2561 | 0.4742 | 0.269 | 0.4906 | 1.6395 | 1.5404 | 0.4215 | 0.1103 | 0.3561 | 0.0621 | 0.2168 | 0.4161 | 0.2187 | 0.4064 | 0.0527 | 0.3079 | 0.1726 | 0.048
Load_TR1_F6_22 | prosumer | 0.1116 | 0.0822 | 0.048 | 0.1191 | 0.048 | 0.1191 | 0.1458 | 0.052 | 0.213 | 0.048 | 0.1458 | 0.048 | 0.048 | 0.2169 | 0.048 | 0.052 | 0.2825 | 0.2528 | 0.3712 | 1.4082 | 0.4229 | 0.7342 | 0.6534 | 0.4122 | 0.3706 | 0.5535 | 0.6936 | 0.3038 | 0.6514 | 0.3452 | 0.333 | 0.6286 | 0.7092 | 0.1786 | 0.5611 | 0.3853 | 0.194 | 0.3459 | 0.1925 | 0.5348 | 0.678 | 1.0413 | 1.1526 | 1.1736 | 1.0433 | 1.2753 | 1.2401 | 0.547
Load_TR1_F6_23 | prosumer | 0.059 | 0.2931 | 0.059 | 0.2076 | 0.1445 | 0.059 | 0.1853 | 0.059 | 0.1726 | 0.1794 | 0.0779 | 0.1663 | 0.1437 | 0.4158 | 1.3566 | 0.3968 | 0.3164 | 0.2508 | 0.2047 | 0.059 | 0.2315 | 0.1206 | 0.1853 | 0.059 | 0.2757 | 0.4446 | 0.4024 | 0.2619 | 0.4132 | 0.5062 | 0.059 | 1.4441 | 0.1845 | 0.1955 | 0.2731 | 0.2912 | 0.2272 | 0.0997 | 0.16 | 0.1129 | 0.1129 | 0.1789 | 0.1731 | 0.1537 | 0.1753 | 0.0821 | 0.059 | 0.059
Load_TR1_F6_24 | prosumer | 0.3915 | 0.047 | 0.047 | 0.047 | 0.1275 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.0783 | 0.0962 | 0.0873 | 0.0873 | 0.047 | 0.047 | 0.1007 | 0.0738 | 0.047 | 0.047 | 0.047 | 0.1275 | 0.047 | 0.1141 | 0.0604 | 0.5079 | 0.1059 | 0.1472 | 0.0627 | 0.1275 | 0.0525 | 0.1179 | 0.2262 | 0.1507 | 0.2066 | 0.1501 | 0.2176 | 0.1383 | 0.123 | 0.0515 | 0.1096 | 0.226 | 0.2922 | 0.5291 | 0.3477 | 0.3217 | 0.6137 | 0.442
Load_TR1_F6_25 | prosumer | 0.526 | 0.4467 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.1007 | 0.052 | 0.052 | 0.052 | 0.052 | 0.1517 | 0.188 | 0.188 | 0.188 | 0.224 | 0.1638 | 0.0531 | 0.3255 | 0.9566 | 2.7955 | 3.0301 | 0.5762 | 0.2264 | 0.2181 | 0.4991 | 0.4115 | 0.2102 | 0.4005 | 0.1449 | 0.052 | 0.052 | 0.1615 | 0.4544 | 0.4366 | 0.9993 | 2.8233 | 4.3317 | 0.493 | 0.3743 | 0.2793
Load_TR1_F6_26 | prosumer | 0.053 | 0.1313 | 0.053 | 0.053 | 0.1313 | 0.053 | 0.1052 | 0.0791 | 0.053 | 0.0747 | 0.1095 | 0.053 | 0.1095 | 0.0747 | 0.053 | 0.1368 | 0.053 | 0.1446 | 0.087 | 0.134 | 0.3873 | 0.053 | 0.1008 | 0.0834 | 0.0965 | 0.0878 | 0.0965 | 0.0878 | 0.053 | 0.1313 | 0.053 | 0.1313 | 0.1116 | 0.213 | 0.2595 | 0.2491 | 0.2867 | 0.4966 | 0.2979 | 0.6647 | 0.5621 | 0.391 | 0.5151 | 0.5018 | 0.4486 | 0.2303 | 0.053 | 0.1313
Load_TR1_F6_27 | customer | 0.3651 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.2718 | 0.917 | 0.0632 | 0.0632 | 0.0438 | 0.0806 | 0.1668 | 0.1651 | 0.3721 | 0.1802 | 0.1625 | 0.156 | 0.2207 | 0.2668 | 0.4471 | 0.2006 | 0.3168 | 0.2551 | 0.0503 | 0.039 | 0.0457 | 0.1263 | 0.1071 | 0.1342 | 0.4198 | 0.618 | 0.588 | 0.7402 | 0.7013 | 0.498 | 0.4347 | 0.5577 | 0.2835 | 0.2792
Load_TR1_F6_28 | customer | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 1.4289 | 0.8769 | 0.2242 | 0.9648 | 0.043 | 0.043 | 1.0505 | 1.1066 | 0.8887 | 0.1043 | 0.1445 | 0.0476 | 0.1007 | 0.8849 | 0.079 | 0.5085 | 2.3571 | 0.1099 | 0.1458 | 0.1279 | 0.0918 | 0.055 | 0.0681 | 0.0673 | 0.4541 | 0.0946 | 0.345 | 0.7276 | 0.5411 | 0.7456 | 0.3214 | 0.3183 | 0.4386 | 0.5325 | 0.3739
Load_TR1_F6_29 | prosumer | 0.1419 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.6957 | 3.0721 | 2.5158 | 0.046 | 0.2272 | 0.2817 | 0.8045 | 0.7067 | 1.743 | 0.1505 | 0.1255 | 0.3696 | 0.2577 | 0.614 | 0.046 | 0.046 | 1.1148 | 1.2253 | 0.3624 | 0.3823 | 0.2686 | 0.2632 | 0.398 | 0.5812 | 0.4828 | 0.5795 | 0.7285 | 0.9078 | 0.5562 | 0.4085 | 0.201 | 0.046
Load_TR1_F6_3 | prosumer | 0.042 | 0.1268 | 0.1394 | 0.3507 | 0.4632 | 0.5421 | 0.2103 | 0.1398 | 0.0746 | 0.1138 | 0.1007 | 0.042 | 0.1333 | 0.0811 | 0.042 | 0.1268 | 0.0877 | 0.042 | 0.1725 | 0.042 | 0.042 | 0.0746 | 0.1543 | 0.0854 | 0.3145 | 0.2644 | 0.1893 | 0.3531 | 0.1492 | 0.3051 | 0.1744 | 0.072 | 0.2062 | 0.2566 | 0.2481 | 0.2943 | 0.042 | 0.0642 | 0.2297 | 0.6666 | 0.76 | 0.6093 | 0.6708 | 0.1545 | 0.4433 | 0.454 | 0.3599 | 0.3368
Load_TR1_F6_30 | prosumer | 0.1965 | 0.037 | 0.037 | 0.2049 | 0.0538 | 0.0454 | 0.2133 | 0.037 | 0.2217 | 0.037 | 0.1747 | 0.1126 | 0.037 | 0.2217 | 0.037 | 0.1126 | 0.1461 | 0.0622 | 0.1965 | 0.037 | 0.2217 | 0.037 | 0.037 | 0.1126 | 0.1461 | 0.1136 | 0.1055 | 0.1045 | 0.1629 | 0.037 | 0.1965 | 0.0622 | 0.0414 | 0.0471 | 0.239 | 0.0532 | 0.037 | 0.2298 | 0.0528 | 0.2498 | 0.1719 | 1.212 | 0.6396 | 0.4117 | 0.4693 | 0.1698 | 0.1965 | 0.037
Load_TR1_F6_31 | prosumer | 0.1157 | 0.248 | 0.04 | 0.1828 | 0.1808 | 0.04 | 0.1913 | 0.0551 | 0.1459 | 0.206 | 0.082 | 0.1762 | 0.1572 | 0.04 | 0.2181 | 0.1455 | 0.1157 | 0.2362 | 0.082 | 0.1762 | 0.1959 | 0.4203 | 0.6333 | 2.1077 | 0.2834 | 0.4991 | 1.8999 | 0.9846 | 0.0414 | 0.1364 | 0.2904 | 0.5936 | 0.1746 | 0.0693 | 0.2357 | 0.1279 | 0.0576 | 0.306 | 0.059 | 0.3328 | 0.558 | 2.3091 | 0.4268 | 0.2453 | 0.2401 | 0.2423 | 0.2588 | 0.2854
Load_TR1_F6_32 | customer | 0.1336 | 0.172 | 0.1121 | 0.0812 | 0.2163 | 0.0761 | 0.0721 | 0.2615 | 0.0961 | 0.056 | 0.1637 | 0.1458 | 0.0723 | 0.2573 | 0.0681 | 0.1001 | 0.184 | 0.0895 | 0.1121 | 0.2214 | 0.04 | 0.1826 | 0.151 | 0.04 | 0.2735 | 0.06 | 0.048 | 0.234 | 0.1361 | 0.1077 | 0.3348 | 0.1748 | 0.2873 | 0.139 | 0.0921 | 0.192 | 0.0895 | 0.0812 | 0.2283 | 0.064 | 0.2214 | 0.0921 | 0.2002 | 0.0812 | 0.1041 | 0.081 | 0.2606 | 0.04
Load_TR1_F6_33 | prosumer | 0.2179 | 0.0812 | 0.1277 | 0.1744 | 0.0679 | 0.1178 | 0.1564 | 0.0978 | 0.0956 | 0.1486 | 0.1377 | 0.0635 | 0.2156 | 0.063 | 0.049 | 0.159 | 0.1377 | 0.0604 | 0.3532 | 0.3178 | 1.0402 | 0.4127 | 0.3865 | 0.1254 | 0.1377 | 0.0635 | 0.2306 | 0.048 | 0.1852 | 0.1089 | 0.0829 | 0.1028 | 0.1254 | 0.2311 | 0.2432 | 0.3421 | 0.2759 | 0.3208 | 0.2201 | 0.4176 | 0.0879 | 0.2241 | 0.3504 | 0.4665 | 0.5227 | 0.5067 | 0.1553 | 0.1616
Load_TR1_F6_34 | prosumer | 0.3133 | 0.0813 | 0.2601 | 0.0551 | 0.1804 | 0.1569 | 0.1315 | 0.2098 | 0.1239 | 0.2023 | 0.1066 | 0.0834 | 0.1727 | 0.1796 | 0.1239 | 0.2174 | 0.1239 | 0.1569 | 0.2324 | 0.2273 | 1.6134 | 0.1723 | 0.3042 | 0.391 | 0.1982 | 0.2474 | 0.1017 | 0.201 | 0.3309 | 0.2633 | 0.3821 | 0.3011 | 0.1481 | 0.1134 | 0.4426 | 0.2289 | 0.2937 | 0.178 | 0.173 | 0.5644 | 0.3678 | 0.5943 | 0.6868 | 0.6629 | 0.1342 | 0.2575 | 0.274 | 0.0915
Load_TR1_F6_35 | prosumer | 0.03 | 0.1614 | 0.03 | 0.1614 | 0.03 | 0.1154 | 0.076 | 0.0826 | 0.1089 | 0.9876 | 0.2438 | 0.03 | 0.03 | 0.1286 | 0.0629 | 0.0694 | 0.122 | 0.03 | 0.1689 | 0.035 | 0.1027 | 0.1154 | 0.0629 | 0.1294 | 0.0308 | 0.3506 | 0.1815 | 0.03 | 0.1614 | 0.03 | 0.03 | 0.1614 | 0.03 | 0.1352 | 0.0563 | 0.0826 | 0.1089 | 0.03 | 0.0629 | 0.1286 | 0.0431 | 0.3232 | 0.3048 | 0.4303 | 0.4162 | 0.03 | 0.03 | 0.03
Load_TR1_F6_36 | prosumer | 0.1604 | 0.2423 | 0.1471 | 0.187 | 0.159 | 0.14 | 0.2131 | 0.225 | 0.0821 | 0.2569 | 0.1471 | 0.2282 | 0.1462 | 0.1263 | 0.2764 | 0.048 | 1.3635 | 3.5399 | 1.9137 | 1.6307 | 2.9215 | 2.3098 | 0.485 | 1.2514 | 0.2973 | 0.3079 | 0.0529 | 0.3852 | 0.048 | 0.269 | 0.169 | 0.0622 | 0.2741 | 0.1498 | 0.2459 | 0.4507 | 0.2666 | 0.4922 | 0.048 | 0.2994 | 0.2725 | 0.4762 | 0.8475 | 1.0006 | 1.0267 | 1.9568 | 0.5738 | 0.9264
Load_TR1_F6_37 | prosumer | 0.2932 | 0.0884 | 0.1978 | 0.0582 | 0.0913 | 0.3387 | 0.041 | 0.2212 | 0.1881 | 0.0617 | 0.128 | 0.302 | 0.041 | 0.3313 | 0.1792 | 0.1438 | 0.2088 | 0.1184 | 0.2357 | 0.117 | 0.3234 | 0.2181 | 0.1137 | 1.2677 | 1.3285 | 0.2468 | 1.5779 | 0.3558 | 0.4135 | 0.6021 | 0.9073 | 0.28 | 1.816 | 0.2338 | 1.1629 | 2.0586 | 0.562 | 0.4417 | 0.2052 | 0.4387 | 0.5516 | 0.4037 | 0.7551 | 0.6624 | 0.542 | 0.4118 | 0.0582 | 0.1913
Load_TR1_F6_38 | prosumer | 0.1241 | 0.14 | 0.1798 | 0.14 | 0.1798 | 0.112 | 0.084 | 0.1365 | 0.0993 | 0.2019 | 0.1179 | 0.14 | 0.056 | 0.2639 | 0.056 | 0.2142 | 0.1056 | 0.166 | 0.1538 | 0.1241 | 0.4294 | 1.8841 | 0.2568 | 1.1737 | 1.2377 | 0.2197 | 0.4275 | 0.1106 | 0.2639 | 0.056 | 0.2032 | 0.1167 | 0.1117 | 0.512 | 0.3887 | 0.3576 | 0.2834 | 0.2197 | 0.3326 | 0.6015 | 0.5656 | 0.5587 | 0.6804 | 0.4121 | 0.5129 | 0.4378 | 0.1756 | 0.07
Load_TR1_F6_39 | prosumer | 0.0954 | 0.0954 | 0.058 | 0.1328 | 0.058 | 0.1328 | 0.058 | 0.058 | 0.1203 | 0.0705 | 0.058 | 0.058 | 0.058 | 0.1328 | 0.058 | 0.1042 | 0.6585 | 1.1697 | 0.3353 | 0.2964 | 0.5069 | 0.3686 | 0.3392 | 0.6903 | 0.5001 | 0.6184 | 0.3052 | 1.5742 | 1.5163 | 1.8786 | 0.2659 | 0.2177 | 0.1077 | 0.2764 | 2.8897 | 0.1229 | 1.2695 | 0.2959 | 0.1783 | 0.4813 | 0.6189 | 0.5553 | 0.5305 | 0.5532 | 0.5008 | 0.8176 | 0.8934 | 1.4333
Load_TR1_F6_4 | customer | 0.056 | 0.2009 | 0.1521 | 0.101 | 0.111 | 0.056 | 0.156 | 0.197 | 0.091 | 0.1723 | 0.1457 | 0.156 | 0.1265 | 0.1265 | 0.071 | 0.282 | 0.056 | 0.2436 | 0.1095 | 0.1345 | 0.5046 | 0.056 | 0.056 | 0.056 | 0.2174 | 0.3315 | 0.3165 | 0.4919 | 0.2629 | 0.3095 | 0.442 | 0.4293 | 0.0816 | 0.156 | 0.056 | 0.2078 | 0.1452 | 0.086 | 0.1645 | 0.1585 | 0.156 | 0.0752 | 0.1778 | 0.056 | 0.5248 | 0.407 | 0.8477 | 0.3234
Load_TR1_F6_40 | customer | 0.0645 | 0.057 | 0.1318 | 0.0869 | 0.057 | 0.1617 | 0.057 | 0.057 | 0.057 | 0.1617 | 0.057 | 0.0645 | 0.1542 | 0.057 | 0.3239 | 0.308 | 0.057 | 0.2489 | 0.2802 | 0.4523 | 0.3208 | 0.4013 | 0.5672 | 0.3064 | 0.573 | 0.4211 | 0.228 | 0.1103 | 0.1019 | 0.1168 | 0.057 | 0.1617 | 0.057 | 0.1243 | 0.0944 | 0.057 | 0.057 | 0.2683 | 0.2205 | 0.2603 | 0.2411 | 0.1165 | 0.4836 | 0.4022 | 0.4627 | 0.7165 | 0.6169 | 0.5997
Load_TR1_F6_41 | customer | 0.5529 | 0.135 | 0.18 | 0.1812 | 0.057 | 0.2657 | 0.1084 | 0.122 | 0.1492 | 0.1339 | 0.057 | 0.1723 | 0.1498 | 0.096 | 0.2261 | 0.135 | 0.1108 | 0.1847 | 0.0647 | 0.7141 | 0.5025 | 0.4722 | 0.1188 | 0.0724 | 1.7641 | 0.9154 | 0.206 | 0.1552 | 0.1108 | 0.1723 | 0.1766 | 1.3491 | 0.3818 | 0.2374 | 0.152 | 0.7484 | 1.0239 | 0.962 | 0.383 | 0.5567 | 0.5009 | 0.5767 | 1.2947 | 1.2529 | 0.7982 | 0.2665 | 0.2031 | 0.1581
Load_TR1_F6_42 | customer | 0.2628 | 0.0545 | 0.2449 | 0.0653 | 0.1687 | 0.157 | 0.1818 | 0.0784 | 0.1177 | 0.1687 | 0.1439 | 0.0522 | 0.2014 | 0.1373 | 1.0754 | 0.3988 | 0.0791 | 0.0875 | 0.1308 | 0.0285 | 0.2259 | 2.0443 | 0.5129 | 0.6517 | 0.2164 | 0.4438 | 0.2123 | 0.2622 | 0.148 | 0.2538 | 1.2904 | 0.8121 | 0.0973 | 0.1813 | 0.1574 | 0.0718 | 0.2669 | 0.026 | 0.1647 | 0.1741 | 0.0849 | 0.4054 | 0.4818 | 0.4924 | 1.225 | 0.2884 | 0.4675 | 0.3096
Load_TR1_F6_43 | customer | 0.1792 | 0.0787 | 0.0572 | 0.2008 | 0.05 | 0.1362 | 0.1218 | 0.0787 | 0.1792 | 0.05 | 0.05 | 0.208 | 0.05 | 0.1649 | 0.2553 | 0.2019 | 0.5247 | 0.05 | 0.2661 | 0.245 | 0.2019 | 0.3168 | 0.2298 | 0.1235 | 0.3168 | 0.4174 | 0.208 | 0.05 | 0.1649 | 0.0931 | 0.05 | 0.05 | 0.3122 | 0.2019 | 0.2521 | 0.3096 | 0.2537 | 0.4001 | 0.2653 | 0.5032 | 0.2595 | 0.3376 | 0.7699 | 0.4169 | 0.3994 | 0.6697 | 0.05 | 0.05
Load_TR1_F6_44 | customer | 0.2269 | 0.0699 | 0.1484 | 0.1484 | 0.062 | 0.117 | 0.1798 | 0.062 | 0.219 | 0.0777 | 0.1719 | 0.1248 | 0.062 | 0.2347 | 0.0639 | 0.2155 | 0.344 | 0.336 | 1.1251 | 0.3158 | 0.29 | 0.117 | 0.2185 | 0.5223 | 2.0403 | 0.5525 | 0.3934 | 0.7104 | 0.1013 | 0.3749 | 0.2419 | 0.2645 | 0.3922 | 0.2245 | 0.2491 | 0.2941 | 0.1496 | 0.0856 | 0.2112 | 0.062 | 0.1562 | 0.1405 | 0.062 | 0.2347 | 0.062 | 0.1641 | 0.1327 | 0.062
Load_TR1_F6_45 | prosumer | 0.0886 | 0.0803 | 0.0803 | 0.101 | 0.0596 | 0.043 | 0.043 | 0.1176 | 0.043 | 0.043 | 0.1176 | 0.043 | 0.0927 | 0.0679 | 0.043 | 0.043 | 0.2416 | 0.2042 | 0.2269 | 0.3214 | 0.0637 | 0.0969 | 0.043 | 0.043 | 0.043 | 0.1176 | 0.0657 | 0.043 | 0.1176 | 0.043 | 0.0844 | 0.0761 | 0.043 | 0.043 | 0.0471 | 0.2973 | 0.2545 | 0.1606 | 0.2493 | 0.2469 | 0.4119 | 0.4043 | 0.4213 | 0.503 | 0.6577 | 0.5122 | 0.345 | 0.2887
Load_TR1_F6_46 | customer | 0.119 | 0.1351 | 0.039 | 0.1911 | 0.063 | 0.039 | 0.1271 | 0.1271 | 0.039 | 0.2151 | 0.039 | 0.063 | 0.1911 | 0.039 | 0.1671 | 0.087 | 0.039 | 0.039 | 0.1448 | 1.0933 | 0.1137 | 0.3879 | 0.4548 | 0.2218 | 0.5245 | 0.354 | 0.0455 | 0.0403 | 0.3384 | 0.1439 | 0.1271 | 0.1271 | 0.0435 | 0.0541 | 2.238 | 3.9898 | 0.7948 | 0.1431 | 0.039 | 0.2151 | 0.039 | 0.039 | 0.087 | 0.1671 | 0.039 | 0.039 | 0.079 | 0.1751
Load_TR1_F6_47 | customer | 0.047 | 0.2342 | 0.0559 | 0.1272 | 0.1629 | 0.047 | 0.2431 | 0.047 | 0.047 | 0.2431 | 0.1201 | 0.1094 | 0.1807 | 0.047 | 0.047 | 0.1985 | 0.0916 | 0.047 | 0.1896 | 0.1005 | 0.0846 | 0.047 | 0.1461 | 0.153 | 0.107 | 0.2346 | 0.2792 | 0.1272 | 0.3574 | 0.0697 | 1.5125 | 0.5336 | 0.3142 | 0.2941 | 0.3789 | 0.1309 | 0.5082 | 0.1433 | 0.3139 | 0.2629 | 0.999 | 0.7833 | 0.6331 | 0.7996 | 0.5206 | 0.853 | 0.5634 | 0.047
Load_TR1_F6_48 | prosumer | 0.4006 | 0.0911 | 0.2539 | 0.036 | 0.2466 | 0.0643 | 0.1479 | 0.163 | 0.064 | 0.2092 | 0.0738 | 0.036 | 0.1899 | 0.121 | 0.0619 | 0.3067 | 0.0767 | 0.1282 | 0.2043 | 0.2191 | 0.064 | 0.2499 | 0.036 | 0.0399 | 0.1626 | 0.1385 | 0.4859 | 0.3705 | 0.2568 | 0.3345 | 0.1912 | 0.2059 | 0.4445 | 0.2387 | 0.4964 | 0.3708 | 0.1561 | 0.3386 | 0.1303 | 0.3627 | 0.4343 | 0.7727 | 0.5724 | 0.4984 | 0.5095 | 0.2083 | 0.1444 | 0.2749
Load_TR1_F6_49 | customer | 0.1264 | 0.1264 | 0.044 | 0.0515 | 0.2013 | 0.044 | 0.089 | 0.1639 | 0.044 | 0.2088 | 0.044 | 0.0815 | 0.1714 | 0.044 | 0.2088 | 0.0921 | 0.9597 | 0.2062 | 0.2162 | 0.7856 | 0.2111 | 0.284 | 0.2887 | 0.2167 | 0.4752 | 0.3406 | 0.2644 | 0.2008 | 2.0375 | 2.4804 | 2.2993 | 0.4566 | 0.089 | 0.044 | 0.4718 | 0.2328 | 0.2604 | 0.3468 | 0.0962 | 0.4681 | 0.534 | 0.9451 | 0.6534 | 0.5449 | 0.7026 | 0.6137 | 0.2394 | 0.2088
Load_TR1_F6_5 | customer | 0.1694 | 0.073 | 0.2433 | 0.1461 | 0.0616 | 0.3277 | 0.053 | 0.2346 | 0.0616 | 0.0929 | 0.2705 | 0.0789 | 0.1461 | 0.2433 | 0.0929 | 0.2619 | 0.0876 | 0.0862 | 0.1129 | 0.053 | 0.3479 | 0.4525 | 0.085 | 0.1777 | 0.2564 | 0.1172 | 0.2516 | 0.2594 | 0.0635 | 0.3164 | 0.073 | 0.1135 | 0.2758 | 0.053 | 0.2346 | 0.1547 | 0.1308 | 0.1654 | 0.253 | 0.3673 | 0.2108 | 0.2902 | 0.2852 | 0.2442 | 0.3849 | 0.2337 | 0.5034 | 0.5649
Load_TR1_F6_50 | customer | 0.1233 | 0.2319 | 0.0561 | 0.1126 | 0.048 | 0.2588 | 0.1045 | 0.0694 | 0.2092 | 0.06 | 0.0939 | 0.2694 | 0.048 | 0.1741 | 0.1549 | 0.1236 | 0.3967 | 1.4683 | 1.0002 | 1.1177 | 0.1742 | 0.0534 | 0.06 | 0.498 | 0.048 | 0.1747 | 0.2193 | 0.0736 | 0.2403 | 0.123 | 0.1566 | 0.4004 | 0.1103 | 0.1678 | 0.073 | 0.3092 | 0.3678 | 0.3425 | 0.1403 | 0.3618 | 1.703 | 1.8987 | 0.888 | 0.2403 | 0.0642 | 0.5544 | 0.2299 | 0.2953
Load_TR1_F6_51 | customer | 0.0898 | 0.1984 | 0.04 | 0.113 | 0.1619 | 0.04 | 0.0887 | 0.1862 | 0.0765 | 0.0765 | 0.1619 | 0.113 | 0.1231 | 0.1518 | 0.2721 | 0.1784 | 0.0602 | 0.0954 | 0.1843 | 0.04 | 0.1619 | 0.4901 | 1.5345 | 0.1023 | 0.0765 | 0.2665 | 0.0927 | 0.1495 | 1.385 | 1.1643 | 1.206 | 0.228 | 0.0519 | 0.1747 | 1.028 | 0.8618 | 0.1532 | 0.5169 | 0.04 | 0.113 | 0.1397 | 0.0622 | 0.04 | 0.2349 | 0.04 | 0.1231 | 0.1396 | 0.0522
Load_TR1_F6_52 | customer | 0.0778 | 0.1228 | 0.051 | 0.2312 | 0.0887 | 0.051 | 0.1896 | 0.1302 | 0.0852 | 0.2347 | 0.051 | 0.1126 | 0.2073 | 0.1177 | 0.0767 | 0.1765 | 0.1433 | 0.1703 | 0.0573 | 0.2563 | 0.0636 | 0.0972 | 0.1537 | 0.1201 | 0.051 | 0.2746 | 0.1233 | 0.2512 | 0.1834 | 0.153 | 0.1117 | 0.175 | 0.051 | 0.2586 | 0.0613 | 0.1138 | 0.1696 | 0.193 | 0.4075 | 0.3068 | 0.281 | 0.0715 | 0.1703 | 0.3054 | 0.2044 | 0.1433 | 0.1765 | 0.051
Load_TR1_F6_53 | prosumer | 0.058 | 0.058 | 0.058 | 0.124 | 0.058 | 0.058 | 0.124 | 0.058 | 0.058 | 0.124 | 0.058 | 0.1093 | 0.0727 | 0.058 | 0.058 | 0.1057 | 0.0763 | 0.2889 | 0.2068 | 0.1429 | 0.2544 | 0.2464 | 0.2464 | 0.2464 | 0.2504 | 0.2922 | 0.4587 | 0.474 | 1.2443 | 0.0653 | 0.1988 | 0.058 | 0.124 | 0.058 | 0.058 | 0.124 | 0.058 | 0.058 | 0.058 | 0.058 | 0.124 | 0.058 | 0.058 | 0.0983 | 0.0837 | 0.058 | 0.058 | 0.124
Load_TR1_F6_54 | prosumer | 0.1531 | 0.1684 | 0.0848 | 0.2953 | 0.0646 | 0.1771 | 0.2117 | 0.08 | 0.1185 | 0.056 | 0.3328 | 0.056 | 0.2944 | 0.0945 | 0.056 | 0.1425 | 0.056 | 0.3328 | 0.0843 | 0.3932 | 0.5963 | 0.4003 | 0.8593 | 2.7715 | 2.6415 | 0.6541 | 0.0646 | 0.056 | 0.2203 | 0.2418 | 0.1396 | 0.2492 | 0.1726 | 0.8238 | 0.9153 | 1.1316 | 0.8455 | 0.2986 | 0.2433 | 0.4562 | 0.4094 | 0.7414 | 0.6522 | 0.6812 | 0.0752 | 0.5267 | 0.3558 | 0.0993
Load_TR1_F6_55 | prosumer | 0.187 | 0.1662 | 0.0881 | 0.2727 | 0.05 | 0.05 | 0.1527 | 0.1356 | 0.0976 | 0.2593 | 0.05 | 0.2984 | 0.0586 | 1.0681 | 1.4265 | 0.214 | 0.5406 | 0.8316 | 0.9966 | 0.6087 | 0.3843 | 0.1442 | 0.547 | 0.1613 | 0.1074 | 0.7758 | 1.09 | 0.6731 | 1.257 | 0.8486 | 1.0352 | 0.6751 | 0.2582 | 0.3401 | 1.3483 | 0.5826 | 0.987 | 0.56 | 1.0996 | 0.0795 | 0.2508 | 0.0805 | 0.2203 | 1.0015 | 0.05 | 0.2383 | 0.1186 | 0.0757
Load_TR1_F6_56 | prosumer | 0.1843 | 0.0682 | 0.2438 | 0.055 | 0.1711 | 0.141 | 0.1116 | 0.1542 | 0.1013 | 0.1145 | 0.1975 | 0.055 | 0.2438 | 0.0682 | 0.0814 | 0.174 | 0.0959 | 0.0707 | 0.1872 | 0.1248 | 0.1309 | 0.1812 | 0.2506 | 0.2246 | 0.0676 | 0.2005 | 0.1116 | 0.055 | 0.2339 | 0.1463 | 0.055 | 0.1909 | 0.1211 | 0.073 | 0.3785 | 0.1552 | 0.1956 | 0.3678 | 0.3704 | 0.7163 | 0.613 | 0.3896 | 0.4531 | 0.0833 | 0.1459 | 0.2476 | 0.055 | 0.1182
Load_TR1_F6_57 | customer | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.0868 | 0.193 | 0.4297 | 0.3687 | 0.1625 | 0.1246 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.1625 | 0.102 | 0.0983 | 0.2442 | 0.2032 | 0.3193 | 0.3671 | 0.4407 | 0.4692 | 0.4998 | 0.4705 | 0.3909 | 0.6031 | 0.049 | 0.049
Load_TR1_F6_58 | customer | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.2316 | 0.0633 | 0.0702 | 0.1614 | 0.053 | 0.053 | 0.0652 | 0.1365 | 0.2334 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.7607 | 0.7597 | 0.0992 | 0.4641 | 0.4855 | 0.2749 | 0.4052 | 0.3632 | 2.1216 | 0.8012 | 0.4918 | 0.1782 | 0.053 | 0.053
Load_TR1_F6_59 | prosumer | 0.3591 | 0.9482 | 0.044 | 0.1133 | 0.0527 | 0.044 | 0.0656 | 0.1003 | 0.044 | 0.0656 | 0.1003 | 0.0786 | 0.0873 | 0.083 | 0.083 | 0.044 | 0.1219 | 0.0997 | 0.3071 | 0.9246 | 0.0632 | 0.1508 | 0.1386 | 0.3964 | 1.0214 | 0.0486 | 0.0496 | 0.1915 | 0.1774 | 0.2525 | 0.2871 | 0.4574 | 1.935 | 0.2351 | 0.2299 | 1.3185 | 1.1608 | 0.4796 | 0.2843 | 0.5727 | 0.5323 | 0.5807 | 0.6233 | 0.3609 | 0.044 | 0.1219 | 0.044 | 0.044
Load_TR1_F6_6 | prosumer | 0.719 | 0.0936 | 0.0603 | 0.2786 | 0.053 | 0.1838 | 0.0821 | 0.126 | 0.1547 | 0.1111 | 0.126 | 0.2128 | 0.053 | 0.1613 | 0.1775 | 0.053 | 0.2858 | 0.053 | 0.2722 | 1.2856 | 3.5097 | 2.2409 | 0.5172 | 2.7508 | 2.9894 | 2.0162 | 0.2556 | 0.4033 | 0.1098 | 0.1935 | 0.2871 | 0.053 | 0.1057 | 0.2331 | 0.126 | 0.1256 | 0.1402 | 0.126 | 0.053 | 0.2858 | 0.053 | 0.1474 | 0.1184 | 0.126 | 0.2128 | 0.053 | 0.0895 | 0.2493
Load_TR1_F6_60 | customer | 0.1378 | 0.2048 | 0.0947 | 0.1595 | 0.1876 | 0.0813 | 0.2121 | 0.0902 | 0.0902 | 0.2479 | 0.0947 | 0.1961 | 0.1465 | 0.0942 | 0.2484 | 0.2445 | 0.2772 | 0.1463 | 0.2755 | 0.3422 | 0.4176 | 0.515 | 1.1808 | 0.5949 | 0.6971 | 0.2829 | 0.1452 | 0.2153 | 0.1126 | 0.2121 | 0.05 | 0.1821 | 0.174 | 0.167 | 0.3619 | 0.1725 | 0.1342 | 0.1458 | 0.1283 | 0.2686 | 0.3135 | 0.4806 | 0.6913 | 0.3774 | 0.5138 | 0.4818 | 0.5363 | 0.2223
Load_TR1_F6_61 | customer | 0.2188 | 0.1888 | 0.1012 | 0.174 | 0.16 | 0.1578 | 0.112 | 0.1338 | 0.1467 | 0.1547 | 0.1793 | 0.053 | 0.2314 | 0.1026 | 0.1012 | 0.1226 | 0.053 | 0.053 | 0.2148 | 0.3728 | 0.0861 | 0.1409 | 0.1671 | 0.7855 | 2.1227 | 0.856 | 0.1642 | 0.6884 | 0.4998 | 0.3126 | 2.2571 | 0.187 | 0.1361 | 0.1956 | 0.2352 | 0.1714 | 0.5405 | 0.299 | 0.1047 | 0.3494 | 0.8437 | 1.4294 | 0.4527 | 0.718 | 0.4858 | 0.6928 | 0.9891 | 0.2623
Load_TR1_F6_62 | prosumer | 0.219 | 0.055 | 0.055 | 0.219 | 0.055 | 0.2115 | 0.0625 | 0.1857 | 0.1519 | 0.055 | 0.055 | 0.1966 | 0.0774 | 0.1519 | 0.1221 | 0.1789 | 0.137 | 0.2196 | 0.1863 | 0.346 | 0.1921 | 0.1402 | 0.2758 | 0.1221 | 0.1789 | 0.9337 | 0.7622 | 0.0923 | 0.1817 | 0.055 | 0.0992 | 0.5318 | 0.4149 | 2.0476 | 2.9623 | 0.4472 | 1.6713 | 0.2061 | 1.5611 | 1.309 | 0.4895 | 0.8395 | 0.8439 | 0.8357 | 0.5523 | 0.4551 | 0.4537 | 0.6877
Load_TR1_F6_63 | customer | 0.11 | 0.1457 | 0.11 | 0.033 | 0.1815 | 0.0743 | 0.033 | 0.1457 | 0.033 | 0.1457 | 0.033 | 0.0929 | 0.1629 | 0.11 | 0.033 | 0.1573 | 0.0984 | 0.033 | 0.0509 | 0.5894 | 0.1192 | 0.0962 | 0.1912 | 0.1252 | 0.033 | 0.2228 | 0.033 | 0.1928 | 0.0815 | 0.312 | 0.3061 | 0.2888 | 0.2141 | 0.2715 | 0.2669 | 0.2891 | 0.2308 | 0.2263 | 0.2908 | 0.4163 | 0.5261 | 0.529 | 0.2993 | 0.2118 | 0.2228 | 0.033 | 0.033 | 0.1457
Load_TR1_F6_64 | prosumer | 0.2849 | 0.2368 | 0.1978 | 0.2302 | 0.1487 | 0.1549 | 0.1925 | 0.2357 | 0.2116 | 0.1294 | 0.1263 | 0.1579 | 0.179 | 0.3426 | 0.0618 | 0.1429 | 0.2493 | 0.082 | 0.5802 | 0.0928 | 0.1294 | 0.3851 | 0.0621 | 0.1782 | 0.3434 | 0.055 | 0.3985 | 0.1231 | 0.2301 | 0.5305 | 0.1643 | 1.2329 | 0.3789 | 0.3637 | 0.5412 | 0.4656 | 0.6471 | 0.2541 | 0.3603 | 0.7856 | 1.6686 | 0.617 | 0.8008 | 0.7364 | 0.7433 | 0.7931 | 0.9316 | 0.6674
Load_TR1_F6_65 | prosumer | 1.7918 | 0.3697 | 0.1176 | 0.11 | 0.1706 | 0.057 | 0.2236 | 0.057 | 0.057 | 0.1024 | 0.1782 | 0.057 | 0.2236 | 0.057 | 0.057 | 0.1479 | 0.1327 | 0.057 | 0.2236 | 0.057 | 0.057 | 0.163 | 0.1176 | 0.057 | 0.057 | 0.2236 | 0.057 | 0.057 | 0.2236 | 0.057 | 0.1327 | 0.3376 | 0.2392 | 0.5259 | 0.3155 | 0.3468 | 0.5131 | 0.414 | 0.265 | 0.4545 | 0.7936 | 0.3432 | 0.3415 | 0.6068 | 0.3692 | 0.057 | 0.2236 | 0.057
Load_TR1_F6_66 | prosumer | 1.9461 | 0.534 | 0.0773 | 0.1474 | 0.1469 | 0.1415 | 0.1528 | 0.054 | 0.1469 | 0.1474 | 0.0617 | 0.2349 | 0.0651 | 0.1055 | 0.1564 | 0.387 | 0.2078 | 0.3349 | 0.2564 | 0.0878 | 0.1096 | 0.1306 | 0.1074 | 0.2727 | 0.164 | 0.2201 | 0.054 | 0.1707 | 0.104 | 0.2111 | 0.1286 | 0.1752 | 0.2884 | 0.2396 | 0.4113 | 0.2575 | 0.3184 | 0.175 | 0.9709 | 0.8176 | 0.6069 | 0.4869 | 0.5375 | 0.4955 | 0.6912 | 0.5086 | 0.1299 | 0.0948
Load_TR1_F6_67 | prosumer | 0.1684 | 0.0842 | 0.1569 | 0.0842 | 0.0496 | 0.1627 | 0.0784 | 0.064 | 0.1253 | 0.041 | 0.2001 | 0.041 | 0.0842 | 0.1569 | 0.0899 | 0.0581 | 0.2001 | 0.041 | 0.1235 | 0.9394 | 0.1202 | 0.2139 | 0.1023 | 0.0928 | 0.2438 | 0.041 | 0.0928 | 0.107 | 0.1906 | 1.1989 | 0.1593 | 0.2097 | 0.1832 | 0.1092 | 0.1483 | 0.0727 | 0.0918 | 0.1176 | 0.0554 | 0.0999 | 0.9906 | 0.8566 | 0.299 | 0.182 | 0.3879 | 0.3345 | 0.041 | 0.1512
Load_TR1_F6_68 | customer | 0.0616 | 0.3393 | 0.1044 | 0.1395 | 0.1598 | 0.206 | 0.1395 | 0.2275 | 0.1383 | 0.1366 | 0.3146 | 0.2966 | 0.2784 | 0.2014 | 0.1941 | 0.4658 | 0.1028 | 0.057 | 0.3872 | 0.1409 | 0.0773 | 0.3343 | 0.0937 | 0.0638 | 0.258 | 0.1561 | 0.0845 | 0.1919 | 0.2564 | 0.057 | 0.3778 | 0.0705 | 0.1395 | 0.206 | 0.1533 | 0.5712 | 0.3863 | 0.1304 | 0.2952 | 0.0797 | 0.1507 | 0.2885 | 0.1395 | 0.0864 | 0.2794 | 0.0983 | 0.201 | 0.1721
Load_TR1_F6_69 | prosumer | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2019 | 0.1946 | 0.1366 | 0.05 | 0.1838 | 1.3797 | 0.2213 | 2.5824 | 1.0973 | 1.7195 | 0.1692 | 0.0628 | 0.2958 | 0.2018 | 0.1493 | 0.1884 | 0.6112 | 1.5205 | 2.6068 | 0.3137 | 1.7604 | 4.0329 | 2.8137 | 0.6546 | 0.2729 | 0.2942 | 1.8944 | 2.5318 | 1.1477 | 0.337 | 0.5458 | 0.3406 | 0.3129
Load_TR1_F6_7 | prosumer | 0.363 | 0.037 | 0.037 | 0.2073 | 0.037 | 0.1299 | 0.1144 | 0.037 | 0.2073 | 0.037 | 0.0447 | 0.1995 | 0.037 | 0.2073 | 0.037 | 0.2492 | 0.2545 | 0.3983 | 0.2073 | 0.0398 | 0.2949 | 0.0944 | 0.1803 | 0.2803 | 0.112 | 0.2888 | 0.1306 | 0.292 | 0.2728 | 0.3161 | 0.1174 | 0.2762 | 0.2059 | 0.037 | 0.2325 | 0.2018 | 0.1148 | 0.1763 | 0.037 | 0.1144 | 0.1299 | 0.037 | 0.0445 | 0.1467 | 0.5123 | 0.3108 | 0.8834 | 0.7567
Load_TR1_F6_70 | prosumer | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.0755 | 0.048 | 0.048 | 0.048 | 0.0522 | 0.2875 | 0.058 | 0.0501 | 0.0649 | 0.5917 | 0.8031 | 0.0988 | 0.0779 | 0.1083 | 0.1485 | 0.1359 | 0.0832 | 0.1466 | 0.2333 | 0.1159 | 0.6739 | 0.3826 | 0.102 | 0.0812 | 0.1445 | 0.1493 | 0.113 | 0.0605 | 0.1499 | 0.1789 | 0.2456 | 0.2739 | 1.324 | 0.6998 | 0.4863 | 0.4052 | 0.5519 | 0.5492 | 0.4068 | 0.2061
Load_TR1_F6_71 | customer | 0.049 | 0.0997 | 0.0744 | 0.0955 | 0.0786 | 0.049 | 0.104 | 0.0701 | 0.1124 | 0.0617 | 0.1082 | 0.0659 | 0.049 | 0.1251 | 0.2793 | 0.2718 | 0.2824 | 0.2498 | 0.3271 | 0.1543 | 0.1632 | 0.1251 | 0.049 | 0.1251 | 0.049 | 0.1251 | 0.1088 | 0.2965 | 0.211 | 0.2478 | 0.172 | 0.0638 | 0.0963 | 0.2109 | 0.0934 | 0.3333 | 1.0791 | 0.1382 | 0.205 | 0.1292 | 0.3058 | 0.4248 | 0.3682 | 0.4856 | 0.1251 | 0.049 | 0.049 | 0.1251
Load_TR1_F6_72 | customer | 0.1592 | 0.057 | 0.1446 | 0.0716 | 0.0716 | 0.1446 | 0.057 | 0.1592 | 0.057 | 0.0862 | 0.13 | 0.057 | 0.1592 | 0.057 | 0.2728 | 0.2027 | 0.0764 | 0.057 | 0.1592 | 0.057 | 0.1592 | 0.057 | 0.057 | 0.1592 | 0.0896 | 2.524 | 2.5641 | 0.2103 | 0.8201 | 2.686 | 2.2205 | 0.1596 | 0.1565 | 0.2469 | 0.3985 | 1.3399 | 0.1766 | 0.1065 | 1.127 | 2.8346 | 2.0007 | 0.3595 | 0.4098 | 0.3344 | 0.057 | 0.1592 | 0.057 | 0.1227
Load_TR1_F6_73 | customer | 0.0675 | 0.2919 | 0.053 | 0.053 | 0.2458 | 0.1136 | 0.053 | 0.3063 | 0.053 | 0.1397 | 0.053 | 0.1852 | 0.1742 | 0.1156 | 0.2437 | 0.1397 | 0.159 | 0.1578 | 1.1347 | 0.458 | 0.2438 | 0.2543 | 0.0964 | 0.0964 | 0.1941 | 0.1652 | 0.1551 | 0.3748 | 0.5858 | 0.3413 | 0.2943 | 0.2267 | 0.258 | 0.2656 | 0.1514 | 0.1742 | 0.117 | 0.1893 | 0.053 | 0.1397 | 0.053 | 0.2196 | 0.053 | 0.053 | 0.1666 | 0.2584 | 0.1454 | 0.2643
Load_TR1_F6_74 | prosumer | 0.1015 | 0.1604 | 0.05 | 0.1236 | 0.1383 | 0.05 | 0.2119 | 0.05 | 0.153 | 0.1162 | 0.05 | 0.2119 | 0.05 | 0.05 | 0.0868 | 0.1751 | 0.2829 | 0.0944 | 0.05 | 0.2119 | 0.05 | 0.1131 | 0.3002 | 0.2788 | 0.1988 | 0.9677 | 0.2367 | 0.0807 | 0.05 | 0.1835 | 0.6644 | 0.9621 | 0.4112 | 0.5032 | 1.1996 | 0.6627 | 0.3797 | 0.2356 | 0.3001 | 0.7988 | 1.7475 | 0.5562 | 0.5453 | 0.4073 | 0.7049 | 0.4486 | 0.364 | 0.2045
Load_TR1_F6_75 | prosumer | 0.055 | 0.1914 | 0.1049 | 0.0838 | 0.1127 | 0.1644 | 0.1319 | 0.1548 | 0.1415 | 0.055 | 0.055 | 0.1548 | 0.055 | 0.1864 | 0.1099 | 1.4883 | 0.2453 | 0.1037 | 0.2926 | 0.1624 | 0.079 | 0.203 | 0.1221 | 0.0886 | 0.2125 | 0.0838 | 0.055 | 0.2365 | 0.0598 | 0.1771 | 0.4343 | 0.4027 | 0.4964 | 0.6243 | 0.7345 | 0.4422 | 0.4739 | 0.5416 | 0.4468 | 0.1415 | 0.1548 | 0.1415 | 0.1192 | 0.0906 | 0.1175 | 0.079 | 0.5105 | 0.4226
Load_TR1_F6_76 | prosumer | 0.2137 | 0.055 | 0.055 | 0.2137 | 0.055 | 0.0983 | 0.1704 | 0.055 | 0.2137 | 0.055 | 0.055 | 0.1921 | 0.0766 | 0.055 | 0.1849 | 0.0839 | 0.055 | 0.2137 | 0.055 | 0.1921 | 0.0766 | 0.055 | 0.1849 | 0.242 | 0.1948 | 0.272 | 0.284 | 0.1887 | 0.3312 | 0.0728 | 0.1989 | 0.2859 | 0.1166 | 0.2003 | 0.055 | 0.2165 | 1.8546 | 0.4684 | 2.2502 | 0.3829 | 0.6911 | 0.4591 | 1.3834 | 0.7137 | 0.91 | 0.818 | 0.3054 | 0.1921
Load_TR1_F6_77 | customer | 0.1596 | 0.058 | 0.058 | 0.3068 | 0.0812 | 0.134 | 0.254 | 0.058 | 0.2138 | 0.1741 | 0.058 | 0.2254 | 0.1625 | 0.1199 | 0.1664 | 0.2558 | 0.3967 | 0.4446 | 0.3787 | 0.37 | 0.3512 | 0.2714 | 0.4475 | 0.2022 | 0.2706 | 0.2293 | 0.1587 | 0.0943 | 0.3423 | 0.2277 | 0.544 | 0.3641 | 0.3131 | 0.5343 | 0.3813 | 0.5955 | 0.058 | 0.058 | 0.2283 | 0.1524 | 0.0653 | 0.1814 | 0.2066 | 0.058 | 0.1819 | 0.1045 | 0.1596 | 0.2283
Load_TR1_F6_78 | customer | 0.4256 | 0.059 | 0.2195 | 0.3158 | 0.059 | 0.059 | 0.2336 | 0.3016 | 0.059 | 0.2866 | 0.2486 | 0.059 | 0.4762 | 0.059 | 0.2993 | 0.2359 | 0.1726 | 0.8566 | 0.561 | 0.2021 | 0.4593 | 0.3356 | 0.1183 | 0.5712 | 0.3807 | 0.2092 | 1.1143 | 0.6441 | 0.2966 | 2.4825 | 2.733 | 1.1558 | 1.4092 | 1.1842 | 1.9046 | 0.5764 | 0.644 | 0.5299 | 0.5408 | 0.6459 | 0.6177 | 0.7055 | 0.7212 | 0.6713 | 0.7422 | 0.669 | 0.3482 | 0.2364
Load_TR1_F6_79 | prosumer | 0.1464 | 0.1814 | 0.1324 | 0.1804 | 0.215 | 0.051 | 0.3513 | 0.051 | 0.2991 | 0.1032 | 0.051 | 0.2683 | 0.134 | 0.1737 | 0.2693 | 0.1729 | 0.2444 | 0.2686 | 0.7101 | 0.7012 | 0.4257 | 0.2242 | 0.1405 | 0.1256 | 0.0883 | 0.314 | 0.051 | 0.0578 | 0.1804 | 0.051 | 1.2044 | 0.1972 | 0.3062 | 0.227 | 0.1421 | 1.4478 | 0.1988 | 0.2699 | 0.28 | 0.1136 | 0.3723 | 0.3352 | 0.346 | 0.2516 | 0.4304 | 0.3387 | 0.3996 | 0.4074
Load_TR1_F6_8 | customer | 0.2256 | 0.053 | 0.1229 | 0.1533 | 0.2138 | 0.0623 | 0.1861 | 0.1763 | 0.0937 | 0.2687 | 0.053 | 0.2256 | 0.1042 | 0.2268 | 0.0844 | 0.1314 | 0.1471 | 0.1229 | 0.2396 | 0.1368 | 0.207 | 0.1725 | 0.1368 | 0.2256 | 0.1368 | 0.0548 | 0.0577 | 0.2734 | 0.0844 | 0.2109 | 0.3884 | 0.2666 | 0.5399 | 0.5149 | 0.3838 | 0.5083 | 0.3842 | 0.4186 | 2.1153 | 2.5706 | 1.6833 | 0.0765 | 0.1829 | 0.1795 | 0.1001 | 0.1785 | 0.1368 | 0.1785
Load_TR1_F6_80 | prosumer | 0.1677 | 0.056 | 0.056 | 0.1677 | 0.056 | 0.1677 | 0.056 | 0.056 | 0.056 | 0.1677 | 0.056 | 0.056 | 0.1677 | 0.056 | 0.1278 | 0.0959 | 0.056 | 0.056 | 0.1677 | 0.056 | 0.1278 | 0.0959 | 0.056 | 0.1677 | 0.056 | 0.056 | 0.056 | 0.1677 | 0.056 | 0.1518 | 0.072 | 0.056 | 0.1677 | 0.056 | 0.056 | 0.1677 | 0.056 | 0.056 | 0.056 | 0.2031 | 0.201 | 0.2158 | 0.2897 | 0.2397 | 0.4504 | 0.3108 | 0.368 | 0.624
Load_TR1_F6_81 | prosumer | 0.7599 | 0.052 | 0.1568 | 0.1246 | 0.0681 | 0.2133 | 0.052 | 0.1568 | 0.1246 | 0.1004 | 0.181 | 0.052 | 0.2133 | 0.0681 | 0.554 | 0.454 | 0.2417 | 0.3635 | 0.1482 | 0.1327 | 0.3543 | 0.052 | 0.0831 | 0.3299 | 0.2479 | 0.2028 | 0.4459 | 0.2545 | 1.0239 | 0.4608 | 0.2786 | 0.285 | 0.3637 | 0.3157 | 0.1003 | 0.3005 | 0.1784 | 0.4586 | 0.4053 | 0.4241 | 0.5774 | 0.7511 | 0.6382 | 0.1165 | 0.1649 | 0.1161 | 0.2214 | 0.052
Load_TR1_F6_82 | prosumer | 0.1068 | 0.265 | 0.1256 | 0.4429 | 0.0893 | 0.366 | 0.2232 | 0.2348 | 0.3348 | 0.1897 | 0.1423 | 0.3065 | 0.1344 | 0.2507 | 0.2752 | 0.2215 | 0.3032 | 0.3596 | 0.2039 | 0.2956 | 0.1957 | 0.1612 | 0.2256 | 0.3191 | 0.1659 | 0.2518 | 0.4052 | 0.3933 | 0.5127 | 0.1799 | 0.1449 | 0.2677 | 0.3708 | 0.1769 | 0.4455 | 0.0954 | 0.4106 | 0.3872 | 0.3908 | 0.278 | 1.7122 | 0.3657 | 0.6276 | 0.8699 | 0.4802 | 0.4697 | 0.4523 | 0.6785
Load_TR1_F6_83 | prosumer | 0.044 | 0.044 | 0.1053 | 0.1506 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.2681 | 0.2037 | 0.2537 | 0.357 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.2698 | 0.2698 | 0.1904 | 0.2077 | 0.1208 | 0.0878 | 0.386 | 0.0954 | 0.044 | 0.044 | 0.044 | 0.044 | 0.1259 | 0.2702 | 0.4128 | 0.2703 | 0.3539 | 0.3838 | 0.3857 | 0.3489 | 0.22 | 0.044
Load_TR1_F6_9 | prosumer | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.3374 | 0.3999 | 0.0501 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.0782 | 0.2179 | 0.5089 | 0.5147 | 0.0601 | 0.0644 | 0.0595 | 0.0733 | 0.1322 | 0.545 | 0.4611 | 0.5946 | 0.4912 | 0.5498 | 0.4401 | 0.6002 | 0.3867 | 0.5132 | 0.4941 | 0.6733 | 0.5128

## 5. Raw batt charge
Raw batt charge
Verbatim copy of Charge_kW (TR1_analysis_data.xlsx). One row per half-hour, one column per battery (kW).
period | hour | BES_TR1_one223_B | BES_TR1_one313_A | BES_TR1_one320_B | BES_TR1_one321_C | BES_TR1_one346_C | BES_TR1_one366_B | BES_TR1_one375_C | BES_TR1_one410_B | BES_TR1_one50_A | BES_TR1_one423_B | BES_TR1_one469_A | BES_TR1_one480_A | BES_TR1_one482_B | BES_TR1_one521_C | BES_TR1_one528_C | BES_TR1_one537_A | BES_TR1_one61_A | BES_TR1_one544_A | BES_TR1_one552_B | BES_TR1_one559_C | BES_TR1_one560_C | BES_TR1_one605_A | BES_TR1_one617_A | BES_TR1_one73_A | BES_TR1_one76_A | BES_TR1_six64_A | BES_TR1_six154_C | BES_TR1_six173_C | BES_TR1_six186_A | BES_TR1_six191_B | BES_TR1_six249_B | BES_TR1_six254_B | BES_TR1_six269_C | BES_TR1_six68_C | BES_TR1_six289_C | BES_TR1_six317_C | BES_TR1_six326_A | BES_TR1_six329_A | BES_TR1_six342_A | BES_TR1_six349_A | BES_TR1_six350_B | BES_TR1_six378_A | BES_TR1_six75_A | BES_TR1_six385_B | BES_TR1_six387_A | BES_TR1_six410_A | BES_TR1_six431_C | BES_TR1_six441_A | BES_TR1_six484_B | BES_TR1_six501_A | BES_TR1_six512_B | BES_TR1_six518_B | BES_TR1_six595_B | BES_TR1_six646_B | BES_TR1_six699_C | BES_TR1_six718_C | BES_TR1_six721_A | BES_TR1_six723_B | BES_TR1_six784_B | BES_TR1_six90_B | BES_TR1_six807_A | BES_TR1_six852_B | BES_TR1_six860_C | BES_TR1_six869_C | BES_TR1_six885_A | BES_TR1_six909_C | BES_TR1_six105_A | BES_TR1_six914_A | BES_TR1_six945_C | BES_TR1_six952_A | BES_TR1_six967_B | BES_TR1_six990_B | BES_TR1_six1006_C | BES_TR1_six1020_A | BES_TR1_six1025_B | BES_TR1_six1064_C | BES_TR1_six128_B
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4.5 | 0.02 | 0.125 | 0.066 | 0.069 | 0.119 | 0 | 0 | 0.025 | 0.061 | 0 | 0.128 | 0.059 | 0.182 | 0 | 0 | 0.1 | 0.075 | 0.105 | 0.157 | 0.013 | 0.034 | 0.044 | 0.124 | 0.119 | 0.146 | 0.088 | 0.183 | 0.166 | 0.008 | 0.179 | 0.174 | 0.044 | 0.114 | 0 | 0.058 | 0 | 0.097 | 0 | 0.127 | 0.093 | 0.158 | 0.187 | 0.061 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.113 | 0.002 | 0.162 | 0.102 | 0 | 0.08 | 0.031 | 0 | 0.118 | 0.109 | 0.005 | 0.061 | 0.103 | 0.13 | 0.085 | 0.075 | 0.095 | 0.108 | 0.156 | 0.116 | 0.061 | 0.003 | 0.129 | 0.036 | 0.132 | 0 | 0.014 | 0.126
11 | 5 | 0.392 | 0.415 | 0.181 | 0.392 | 0.291 | 0.177 | 0.188 | 0.139 | 0.176 | 0.17 | 0.3 | 0 | 0.286 | 0.073 | 0.225 | 0.243 | 0.253 | 0.37 | 0.312 | 0 | 0.301 | 0.225 | 0.296 | 0.291 | 0.346 | 0.158 | 0.396 | 0.339 | 0.103 | 0.407 | 0.295 | 0.157 | 0.286 | 0.051 | 0.011 | 0.078 | 0.143 | 0.21 | 0.268 | 0.236 | 0.352 | 0.415 | 0.245 | 0 | 0.091 | 0.093 | 0.182 | 0.218 | 0.199 | 0.218 | 0.286 | 0.403 | 0.171 | 0.215 | 0.346 | 0 | 0.123 | 0.264 | 0.246 | 0.105 | 0.176 | 0.335 | 0.283 | 0.4 | 0.031 | 0.238 | 0.244 | 0.356 | 0.411 | 0.176 | 0.06 | 0.41 | 0.348 | 0.28 | 0.204 | 0.071 | 0.298
12 | 5.5 | 0.46 | 0.559 | 0.238 | 0.685 | 0.415 | 0.111 | 0.22 | 0.307 | 0.316 | 0.31 | 0.51 | 0.306 | 0.644 | 0.383 | 0.416 | 0.252 | 0.646 | 0.444 | 0.482 | 0.322 | 0.618 | 0.362 | 0.506 | 0.459 | 0.591 | 0.367 | 0.604 | 0.523 | 0.321 | 0.672 | 0.683 | 0.1 | 0.288 | 0.142 | 0.18 | 0.361 | 0.416 | 0.297 | 0.46 | 0.412 | 0.689 | 0.696 | 0.514 | 0.166 | 0.102 | 0.307 | 0.38 | 0.712 | 0.328 | 0.254 | 0.509 | 0.684 | 0.421 | 0.428 | 0.54 | 0.222 | 0 | 0.687 | 0.478 | 0.158 | 0.174 | 0.584 | 0.685 | 0.507 | 0.33 | 0.414 | 0.264 | 0.601 | 0.53 | 0.216 | 0 | 0.474 | 0.593 | 0.69 | 0.25 | 0.141 | 0.508
13 | 6 | 0.926 | 1.008 | 0.474 | 0.949 | 0.659 | 0.321 | 0.602 | 0.321 | 0.389 | 0.299 | 0.74 | 0.387 | 0.997 | 0.416 | 0.599 | 0.61 | 0.814 | 0.994 | 0.87 | 0.287 | 0.825 | 0.598 | 0.736 | 0.591 | 0.775 | 0.598 | 0.998 | 0.926 | 0.193 | 0.127 | 0.882 | 0.48 | 0.726 | 0.343 | 0.412 | 0.44 | 0.607 | 0.511 | 0.699 | 0.603 | 0.938 | 1.002 | 0.653 | 0.356 | 0.236 | 0.308 | 0.482 | 1.018 | 0.64 | 0.745 | 0.861 | 0.99 | 0.562 | 0.465 | 0.844 | 0.099 | 0.334 | 0.804 | 0.699 | 0.471 | 0.447 | 0.869 | 0.824 | 0.983 | 0.44 | 0.605 | 0.618 | 0.865 | 0.998 | 0.469 | 0.185 | 0.914 | 0.749 | 0.835 | 0.652 | 0.218 | 0.738
14 | 6.5 | 1.205 | 1.318 | 0.629 | 1.224 | 0.949 | 0.502 | 0.659 | 0.686 | 0 | 0.618 | 0.972 | 0.409 | 1.213 | 0.684 | 0.637 | 0.804 | 1.272 | 1.149 | 0.976 | 0.478 | 1.231 | 0.772 | 0.968 | 0.915 | 1.13 | 0.792 | 1.308 | 1.199 | 0.629 | 0 | 1.185 | 0.378 | 0.876 | 0.438 | 0.52 | 0.676 | 0.632 | 0.433 | 0.931 | 0.748 | 1.283 | 1.312 | 0.937 | 0.287 | 0.469 | 0.616 | 0.669 | 1.229 | 0.892 | 0.687 | 0.924 | 1.225 | 0.781 | 0.728 | 1.13 | 0.415 | 0 | 1.29 | 0.935 | 0.518 | 0.527 | 1.015 | 1.301 | 1.252 | 0.522 | 0.799 | 0.641 | 0.901 | 1.308 | 0.492 | 0.284 | 1.184 | 1.132 | 1.29 | 0.768 | 0.295 | 0.97
15 | 7 | 1.399 | 1.396 | 0.769 | 1.609 | 1.05 | 0.695 | 0.832 | 0.99 | 0.778 | 0.66 | 1.203 | 0.687 | 1.537 | 0.934 | 0.993 | 0.989 | 1.465 | 1.605 | 1.411 | 0.784 | 1.519 | 0.842 | 1.199 | 1.194 | 1.4 | 0.962 | 1.57 | 1.495 | 0.557 | 1.603 | 1.607 | 0.604 | 1.064 | 0.435 | 0.637 | 0.733 | 0.993 | 0 | 1.202 | 0.989 | 1.613 | 1.62 | 1.207 | 0.588 | 0.407 | 0.784 | 0.917 | 1.603 | 0.973 | 1.07 | 1.402 | 1.608 | 0.998 | 0.979 | 1.4 | 0.569 | 0 | 1.585 | 1.167 | 0.655 | 0.711 | 1.604 | 1.609 | 1.51 | 0.743 | 0.991 | 1.004 | 1.4 | 1.579 | 0.723 | 0.232 | 1.397 | 1.33 | 1.112 | 0.974 | 0.372 | 1.201
16 | 7.5 | 1.627 | 1.318 | 0.868 | 1.29 | 1.426 | 0.72 | 1.011 | 1.094 | 0.886 | 0.844 | 1.435 | 0.807 | 1.622 | 0.861 | 1.186 | 0.795 | 1.809 | 1.854 | 1.568 | 0.769 | 1.656 | 1.148 | 1.431 | 1.426 | 1.53 | 1.087 | 1.019 | 1.908 | 0.785 | 1.727 | 1.62 | 0 | 1.348 | 0.621 | 0.004 | 1.047 | 1.182 | 0.837 | 1.434 | 1.182 | 1.012 | 0.589 | 1.354 | 0.628 | 0.595 | 0.828 | 1.017 | 1.905 | 1.433 | 1.337 | 1.514 | 1.08 | 1.191 | 0.927 | 1.622 | 0.598 | 0.526 | 1.801 | 1.437 | 0.934 | 0.808 | 1.832 | 1.827 | 1.588 | 0.929 | 1.032 | 0.985 | 1.494 | 1.465 | 0 | 0.41 | 1.802 | 1.632 | 1.521 | 1.26 | 0.226 | 1.433
17 | 8 | 0.955 | 0 | 1.082 | 0 | 1.441 | 0.968 | 1.001 | 1.255 | 0.932 | 1.071 | 1.652 | 0.94 | 0 | 1.318 | 1.204 | 1.334 | 0.309 | 0.355 | 0.683 | 0.909 | 0.942 | 0.403 | 0.507 | 1.307 | 0.294 | 1.11 | 0 | 0.367 | 0.818 | 1.793 | 0.142 | 0.875 | 1.503 | 0.469 | 0.631 | 0.886 | 1.133 | 1.099 | 1.089 | 1.363 | 0 | 0 | 1.611 | 0.703 | 0.733 | 0.994 | 1.291 | 0.292 | 0.335 | 1.489 | 1.093 | 0 | 1.174 | 1.338 | 0.026 | 0.793 | 0.309 | 0.073 | 1.576 | 0.846 | 0.995 | 1.014 | 1.31 | 1.645 | 0.932 | 1.221 | 1.161 | 0 | 0 | 0.887 | 0.511 | 0.73 | 0.374 | 1.292 | 1.395 | 0.362 | 0.473
18 | 8.5 | 0 | 0 | 1.218 | 0 | 0 | 1.062 | 0 | 1.485 | 1.042 | 0.971 | 0.295 | 0.728 | 0 | 1.38 | 1.169 | 0.057 | 0 | 0 | 0 | 0.423 | 0 | 1.485 | 0 | 1.667 | 0 | 0.389 | 0 | 0 | 0.908 | 0.339 | 0 | 1.13 | 0.615 | 0 | 0.934 | 0.149 | 1.116 | 1.335 | 0 | 1.134 | 0 | 0 | 1.007 | 0.889 | 0.715 | 1.208 | 1.429 | 0 | 0 | 1.041 | 0 | 0 | 0.605 | 1.457 | 0 | 0.618 | 0.12 | 0 | 0.59 | 1.215 | 1.049 | 0 | 0 | 0 | 1.227 | 0.381 | 1.187 | 0 | 0 | 1.165 | 0.42 | 0 | 0 | 0 | 1.424 | 0.381 | 0
19 | 9 | 0 | 0 | 0.535 | 0 | 0 | 1.089 | 1.489 | 0.563 | 1.158 | 1.184 | 0 | 0.515 | 0 | 0.823 | 0 | 1.096 | 0 | 0 | 0 | 0.028 | 0 | 0.481 | 0 | 0 | 0 | 1.113 | 0 | 0 | 1.065 | 0 | 0 | 1.076 | 0 | 0 | 0.11 | 1.628 | 0 | 1.526 | 0 | 0 | 0 | 0.253 | 0 | 0.842 | 0.956 | 1.031 | 0.652 | 0 | 0.163 | 0 | 0 | 0 | 0 | 0.439 | 0 | 0.954 | 0.042 | 0 | 0 | 1.112 | 1.198 | 0 | 0 | 0 | 1.136 | 0 | 0.363 | 0 | 0 | 1.092 | 0.637 | 0 | 0 | 0 | 0.063 | 0.335 | 0
20 | 9.5 | 0 | 0 | 0 | 0 | 0 | 1.313 | 0 | 0 | 1.257 | 0.961 | 0 | 1.262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043 | 0 | 0 | 0 | 0 | 0 | 0.077 | 0 | 0 | 1.394 | 0 | 0 | 1.417 | 0 | 0 | 0.238 | 1.309 | 0 | 0.792 | 0 | 0 | 0 | 0.342 | 0 | 1.075 | 0.936 | 0.411 | 0 | 0 | 0.594 | 0 | 0 | 0 | 0 | 0 | 0 | 0.719 | 0.504 | 0 | 0 | 0.198 | 0.486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.321 | 0.55 | 0 | 0 | 0 | 0 | 0.698 | 0
21 | 10 | 0 | 0 | 0 | 0 | 0 | 0.336 | 1.25 | 0 | 0.501 | 0 | 0 | 1.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.079 | 0 | 0 | 0.578 | 0 | 0.98 | 1.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.871 | 0.982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.581 | 0.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.505 | 0.708 | 0 | 0 | 0 | 0 | 0.741 | 0
22 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.108 | 0 | 0 | 0 | 0 | 1.025 | 1.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.533 | 0 | 0 | 0 | 0.153 | 0 | 0 | 0 | 0 | 0 | 0 | 0.831 | 1.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.766 | 0 | 0 | 0 | 0.032 | 0.777 | 0
23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.869 | 1.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41 | 0.722 | 0 | 0 | 1.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.661 | 0 | 0 | 0 | 0 | 0.802 | 0
24 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018 | 0 | 0 | 0 | 0.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.519 | 0 | 0 | 0 | 0 | 0.615 | 0 | 0 | 0 | 0.198 | 0.49 | 0
25 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.913 | 0 | 0 | 0 | 0.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.517 | 0 | 0 | 0 | 0.499 | 0 | 0
26 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.367 | 0.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.161 | 0 | 0 | 1.413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.149 | 0.532 | 0 | 0 | 1.203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.863 | 0 | 0 | 0.027 | 0
29 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.929 | 0 | 0 | 0 | 1.423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.626 | 0 | 0 | 0.576 | 0
30 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.087 | 0 | 0 | 0 | 0 | 0 | 1.223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.837 | 0.231 | 0 | 0 | 1.246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004 | 0 | 0 | 0.485 | 0
31 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.232 | 0 | 0 | 0 | 0.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086 | 0 | 0 | 0 | 0.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.247 | 0 | 0 | 0 | 0 | 0
38 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031 | 0 | 0.335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0 | 0.106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077 | 0 | 0 | 0 | 0.021 | 0.071 | 0 | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 6. Raw batt discharge
Raw batt discharge
Verbatim copy of Discharge_kW (TR1_analysis_data.xlsx). One row per half-hour, one column per battery (kW).
period | hour | BES_TR1_one223_B | BES_TR1_one313_A | BES_TR1_one320_B | BES_TR1_one321_C | BES_TR1_one346_C | BES_TR1_one366_B | BES_TR1_one375_C | BES_TR1_one410_B | BES_TR1_one50_A | BES_TR1_one423_B | BES_TR1_one469_A | BES_TR1_one480_A | BES_TR1_one482_B | BES_TR1_one521_C | BES_TR1_one528_C | BES_TR1_one537_A | BES_TR1_one61_A | BES_TR1_one544_A | BES_TR1_one552_B | BES_TR1_one559_C | BES_TR1_one560_C | BES_TR1_one605_A | BES_TR1_one617_A | BES_TR1_one73_A | BES_TR1_one76_A | BES_TR1_six64_A | BES_TR1_six154_C | BES_TR1_six173_C | BES_TR1_six186_A | BES_TR1_six191_B | BES_TR1_six249_B | BES_TR1_six254_B | BES_TR1_six269_C | BES_TR1_six68_C | BES_TR1_six289_C | BES_TR1_six317_C | BES_TR1_six326_A | BES_TR1_six329_A | BES_TR1_six342_A | BES_TR1_six349_A | BES_TR1_six350_B | BES_TR1_six378_A | BES_TR1_six75_A | BES_TR1_six385_B | BES_TR1_six387_A | BES_TR1_six410_A | BES_TR1_six431_C | BES_TR1_six441_A | BES_TR1_six484_B | BES_TR1_six501_A | BES_TR1_six512_B | BES_TR1_six518_B | BES_TR1_six595_B | BES_TR1_six646_B | BES_TR1_six699_C | BES_TR1_six718_C | BES_TR1_six721_A | BES_TR1_six723_B | BES_TR1_six784_B | BES_TR1_six90_B | BES_TR1_six807_A | BES_TR1_six852_B | BES_TR1_six860_C | BES_TR1_six869_C | BES_TR1_six885_A | BES_TR1_six909_C | BES_TR1_six105_A | BES_TR1_six914_A | BES_TR1_six945_C | BES_TR1_six952_A | BES_TR1_six967_B | BES_TR1_six990_B | BES_TR1_six1006_C | BES_TR1_six1020_A | BES_TR1_six1025_B | BES_TR1_six1064_C | BES_TR1_six128_B
1 | 0 | 0.183 | 0.094 | 0.05 | 0.057 | 0.055 | 0.192 | 0.229 | 0.256 | 0.56 | 0.378 | 0.484 | 0.353 | 0.183 | 0.229 | 0.13 | 0.045 | 0.079 | 0.378 | 0.107 | 0.22 | 0.1 | 0.051 | 0.05 | 2.391 | 0.095 | 0.522 | 0.133 | 0.197 | 0.655 | 0.245 | 0.059 | 0.147 | 0.168 | 0.07 | 0.073 | 0.269 | 0.112 | 0.059 | 0.391 | 0.526 | 0.053 | 0.142 | 0.042 | 0.197 | 0.116 | 0.218 | 0.313 | 0.03 | 0.16 | 0.293 | 0.124 | 0.095 | 0.089 | 0.401 | 0.058 | 0.153 | 0.187 | 0.184 | 0.359 | 0.719 | 0.219 | 0.285 | 1.792 | 1.946 | 0.168 | 0.05 | 0.363 | 0.048 | 0.102 | 0.055 | 0.214 | 0.146 | 0.168 | 0.76 | 0.107 | 0.044 | 0.048
2 | 0.5 | 0.24 | 0.04 | 0.133 | 0.057 | 0.055 | 0.218 | 0.108 | 0.095 | 0.534 | 0.382 | 0.506 | 0.503 | 0.051 | 0.084 | 0.13 | 0.045 | 0.288 | 0.216 | 0.047 | 0.104 | 0.331 | 0.168 | 0.05 | 0 | 0.104 | 0.097 | 0.05 | 0.055 | 0.693 | 0.388 | 0.173 | 0.198 | 0.117 | 0.372 | 0.298 | 0.225 | 0.082 | 0.293 | 0.047 | 0.447 | 0.131 | 0.046 | 0.127 | 0.037 | 0.248 | 0.081 | 0.081 | 0.161 | 0.242 | 0.088 | 0.14 | 0.095 | 0.08 | 0.091 | 0.058 | 0.168 | 0.166 | 0.068 | 0.948 | 0.094 | 0.055 | 0.237 | 0.37 | 0.445 | 0.084 | 0.05 | 0.037 | 0.048 | 0.16 | 0.191 | 0.055 | 0.181 | 0.056 | 0.052 | 0.265 | 0.044 | 0.048
3 | 1 | 0.152 | 0.04 | 0.05 | 0.057 | 0.214 | 0.08 | 0.111 | 0.051 | 0.055 | 0.061 | 0.384 | 0.71 | 0.067 | 0.319 | 0.112 | 0.06 | 0.05 | 0.054 | 0.16 | 0.289 | 0.058 | 0.108 | 0.05 | 0 | 0.058 | 0.13 | 0.086 | 0.388 | 0.479 | 0.269 | 0.166 | 0.096 | 0.161 | 0.161 | 0.15 | 0.181 | 0.048 | 0.059 | 0.047 | 0.052 | 0.053 | 0.046 | 0.139 | 0.037 | 0.04 | 0.128 | 0.26 | 0.03 | 0.147 | 0.198 | 0.18 | 0.058 | 0.08 | 0.254 | 0.058 | 0.085 | 0.088 | 0.244 | 0.044 | 0.06 | 0.055 | 0.198 | 0.118 | 0 | 0.157 | 0.05 | 0.037 | 0.048 | 0.05 | 0.105 | 0.055 | 0.132 | 0.056 | 0.157 | 0.126 | 0.105 | 0.048
4 | 1.5 | 0.223 | 0.094 | 0.133 | 0.175 | 0.055 | 0.306 | 0.222 | 0.3 | 0.055 | 0.225 | 0.167 | 0.369 | 0.207 | 0.052 | 0.107 | 0.196 | 0.05 | 0.054 | 0.1 | 0.074 | 0.226 | 0.051 | 0.05 | 0 | 0.132 | 0.057 | 0.117 | 0.07 | 0.091 | 0.054 | 0.173 | 0.096 | 0.161 | 0.05 | 0.166 | 0.131 | 0.119 | 0.208 | 0.047 | 0.052 | 0.053 | 0.046 | 0.351 | 0.205 | 0.183 | 0.174 | 0.055 | 0.161 | 0.187 | 0.058 | 0.14 | 0.133 | 0.101 | 0.036 | 0.124 | 0.295 | 0.273 | 0.055 | 0.113 | 0.279 | 0.219 | 0.23 | 0.11 | 0 | 0.084 | 0.05 | 0.207 | 0.048 | 0.124 | 0.084 | 0.214 | 0.18 | 0.168 | 0.125 | 0.443 | 0.151 | 0.048
5 | 2 | 0.141 | 0.135 | 0.05 | 0.057 | 0.164 | 0.151 | 0.075 | 0.051 | 0.055 | 0.061 | 0.046 | 0.235 | 0.051 | 0.064 | 0.152 | 0.045 | 0.295 | 0.054 | 0.051 | 0.132 | 0.155 | 0.184 | 0.05 | 0 | 0.067 | 0.057 | 0.05 | 0.107 | 0.16 | 0.054 | 0.059 | 0.044 | 0.135 | 0.208 | 0.256 | 0.184 | 0.048 | 0.144 | 0.128 | 0.052 | 0.131 | 0.046 | 0.463 | 0.054 | 0.181 | 0.068 | 0.18 | 0.03 | 0.159 | 0.091 | 0.18 | 0.058 | 0.06 | 0.247 | 0.058 | 0.065 | 0.05 | 0.171 | 0.053 | 0.053 | 0.055 | 0.149 | 0.002 | 0 | 0.05 | 0.05 | 0.037 | 0.048 | 0.138 | 0.113 | 0.055 | 0.215 | 0.056 | 0.068 | 0.089 | 0.044 | 0.048
6 | 2.5 | 0.148 | 0.04 | 0.064 | 0.175 | 0.106 | 0.149 | 0.147 | 0.102 | 0.055 | 0.061 | 0.046 | 0.139 | 0.207 | 0.331 | 0.048 | 0.075 | 0.072 | 0.12 | 0.194 | 0.223 | 0.174 | 0.092 | 0.05 | 0 | 0.1 | 0.068 | 0.154 | 0.234 | 0.05 | 0.054 | 0.268 | 0.175 | 0.168 | 0.05 | 0.1 | 0.257 | 0.119 | 0.059 | 0.047 | 0.052 | 0.053 | 0.046 | 0.542 | 0.045 | 0.04 | 0.118 | 0.157 | 0.115 | 0.14 | 0.339 | 0.112 | 0.133 | 0.043 | 0.064 | 0.058 | 0.177 | 0.05 | 0.141 | 0.044 | 0.184 | 0.212 | 0.155 | 0 | 0 | 0.163 | 0.05 | 0.13 | 0.048 | 0.05 | 0.164 | 0.098 | 0.051 | 0.168 | 0.213 | 0.366 | 0.044 | 0.048
7 | 3 | 0.279 | 0.19 | 0.119 | 0.057 | 0.077 | 0.315 | 0.197 | 0.249 | 0.055 | 0.21 | 0.046 | 0.048 | 0.067 | 0.06 | 0.063 | 0.181 | 0.127 | 0.268 | 0.16 | 0.108 | 0.209 | 0.051 | 0.05 | 0 | 0.1 | 0.159 | 0.05 | 0.1 | 0.208 | 0.054 | 0.07 | 0.17 | 0.161 | 0.208 | 0.319 | 0.223 | 0.146 | 0.185 | 0.047 | 0.052 | 0.105 | 0.046 | 0.21 | 0.213 | 0.191 | 0.156 | 0.132 | 0.076 | 0.213 | 0.041 | 0.084 | 0.058 | 0.043 | 0.148 | 0.124 | 0.212 | 0.153 | 0.112 | 0.066 | 0.082 | 0.062 | 0.193 | 0 | 0 | 0.078 | 0.05 | 0.114 | 0.048 | 0.212 | 0.132 | 0.17 | 0.351 | 0.056 | 0.052 | 0.223 | 0.044 | 0.048
8 | 3.5 | 0.043 | 0.037 | 0.048 | 0.16 | 0.19 | 0.093 | 0.051 | 0.094 | 0.053 | 0.074 | 0.043 | 0.033 | 0.048 | 0.173 | 0.195 | 0.043 | 0.222 | 0.051 | 0.044 | 0.279 | 0.244 | 0.077 | 0.047 | 0 | 0.055 | 0.055 | 0.047 | 0.163 | 0.054 | 0.051 | 0.078 | 0.05 | 0.121 | 0.049 | 0.143 | 0.152 | 0.05 | 0.057 | 0.044 | 0.05 | 0.076 | 0.043 | 0.137 | 0.036 | 0.054 | 0.096 | 0.208 | 0.079 | 0.222 | 0.219 | 0.133 | 0.055 | 0.115 | 0.161 | 0.055 | 0.079 | 0.134 | 0.151 | 0.098 | 0.124 | 0.184 | 0.232 | 0 | 0 | 0.062 | 0.048 | 0.035 | 0.045 | 0.047 | 0.153 | 0.054 | 0.048 | 0.053 | 0.153 | 0.232 | 0.043 | 0.045
9 | 4 | 0.095 | 0.072 | 0.025 | 0.019 | 0.018 | 0.182 | 0.147 | 0.199 | 0.03 | 0.036 | 0.009 | 0 | 0.172 | 0.021 | 0.017 | 0.18 | 0.015 | 0.211 | 0.169 | 0.141 | 0.134 | 0.159 | 0.013 | 0 | 0.098 | 0.139 | 0.0003 | 0.136 | 0 | 0.004 | 0.1 | 0.241 | 0.167 | 0.147 | 0.141 | 0.094 | 0.182 | 0.142 | 0.01 | 0.021 | 0.003 | 0 | 0.037 | 0.203 | 0.127 | 0.071 | 0.093 | 0.059 | 0.045 | 0.151 | 0.056 | 0.071 | 0.012 | 0.033 | 0.014 | 0.1 | 0.079 | 0.052 | 0.007 | 0.13 | 0.127 | 0.162 | 0 | 0 | 0.1 | 0.019 | 0.176 | 0.032 | 0.103 | 0.117 | 0.201 | 0.249 | 0.012 | 0.075 | 0.297 | 0.032 | 0.011
10 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0.099 | 0.02 | 0 | 0 | 0.109 | 0 | 0 | 0 | 0.071 | 0.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.006 | 0 | 0.078 | 0 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0.119 | 0.032 | 0.057 | 0.755 | 0.082 | 0 | 0 | 0 | 0 | 0.064 | 0 | 0 | 0.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015 | 0 | 0
11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 0
13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.535 | 0 | 0 | 0 | 0 | 0 | 0 | 1.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.485 | 0 | 0 | 0 | 1.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.351 | 0 | 0 | 0 | 1.268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.943 | 0 | 0 | 0.48 | 0
27 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0.499 | 0
28 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.078 | 0 | 0 | 0 | 0 | 0 | 1.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.308 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.422 | 0 | 0 | 0 | 0 | 0.209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.132 | 0 | 0 | 0 | 0 | 1.126 | 0 | 0 | 0 | 0 | 1.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0 | 0 | 0 | 0.008 | 0 | 0.453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.009 | 0 | 1.35 | 0 | 0 | 0 | 0.338 | 0.771 | 0 | 0 | 0 | 2.193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0.109 | 0 | 0 | 0 | 0 | 0 | 1.069 | 0 | 0 | 0 | 0.067 | 0 | 0 | 0 | 0 | 0 | 0.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.139 | 0 | 0 | 0 | 0 | 0 | 0.672 | 0.123 | 0 | 0.399 | 0 | 0 | 0 | 0 | 0 | 0 | 0.994 | 0 | 0 | 0 | 0 | 0 | 0.222 | 0 | 0 | 0 | 0 | 0
37 | 18 | 0 | 0 | 0 | 0 | 0 | 1.908 | 0 | 0 | 0 | 0.056 | 0 | 0 | 0 | 0 | 0.027 | 0 | 0 | 0 | 0 | 0.057 | 0 | 1.021 | 0 | 0 | 0 | 0 | 0 | 0 | 1.104 | 0 | 0 | 0 | 0 | 0.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.347 | 0 | 0 | 0 | 0.499 | 0.641 | 0 | 0.469 | 0 | 1.21 | 0 | 0 | 0 | 0 | 3.456 | 0 | 0 | 0 | 0.012 | 1.624 | 0 | 0 | 0 | 0 | 0 | 0
38 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0.175 | 0 | 0 | 0.151 | 0.058 | 0 | 2.432 | 0 | 0 | 0 | 0.33 | 0 | 0 | 0 | 0.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.231 | 0 | 0 | 0 | 0 | 0.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.069 | 0.005 | 0 | 0 | 0.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062 | 0.324 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 0 | 1.687 | 0 | 0 | 0 | 0.226 | 0.311 | 0 | 0 | 0 | 0 | 0 | 0
39 | 19 | 0 | 0 | 0.189 | 0 | 0 | 0.235 | 0.166 | 0.054 | 0 | 0.465 | 0 | 0.445 | 0 | 0.178 | 0.633 | 0.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072 | 1.76 | 0 | 0 | 0.039 | 0.2 | 1.474 | 0.121 | 0.126 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0.036 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0.019 | 0 | 0 | 0.105 | 0.961 | 0.002 | 0.008 | 0 | 1.377 | 0 | 0 | 0.603 | 0 | 0 | 0 | 0 | 0 | 0.263 | 2.158 | 0 | 0 | 0.037 | 0.115 | 0.034 | 0.318
40 | 19.5 | 0.35 | 0 | 1.273 | 0.056 | 0.083 | 0.667 | 0.635 | 0 | 0.171 | 0.767 | 0.237 | 0.367 | 0.186 | 0.041 | 0.861 | 0.289 | 0.309 | 0.538 | 0.118 | 0.298 | 0.338 | 0.249 | 0 | 0 | 0.021 | 0.461 | 0.088 | 0.263 | 0 | 0.137 | 0.141 | 0.372 | 0.352 | 0.937 | 0.571 | 0 | 0.468 | 0.046 | 0 | 0.094 | 0.557 | 0.474 | 0.586 | 0.21 | 0.293 | 0.364 | 0.497 | 0.021 | 0.219 | 0.358 | 0.508 | 0.374 | 0.18 | 0.296 | 0 | 0.416 | 0.039 | 0.609 | 0.492 | 0.232 | 1.255 | 0.678 | 0.347 | 0.71 | 0.046 | 0 | 0.047 | 0.18 | 0.692 | 0.088 | 0.356 | 0.006 | 0.109 | 0.317 | 0.198 | 0.243 | 0.411
41 | 20 | 0.986 | 0.17 | 0.462 | 0.049 | 0.04 | 0.765 | 1.054 | 0.276 | 0.409 | 1.423 | 0.295 | 0.474 | 0.428 | 0.283 | 1.533 | 0.473 | 1.865 | 0.309 | 0.03 | 0.336 | 0.593 | 0.304 | 0.131 | 0.04 | 0.172 | 0.816 | 0.147 | 0.65 | 0 | 0.221 | 0.553 | 0.568 | 0.419 | 1.183 | 0.911 | 0.204 | 0.666 | 0.101 | 0.095 | 0.442 | 0.542 | 0.463 | 0.745 | 0.164 | 0.551 | 0.078 | 0.355 | 0.023 | 0.258 | 0.537 | 0.548 | 0.599 | 0.399 | 0.422 | 0.107 | 0.402 | 0.243 | 0.593 | 0.517 | 0.043 | 0.259 | 1.649 | 0.774 | 0.587 | 0.981 | 0 | 0.118 | 1.307 | 1.728 | 0.145 | 0.686 | 0.353 | 0.184 | 0.558 | 1.697 | 0.408 | 0.535
42 | 20.5 | 0.727 | 0.04 | 0.5 | 0.093 | 0.062 | 1.207 | 0.563 | 0.062 | 1.685 | 0.98 | 0.476 | 0.631 | 0.629 | 0.052 | 0.864 | 1.657 | 0.609 | 0.437 | 0.071 | 0.993 | 0.505 | 0.108 | 0.483 | 0.055 | 1.781 | 0.735 | 0.05 | 1.325 | 0 | 0.299 | 0.636 | 0.617 | 0.299 | 0.213 | 1.546 | 0.416 | 1.041 | 0.179 | 0.226 | 0.437 | 0.391 | 0.579 | 0.609 | 1.212 | 2.309 | 0.224 | 0.594 | 0.323 | 0.476 | 0.404 | 0.559 | 0.555 | 0.404 | 0.773 | 0.058 | 0.741 | 0.08 | 0.39 | 0.581 | 0.147 | 0 | 0.617 | 0.343 | 0.487 | 0.857 | 0 | 0.037 | 0.7 | 0.556 | 0.141 | 0.459 | 0.335 | 0.216 | 0.751 | 0.366 | 0.27 | 0.44
43 | 21 | 0.969 | 0.04 | 0.407 | 0.14 | 0.207 | 1.081 | 0.72 | 0.175 | 0.605 | 0.696 | 0.438 | 0.7 | 0.568 | 0.228 | 0.493 | 1.188 | 0.763 | 0.738 | 0.213 | 0.281 | 0.217 | 0.11 | 0.506 | 0.055 | 1.476 | 0.546 | 0.05 | 3.07 | 0 | 0.299 | 0.494 | 0.243 | 0.307 | 0.315 | 1.017 | 0.219 | 1.153 | 0.173 | 0.292 | 0.999 | 0.515 | 0.728 | 0.671 | 0.64 | 0.427 | 0.35 | 0.687 | 0.305 | 0.848 | 0.755 | 0.68 | 0.531 | 0.421 | 0.572 | 0.058 | 0.652 | 0.22 | 0.453 | 0.623 | 0.118 | 0 | 0.801 | 0.342 | 0.537 | 0.299 | 0 | 0.044 | 0.486 | 0.545 | 0.119 | 1.383 | 0.346 | 0.29 | 0.638 | 0.628 | 0.354 | 0.6
44 | 21.5 | 0.596 | 0.06 | 0.453 | 0.093 | 0.055 | 0.861 | 0.506 | 0.277 | 0.739 | 1.744 | 0.488 | 0.302 | 0.437 | 0.052 | 1.562 | 0.867 | 0.929 | 0.724 | 0.478 | 0.057 | 0.361 | 0.166 | 0.614 | 0.306 | 1.019 | 0.553 | 0.05 | 1.792 | 0 | 0.599 | 0.605 | 0.653 | 0.317 | 0.423 | 0.956 | 0.406 | 1.174 | 0.154 | 0.529 | 2.823 | 0.502 | 0.908 | 0.154 | 0.412 | 0.245 | 0.467 | 0.663 | 0.43 | 1.001 | 0.662 | 0.412 | 0.553 | 0.503 | 0.498 | 0.098 | 0.681 | 1.002 | 0.083 | 0.361 | 0.126 | 0 | 0.736 | 0.607 | 0.495 | 0.182 | 0 | 0.147 | 0.405 | 0.407 | 0.091 | 0.195 | 0.252 | 0.24 | 0.117 | 0.87 | 0.384 | 0.387
45 | 22 | 1.725 | 0.169 | 0.273 | 0.14 | 0.214 | 0.165 | 0.899 | 0.082 | 0.777 | 0.983 | 0.405 | 0.221 | 0.467 | 0.175 | 0.385 | 0.9 | 0.731 | 0.654 | 0.326 | 0.934 | 0.058 | 0.051 | 0.124 | 0.364 | 0.51 | 0.969 | 0.149 | 0 | 0 | 0.32 | 0.855 | 0.453 | 0.297 | 0.27 | 1.359 | 0.053 | 1.043 | 0.175 | 0.348 | 2.376 | 0.449 | 0.556 | 0.443 | 0.469 | 0.24 | 0.523 | 0.134 | 0.416 | 1.027 | 0.542 | 0.513 | 0.501 | 0.658 | 0.51 | 0.084 | 0.075 | 0.05 | 0.146 | 0.044 | 0.213 | 0 | 0.743 | 0.369 | 0.691 | 0.388 | 0 | 0.512 | 0.552 | 0.705 | 0.117 | 0 | 0.43 | 0.45 | 0.165 | 0.48 | 0.386 | 0.513
46 | 22.5 | 0.708 | 0.04 | 0.503 | 0.057 | 0.055 | 0 | 0.676 | 0.269 | 0.545 | 0 | 0.323 | 0.186 | 0.762 | 0.132 | 0.401 | 0.083 | 0.55 | 0.825 | 0.266 | 0.137 | 0.306 | 0.108 | 0.702 | 0.259 | 0.319 | 0.69 | 0.055 | 0 | 0 | 0.665 | 0.605 | 0.409 | 0.408 | 0.25 | 0.573 | 0.308 | 1.275 | 0.082 | 0.322 | 0 | 0.23 | 0.408 | 0.454 | 0.17 | 0.242 | 0.507 | 0.258 | 0.03 | 1.957 | 0.412 | 0.438 | 0.818 | 0.512 | 0.208 | 0.058 | 0.527 | 0.238 | 0.248 | 0.122 | 0.053 | 0 | 0.793 | 0.057 | 0.509 | 0.335 | 0 | 0.311 | 0.549 | 0.449 | 0.079 | 0 | 0.339 | 0.311 | 0.116 | 0.47 | 0.349 | 0.494
47 | 23 | 0.526 | 0.122 | 0.456 | 0.057 | 0.084 | 0 | 1.825 | 0.051 | 0.219 | 0 | 0.594 | 0.394 | 0.317 | 0.271 | 0.441 | 0 | 0.442 | 0.826 | 0.362 | 0.151 | 0.151 | 0.109 | 0.414 | 0.055 | 0.142 | 1.179 | 0.066 | 0 | 0 | 0.054 | 0.151 | 0.312 | 0.141 | 0.179 | 0.119 | 0.173 | 0.353 | 0.059 | 0.614 | 0 | 0.053 | 0.201 | 0.36 | 0.197 | 0.259 | 0.155 | 0.274 | 0.03 | 0.574 | 0.058 | 0.176 | 0.893 | 0.345 | 0.144 | 0.058 | 0.356 | 0.119 | 0.055 | 0.044 | 0.09 | 0 | 0.932 | 0.224 | 0.13 | 0.041 | 0 | 0.883 | 0.407 | 0.364 | 0.511 | 0 | 0.4 | 0.368 | 0.221 | 0.452 | 0.22 | 0.673
48 | 23.5 | 0.532 | 0.108 | 0.311 | 0.14 | 0.185 | 0 | 0.128 | 0.231 | 0.055 | 0 | 0.504 | 0.03 | 0.434 | 0.068 | 0 | 0 | 0.616 | 0.647 | 0.557 | 0.187 | 0.062 | 0.167 | 0.341 | 0.055 | 0.058 | 0.704 | 0.138 | 0 | 0 | 0.054 | 0.165 | 0.118 | 0.142 | 0.102 | 0 | 0.048 | 0 | 0.059 | 0.442 | 0 | 0.131 | 0.046 | 0.337 | 0.037 | 0.285 | 0.162 | 0.092 | 0.03 | 0.814 | 0.191 | 0.07 | 1.433 | 0.289 | 0.275 | 0.124 | 0.099 | 0.076 | 0.118 | 0.044 | 0.249 | 0 | 0.223 | 0.057 | 0.095 | 0.151 | 0 | 0.757 | 0.206 | 0.205 | 0.423 | 0 | 0.407 | 0.624 | 0.052 | 0.678 | 0.044 | 0.513

## 7. PV allocation (per period)
TR1 PV allocation — per half-hour
VIOLET = aggregated live from the raw sheets 3–6 (SUM / SUMIF). AMBER = priority split (MIN formulas): PV → prosumer load → battery → customer load → export.
period | hour (h) | PV (kW) | prosumer load (kW) | customer load (kW) | batt charge (kW) | batt discharge (kW) | batt net =chg−dis | PV→ prosumer | PV→ battery | PV→ customer | PV→ export | customer ←grid
1 | 0 | 0 | 21.0715 | 7.851 | 0 | 21.023 | -21.023 | 0 | 0 | 0 | 0 | 7.851
2 | 0.5 | 0 | 13.7 | 6.5979 | 0 | 13.552 | -13.552 | 0 | 0 | 0 | 0 | 6.5979
3 | 1 | 0 | 9.6827 | 5.4129 | 0 | 9.549 | -9.549 | 0 | 0 | 0 | 0 | 5.4129
4 | 1.5 | 0 | 10.9238 | 7.0902 | 0 | 10.722 | -10.722 | 0 | 0 | 0 | 0 | 7.0902
5 | 2 | 0 | 8.1915 | 5.8701 | 0 | 7.822 | -7.822 | 0 | 0 | 0 | 0 | 5.8701
6 | 2.5 | 0 | 9.5869 | 5.9723 | 0 | 9.334 | -9.334 | 0 | 0 | 0 | 0 | 5.9723
7 | 3 | 0 | 10.1676 | 6.1997 | 0 | 9.736 | -9.736 | 0 | 0 | 0 | 0 | 6.1997
8 | 3.5 | 0.1913 | 7.875 | 6.9557 | 0 | 7.27 | -7.27 | 0.1913 | 0 | 0 | 0 | 6.9557
9 | 4 | 2.7665 | 10.0019 | 5.9338 | 0.004 | 6.7423 | -6.7383 | 2.7665 | 0 | 0 | 0 | 5.9338
10 | 4.5 | 12.9378 | 8.9887 | 6.8415 | 5.71 | 1.764 | 3.946 | 8.9887 | 3.946 | 0.0031 | 0 | 6.8384
11 | 5 | 25.661 | 8.3604 | 6.1488 | 17.673 | 0.32 | 17.353 | 8.3604 | 17.3006 | 0 | 0 | 6.1488
12 | 5.5 | 41.267 | 9.6716 | 6.5477 | 31.624 | 0.027 | 31.597 | 9.6716 | 31.5954 | 0 | 0 | 6.5477
13 | 6 | 58.2894 | 9.6461 | 7.045 | 48.648 | 0 | 48.648 | 9.6461 | 48.6433 | 0 | 0 | 7.045
14 | 6.5 | 75.524 | 13.654 | 7.6288 | 63.153 | 1.279 | 61.874 | 13.654 | 61.87 | 0 | 0 | 7.6288
15 | 7 | 92.6699 | 11.7598 | 11.2833 | 82.028 | 1.117 | 80.911 | 11.7598 | 80.9101 | 0 | 0 | 11.2833
16 | 7.5 | 109.8377 | 15.6407 | 10.4029 | 89.354 | 0.659 | 88.695 | 15.6407 | 88.695 | 5.502 | 0 | 4.9009
17 | 8 | 125.9525 | 18.5108 | 13.5521 | 63.118 | 0 | 63.118 | 18.5108 | 63.118 | 13.5521 | 30.7716 | 0
18 | 8.5 | 141.102 | 32.9066 | 12.7291 | 39.159 | 2.901 | 36.258 | 32.9066 | 36.258 | 12.7291 | 59.2083 | 0
19 | 9 | 154.0028 | 29.6883 | 15.5878 | 26.747 | 1.019 | 25.728 | 29.6883 | 25.728 | 15.5878 | 82.9987 | 0
20 | 9.5 | 165.006 | 28.467 | 15.7189 | 17.897 | 0.352 | 17.545 | 28.467 | 17.545 | 15.7189 | 103.2751 | 0
21 | 10 | 174.6625 | 30.7519 | 19.277 | 12.522 | 2.507 | 10.015 | 30.7519 | 10.015 | 19.277 | 114.6186 | 0
22 | 10.5 | 182.635 | 29.5345 | 23.9829 | 8.378 | 0.599 | 7.779 | 29.5345 | 7.779 | 23.9829 | 121.3386 | 0
23 | 11 | 188.2898 | 29.7675 | 15.3153 | 9.445 | 0.577 | 8.868 | 29.7675 | 8.868 | 15.3153 | 134.339 | 0
24 | 11.5 | 190.7715 | 34.9217 | 15.7782 | 5.251 | 3.343 | 1.908 | 34.9217 | 1.908 | 15.7782 | 138.1636 | 0
25 | 12 | 191.4891 | 29.9438 | 22.0519 | 3.84 | 2.619 | 1.221 | 29.9438 | 1.221 | 22.0519 | 138.2724 | 0
26 | 12.5 | 190.1445 | 27.5602 | 16.9215 | 1.767 | 1.73 | 0.037 | 27.5602 | 0.037 | 16.9215 | 145.6258 | 0
27 | 13 | 185.6304 | 23.5457 | 16.8689 | 2.764 | 3.347 | -0.583 | 23.5457 | 0 | 16.8689 | 145.2158 | 0
28 | 13.5 | 178.741 | 21.435 | 12.8519 | 4.049 | 0.787 | 3.262 | 21.435 | 3.262 | 12.8519 | 141.1921 | 0
29 | 14 | 170.5184 | 26.2505 | 17.9662 | 6.054 | 1.299 | 4.755 | 26.2505 | 4.755 | 17.9662 | 121.5467 | 0
30 | 14.5 | 160.0993 | 25.2213 | 22.1893 | 4.113 | 0 | 4.113 | 25.2213 | 4.113 | 22.1893 | 108.5757 | 0
31 | 15 | 149.0265 | 20.8413 | 26.4226 | 1.163 | 1.568 | -0.405 | 20.8413 | 0 | 26.4226 | 101.7626 | 0
32 | 15.5 | 135.7014 | 23.3259 | 15.8774 | 0.204 | 1.397 | -1.193 | 23.3259 | 0 | 15.8774 | 96.4981 | 0
33 | 16 | 120.6957 | 24.1468 | 15.5327 | 0.576 | 0.661 | -0.085 | 24.1468 | 0 | 15.5327 | 81.0162 | 0
34 | 16.5 | 102.5765 | 26.5049 | 14.2915 | 1.39 | 3.343 | -1.953 | 26.5049 | 0 | 14.2915 | 61.7801 | 0
35 | 17 | 85.618 | 31.8309 | 20.6869 | 1.31 | 6.88 | -5.57 | 31.8309 | 0 | 20.6869 | 33.1002 | 0
36 | 17.5 | 68.1927 | 28.8887 | 25.3824 | 1.678 | 5.627 | -3.949 | 28.8887 | 0 | 25.3824 | 13.9216 | 0
37 | 18 | 51.3375 | 34.9646 | 21.4717 | 0.632 | 12.589 | -11.957 | 34.9646 | 0 | 16.3729 | 0 | 5.0988
38 | 18.5 | 35.0869 | 28.412 | 17.0085 | 0.831 | 9.59 | -8.759 | 28.412 | 0 | 6.6749 | 0 | 10.3336
39 | 19 | 20.4875 | 29.1418 | 17.4288 | 0.613 | 12.484 | -11.871 | 20.4875 | 0 | 0 | 0 | 17.4288
40 | 19.5 | 5.963 | 31.6222 | 23.8478 | 0.021 | 24.192 | -24.171 | 5.963 | 0 | 0 | 0 | 23.8478
41 | 20 | 1.1008 | 41.6363 | 24.2243 | 0 | 39.434 | -39.434 | 1.1008 | 0 | 0 | 0 | 24.2243
42 | 20.5 | 0 | 44.6239 | 26.5121 | 0 | 41.273 | -41.273 | 0 | 0 | 0 | 0 | 26.5121
43 | 21 | 0 | 43.7975 | 24.6838 | 0 | 39.857 | -39.857 | 0 | 0 | 0 | 0 | 24.6838
44 | 21.5 | 0 | 44.5365 | 21.4897 | 0 | 40.056 | -40.056 | 0 | 0 | 0 | 0 | 21.4897
45 | 22 | 0 | 40.8492 | 21.637 | 0 | 34.493 | -34.493 | 0 | 0 | 0 | 0 | 21.637
46 | 22.5 | 0 | 32.7518 | 21.8985 | 0 | 26.905 | -26.905 | 0 | 0 | 0 | 0 | 21.8985
47 | 23 | 0 | 28.4921 | 15.8724 | 0 | 21.676 | -21.676 | 0 | 0 | 0 | 0 | 15.8724
48 | 23.5 | 0 | 21.8917 | 11.7468 | 0 | 16.725 | -16.725 | 0 | 0 | 0 | 0 | 11.7468
TOTAL | kWh/day | 1796.988 | 572.8426 | 360.2937 | 275.858 | 230.3731 | 45.4849 | 357.8252 | 258.7837 | 193.7687 | 986.6104 | 166.5251
Each half-hour is 0.5 h, so daily energy (kWh) = Σ(power in kW) × 0.5.
Trace any input: e.g. cell C5 = SUM of column C on sheet 3 (PV of all 132 connections at 00:00).

## 8. Results & charts
TR1 PV allocation — results
Where the day's PV goes |  |  | How the customers (55) are supplied
Destination | kWh/day | % of PV | Source | kWh/day | % of cust. load
PV → prosumers' own load | 357.8252 | 19.91% | From prosumer PV (day) | 193.7687 | 53.78%
PV → battery storage | 258.7837 | 14.4% | From grid import (night) | 166.5251 | 46.22%
PV → customers | 193.7687 | 10.78% | TOTAL customer load | 360.2937 | 100%
PV → export to grid | 986.6104 | 54.9%
TOTAL (= PV) | 1796.988 | 100%