## 1. Overview
TR6 — Where does the PV energy go?
Prosumers vs. pure customers — every kWh traced from the raw model inputs
Purpose
This workbook accounts for every kWh of PV generated on transformer TR6 over one representative day, and it is fully auditable: nothing is hand-typed except the raw model outputs. Follow the data chain below — each step is a live formula, so changing any raw number updates everything.
The data chain (how each number is built)
Sheet 3 · Raw PV per load | The PV profile of every connection, 48 half-hours. Copied verbatim from TR6_load_PV_48periods.xlsx (sheet PV_generation_kW). Customers = 0.
Sheet 4 · Raw load per load | The load profile of every connection, 48 half-hours, tagged prosumer / customer. Copied from TR6_load_PV_48periods.xlsx (sheet Load_P_kW).
Sheet 5 · Raw batt charge | Charging power of every battery, 48 half-hours. Copied from the rolling dispatch TR6_analysis_data.xlsx (sheet Charge_kW).
Sheet 6 · Raw batt discharge | Discharging power of every battery. Copied from the same run (Discharge_kW).
Sheet 7 · PV allocation | Per half-hour: the five blue inputs are AGGREGATED from sheets 3–6 by SUM / SUMIF; the amber columns then split the PV by the priority rule.
Sheets 1 & 8 · Results | Daily totals (Σ×0.5 h) and shares. Every headline cell links to sheet 7.
The aggregation formulas (sheet 7, per half-hour)
PV (all)
prosumer load
customer load
battery charge
battery discharge
Headline results (all linked live to sheet 7)
Quantity | Value | Unit
Prosumers (PV + battery) | 262 | connections
Pure customers (load only) | 272 | connections
PV generated | 6477.2304 | kWh/day
PV → prosumers' own load (direct) | 1206.3698 | kWh/day
PV → battery storage | 875.6722 | kWh/day
PV → customers | 1009.8668 | kWh/day
PV → export to grid | 3385.3216 | kWh/day
PV share reaching customers | 15.59% | % of PV
Customer load covered by PV | 51.07% | % of customer load
Customer load covered by grid | 48.93% | % of customer load
Colour key & provenance
• LIGHT-BLUE cell = data belonging to a prosumer (its rooftop PV, load, or battery). WHITE = a pure customer (load only). On sheet 7: VIOLET = value aggregated live from the raw sheets (SUM/SUMIF); AMBER = allocation formula; GREEN = daily total (Σ × 0.5 h).
• Per-load PV & load profiles: results/tables/TR6_load_PV_48periods.xlsx (built from OpData.xls).
• Per-battery charge/discharge: TR6_analysis/01_DAILY_ROLLING_DISPATCH/TR6_analysis_data.xlsx (exact-QCP rolling dispatch, RunFOR_Rolling, CPLEX).
• Load classification (PV size > 0 = prosumer): sheet 'Customers' of the load/PV workbook.
• Method note: priority energy allocation per half-hour; downstream network + battery round-trip losses (~3–4% of PV) are not separated out in the per-period disposition.

## 2. Load classification
TR6 load classification — 534 connections
262 prosumers (PV + battery) · 272 pure customers (load only)
ID | Load name | Bus | Phase | PV size (kW) | Type
873 | Load_TR6_F1_10 | TR6_one195 | 3 | 0 | customer
874 | Load_TR6_F1_11 | TR6_one223 | 2 | 0 | customer
875 | Load_TR6_F1_12 | TR6_one235 | 1 | 0 | customer
883 | Load_TR6_F1_2 | TR6_one42 | 2 | 0 | customer
885 | Load_TR6_F1_21 | TR6_one321 | 3 | 0 | customer
886 | Load_TR6_F1_22 | TR6_one328 | 1 | 0 | customer
887 | Load_TR6_F1_23 | TR6_one345 | 1 | 0 | customer
889 | Load_TR6_F1_25 | TR6_one363 | 3 | 0 | customer
890 | Load_TR6_F1_26 | TR6_one366 | 2 | 0 | customer
891 | Load_TR6_F1_27 | TR6_one371 | 3 | 0 | customer
892 | Load_TR6_F1_28 | TR6_one375 | 3 | 0 | customer
893 | Load_TR6_F1_29 | TR6_one410 | 2 | 0 | customer
894 | Load_TR6_F1_3 | TR6_one50 | 1 | 0 | customer
896 | Load_TR6_F1_31 | TR6_one423 | 2 | 0 | customer
898 | Load_TR6_F1_33 | TR6_one469 | 1 | 0 | customer
903 | Load_TR6_F1_38 | TR6_one528 | 3 | 0 | customer
905 | Load_TR6_F1_4 | TR6_one61 | 1 | 0 | customer
906 | Load_TR6_F1_40 | TR6_one544 | 1 | 0 | customer
907 | Load_TR6_F1_41 | TR6_one552 | 2 | 0 | customer
909 | Load_TR6_F1_43 | TR6_one560 | 3 | 0 | customer
911 | Load_TR6_F1_45 | TR6_one585 | 1 | 0 | customer
915 | Load_TR6_F1_49 | TR6_one617 | 1 | 0 | customer
918 | Load_TR6_F1_7 | TR6_one133 | 1 | 0 | customer
921 | Load_TR6_F4_1 | TR6_four50 | 3 | 0 | customer
923 | Load_TR6_F4_100 | TR6_four1252 | 3 | 0 | customer
926 | Load_TR6_F4_13 | TR6_four174 | 3 | 0 | customer
927 | Load_TR6_F4_14 | TR6_four180 | 1 | 0 | customer
932 | Load_TR6_F4_19 | TR6_four265 | 3 | 0 | customer
933 | Load_TR6_F4_2 | TR6_four54 | 3 | 0 | customer
934 | Load_TR6_F4_20 | TR6_four279 | 2 | 0 | customer
937 | Load_TR6_F4_23 | TR6_four292 | 3 | 0 | customer
940 | Load_TR6_F4_26 | TR6_four326 | 1 | 0 | customer
941 | Load_TR6_F4_27 | TR6_four352 | 1 | 0 | customer
945 | Load_TR6_F4_30 | TR6_four368 | 3 | 0 | customer
946 | Load_TR6_F4_31 | TR6_four372 | 3 | 0 | customer
947 | Load_TR6_F4_32 | TR6_four381 | 1 | 0 | customer
952 | Load_TR6_F4_37 | TR6_four437 | 1 | 0 | customer
955 | Load_TR6_F4_4 | TR6_four67 | 1 | 0 | customer
956 | Load_TR6_F4_40 | TR6_four455 | 1 | 0 | customer
957 | Load_TR6_F4_41 | TR6_four459 | 2 | 0 | customer
959 | Load_TR6_F4_43 | TR6_four467 | 3 | 0 | customer
960 | Load_TR6_F4_44 | TR6_four480 | 1 | 0 | customer
961 | Load_TR6_F4_45 | TR6_four532 | 1 | 0 | customer
962 | Load_TR6_F4_46 | TR6_four548 | 2 | 0 | customer
963 | Load_TR6_F4_47 | TR6_four553 | 2 | 0 | customer
965 | Load_TR6_F4_49 | TR6_four562 | 3 | 0 | customer
968 | Load_TR6_F4_51 | TR6_four586 | 2 | 0 | customer
969 | Load_TR6_F4_52 | TR6_four590 | 1 | 0 | customer
970 | Load_TR6_F4_53 | TR6_four593 | 3 | 0 | customer
971 | Load_TR6_F4_54 | TR6_four604 | 1 | 0 | customer
972 | Load_TR6_F4_55 | TR6_four659 | 2 | 0 | customer
975 | Load_TR6_F4_58 | TR6_four704 | 2 | 0 | customer
977 | Load_TR6_F4_6 | TR6_four78 | 2 | 0 | customer
980 | Load_TR6_F4_62 | TR6_four734 | 1 | 0 | customer
981 | Load_TR6_F4_63 | TR6_four763 | 1 | 0 | customer
982 | Load_TR6_F4_64 | TR6_four797 | 3 | 0 | customer
985 | Load_TR6_F4_67 | TR6_four829 | 2 | 0 | customer
988 | Load_TR6_F4_7 | TR6_four98 | 3 | 0 | customer
989 | Load_TR6_F4_70 | TR6_four846 | 3 | 0 | customer
990 | Load_TR6_F4_71 | TR6_four853 | 3 | 0 | customer
991 | Load_TR6_F4_72 | TR6_four854 | 1 | 0 | customer
992 | Load_TR6_F4_73 | TR6_four926 | 2 | 0 | customer
993 | Load_TR6_F4_74 | TR6_four936 | 3 | 0 | customer
994 | Load_TR6_F4_75 | TR6_four950 | 2 | 0 | customer
996 | Load_TR6_F4_77 | TR6_four958 | 3 | 0 | customer
997 | Load_TR6_F4_78 | TR6_four963 | 3 | 0 | customer
999 | Load_TR6_F4_8 | TR6_four104 | 1 | 0 | customer
1004 | Load_TR6_F4_84 | TR6_four1091 | 2 | 0 | customer
1006 | Load_TR6_F4_86 | TR6_four1108 | 3 | 0 | customer
1007 | Load_TR6_F4_87 | TR6_four1123 | 3 | 0 | customer
1008 | Load_TR6_F4_88 | TR6_four1132 | 3 | 0 | customer
1010 | Load_TR6_F4_9 | TR6_four126 | 1 | 0 | customer
1012 | Load_TR6_F4_91 | TR6_four1187 | 1 | 0 | customer
1013 | Load_TR6_F4_92 | TR6_four1193 | 3 | 0 | customer
1014 | Load_TR6_F4_93 | TR6_four1207 | 2 | 0 | customer
1015 | Load_TR6_F4_94 | TR6_four1216 | 3 | 0 | customer
1017 | Load_TR6_F4_96 | TR6_four1226 | 1 | 0 | customer
1018 | Load_TR6_F4_97 | TR6_four1230 | 3 | 0 | customer
1019 | Load_TR6_F4_98 | TR6_four1241 | 3 | 0 | customer
1020 | Load_TR6_F4_99 | TR6_four1244 | 2 | 0 | customer
1021 | Load_TR6_F5_1 | TR6_five58 | 3 | 0 | customer
1023 | Load_TR6_F5_10 | TR6_five147 | 3 | 0 | customer
1026 | Load_TR6_F5_11_dup | TR6_five149_dup | 1 | 0 | customer
1027 | Load_TR6_F5_12 | TR6_five160 | 3 | 0 | customer
1028 | Load_TR6_F5_12_dup | TR6_five160_dup | 3 | 0 | customer
1030 | Load_TR6_F5_13_dup | TR6_five168_dup | 1 | 0 | customer
1033 | Load_TR6_F5_15 | TR6_five177 | 1 | 0 | customer
1034 | Load_TR6_F5_15_dup | TR6_five177_dup | 1 | 0 | customer
1038 | Load_TR6_F5_17_dup | TR6_five194_dup | 3 | 0 | customer
1039 | Load_TR6_F5_18 | TR6_five199 | 3 | 0 | customer
1041 | Load_TR6_F5_19 | TR6_five220 | 3 | 0 | customer
1042 | Load_TR6_F5_19_dup | TR6_five220_dup | 3 | 0 | customer
1022 | Load_TR6_F5_1_dup | TR6_five58_dup | 3 | 0 | customer
1047 | Load_TR6_F5_21 | TR6_five242 | 1 | 0 | customer
1056 | Load_TR6_F5_25_dup | TR6_five303_dup | 2 | 0 | customer
1057 | Load_TR6_F5_26 | TR6_five309 | 3 | 0 | customer
1058 | Load_TR6_F5_26_dup | TR6_five309_dup | 3 | 0 | customer
1059 | Load_TR6_F5_27 | TR6_five324 | 2 | 0 | customer
1060 | Load_TR6_F5_27_dup | TR6_five324_dup | 2 | 0 | customer
1061 | Load_TR6_F5_28 | TR6_five345 | 1 | 0 | customer
1062 | Load_TR6_F5_28_dup | TR6_five345_dup | 1 | 0 | customer
1063 | Load_TR6_F5_29 | TR6_five355 | 1 | 0 | customer
1064 | Load_TR6_F5_29_dup | TR6_five355_dup | 1 | 0 | customer
1070 | Load_TR6_F5_31_dup | TR6_five421_dup | 1 | 0 | customer
1071 | Load_TR6_F5_32 | TR6_five445 | 3 | 0 | customer
1073 | Load_TR6_F5_33 | TR6_five451 | 1 | 0 | customer
1074 | Load_TR6_F5_33_dup | TR6_five451_dup | 1 | 0 | customer
1076 | Load_TR6_F5_34_dup | TR6_five457_dup | 2 | 0 | customer
1077 | Load_TR6_F5_35 | TR6_five466 | 1 | 0 | customer
1078 | Load_TR6_F5_35_dup | TR6_five466_dup | 1 | 0 | customer
1079 | Load_TR6_F5_36 | TR6_five472 | 1 | 0 | customer
1080 | Load_TR6_F5_36_dup | TR6_five472_dup | 1 | 0 | customer
1081 | Load_TR6_F5_37 | TR6_five488 | 2 | 0 | customer
1082 | Load_TR6_F5_37_dup | TR6_five488_dup | 2 | 0 | customer
1084 | Load_TR6_F5_38_dup | TR6_five494_dup | 2 | 0 | customer
1086 | Load_TR6_F5_39_dup | TR6_five499_dup | 2 | 0 | customer
1087 | Load_TR6_F5_4 | TR6_five92 | 1 | 0 | customer
1089 | Load_TR6_F5_40 | TR6_five512 | 1 | 0 | customer
1097 | Load_TR6_F5_44 | TR6_five540 | 1 | 0 | customer
1098 | Load_TR6_F5_44_dup | TR6_five540_dup | 1 | 0 | customer
1099 | Load_TR6_F5_45 | TR6_five545 | 2 | 0 | customer
1100 | Load_TR6_F5_45_dup | TR6_five545_dup | 2 | 0 | customer
1102 | Load_TR6_F5_46_dup | TR6_five551_dup | 3 | 0 | customer
1104 | Load_TR6_F5_47_dup | TR6_five585_dup | 1 | 0 | customer
1105 | Load_TR6_F5_48 | TR6_five588 | 1 | 0 | customer
1107 | Load_TR6_F5_49 | TR6_five631 | 2 | 0 | customer
1108 | Load_TR6_F5_49_dup | TR6_five631_dup | 2 | 0 | customer
1109 | Load_TR6_F5_5 | TR6_five108 | 2 | 0 | customer
1112 | Load_TR6_F5_50_dup | TR6_five649_dup | 1 | 0 | customer
1115 | Load_TR6_F5_52 | TR6_five670 | 3 | 0 | customer
1117 | Load_TR6_F5_53 | TR6_five685 | 2 | 0 | customer
1118 | Load_TR6_F5_53_dup | TR6_five685_dup | 2 | 0 | customer
1119 | Load_TR6_F5_54 | TR6_five695 | 1 | 0 | customer
1120 | Load_TR6_F5_54_dup | TR6_five695_dup | 1 | 0 | customer
1122 | Load_TR6_F5_55_dup | TR6_five704_dup | 1 | 0 | customer
1123 | Load_TR6_F5_56 | TR6_five719 | 1 | 0 | customer
1124 | Load_TR6_F5_56_dup | TR6_five719_dup | 1 | 0 | customer
1126 | Load_TR6_F5_57_dup | TR6_five733_dup | 3 | 0 | customer
1130 | Load_TR6_F5_59_dup | TR6_five748_dup | 2 | 0 | customer
1131 | Load_TR6_F5_6 | TR6_five117 | 2 | 0 | customer
1134 | Load_TR6_F5_60_dup | TR6_five750_dup | 2 | 0 | customer
1135 | Load_TR6_F5_61 | TR6_five778 | 2 | 0 | customer
1138 | Load_TR6_F5_62_dup | TR6_five793_dup | 1 | 0 | customer
1139 | Load_TR6_F5_63 | TR6_five799 | 3 | 0 | customer
1140 | Load_TR6_F5_63_dup | TR6_five799_dup | 3 | 0 | customer
1141 | Load_TR6_F5_64 | TR6_five801 | 3 | 0 | customer
1142 | Load_TR6_F5_64_dup | TR6_five801_dup | 3 | 0 | customer
1143 | Load_TR6_F5_65 | TR6_five809 | 2 | 0 | customer
1144 | Load_TR6_F5_65_dup | TR6_five809_dup | 2 | 0 | customer
1145 | Load_TR6_F5_66 | TR6_five831 | 3 | 0 | customer
1146 | Load_TR6_F5_66_dup | TR6_five831_dup | 3 | 0 | customer
1148 | Load_TR6_F5_67_dup | TR6_five881_dup | 3 | 0 | customer
1150 | Load_TR6_F5_68_dup | TR6_five905_dup | 2 | 0 | customer
1156 | Load_TR6_F5_9_dup | TR6_five129_dup | 3 | 0 | customer
1160 | Load_TR6_F6_10 | TR6_six154 | 3 | 0 | customer
1165 | Load_TR6_F6_11_tri | TR6_six173_tri | 3 | 0 | customer
1166 | Load_TR6_F6_12 | TR6_six186 | 1 | 0 | customer
1167 | Load_TR6_F6_12_dup | TR6_six186_dup | 1 | 0 | customer
1168 | Load_TR6_F6_12_tri | TR6_six186_tri | 1 | 0 | customer
1171 | Load_TR6_F6_13_tri | TR6_six191_tri | 2 | 0 | customer
1176 | Load_TR6_F6_15_dup | TR6_six232_dup | 3 | 0 | customer
1177 | Load_TR6_F6_15_tri | TR6_six232_tri | 3 | 0 | customer
1179 | Load_TR6_F6_16_dup | TR6_six238_dup | 1 | 0 | customer
1181 | Load_TR6_F6_17 | TR6_six249 | 2 | 0 | customer
1183 | Load_TR6_F6_17_tri | TR6_six249_tri | 2 | 0 | customer
1184 | Load_TR6_F6_18 | TR6_six254 | 2 | 0 | customer
1185 | Load_TR6_F6_18_dup | TR6_six254_dup | 2 | 0 | customer
1186 | Load_TR6_F6_18_tri | TR6_six254_tri | 2 | 0 | customer
1187 | Load_TR6_F6_19 | TR6_six269 | 3 | 0 | customer
1188 | Load_TR6_F6_19_dup | TR6_six269_dup | 3 | 0 | customer
1159 | Load_TR6_F6_1_tri | TR6_six64_tri | 1 | 0 | customer
1194 | Load_TR6_F6_20_dup | TR6_six289_dup | 3 | 0 | customer
1196 | Load_TR6_F6_21 | TR6_six317 | 3 | 0 | customer
1199 | Load_TR6_F6_22 | TR6_six326 | 1 | 0 | customer
1200 | Load_TR6_F6_22_dup | TR6_six326_dup | 1 | 0 | customer
1203 | Load_TR6_F6_23_dup | TR6_six329_dup | 1 | 0 | customer
1206 | Load_TR6_F6_24_dup | TR6_six342_dup | 1 | 0 | customer
1207 | Load_TR6_F6_24_tri | TR6_six342_tri | 1 | 0 | customer
1208 | Load_TR6_F6_25 | TR6_six349 | 1 | 0 | customer
1211 | Load_TR6_F6_26 | TR6_six350 | 2 | 0 | customer
1214 | Load_TR6_F6_27 | TR6_six362 | 3 | 0 | customer
1215 | Load_TR6_F6_27_dup | TR6_six362_dup | 3 | 0 | customer
1217 | Load_TR6_F6_28 | TR6_six365 | 3 | 0 | customer
1218 | Load_TR6_F6_28_dup | TR6_six365_dup | 3 | 0 | customer
1220 | Load_TR6_F6_29 | TR6_six378 | 1 | 0 | customer
1223 | Load_TR6_F6_3 | TR6_six75 | 1 | 0 | customer
1227 | Load_TR6_F6_30_dup | TR6_six385_dup | 2 | 0 | customer
1229 | Load_TR6_F6_31 | TR6_six387 | 1 | 0 | customer
1231 | Load_TR6_F6_31_tri | TR6_six387_tri | 1 | 0 | customer
1233 | Load_TR6_F6_32_dup | TR6_six392_dup | 3 | 0 | customer
1234 | Load_TR6_F6_32_tri | TR6_six392_tri | 3 | 0 | customer
1235 | Load_TR6_F6_33 | TR6_six410 | 1 | 0 | customer
1236 | Load_TR6_F6_33_dup | TR6_six410_dup | 1 | 0 | customer
1238 | Load_TR6_F6_34 | TR6_six431 | 3 | 0 | customer
1241 | Load_TR6_F6_35 | TR6_six441 | 1 | 0 | customer
1244 | Load_TR6_F6_36 | TR6_six484 | 2 | 0 | customer
1246 | Load_TR6_F6_36_tri | TR6_six484_tri | 2 | 0 | customer
1247 | Load_TR6_F6_37 | TR6_six501 | 1 | 0 | customer
1249 | Load_TR6_F6_37_tri | TR6_six501_tri | 1 | 0 | customer
1250 | Load_TR6_F6_38 | TR6_six512 | 2 | 0 | customer
1253 | Load_TR6_F6_39 | TR6_six518 | 2 | 0 | customer
1254 | Load_TR6_F6_39_dup | TR6_six518_dup | 2 | 0 | customer
1255 | Load_TR6_F6_39_tri | TR6_six518_tri | 2 | 0 | customer
1224 | Load_TR6_F6_3_dup | TR6_six75_dup | 1 | 0 | customer
1259 | Load_TR6_F6_40 | TR6_six523 | 3 | 0 | customer
1261 | Load_TR6_F6_40_tri | TR6_six523_tri | 3 | 0 | customer
1262 | Load_TR6_F6_41 | TR6_six534 | 2 | 0 | customer
1263 | Load_TR6_F6_41_dup | TR6_six534_dup | 2 | 0 | customer
1264 | Load_TR6_F6_41_tri | TR6_six534_tri | 2 | 0 | customer
1266 | Load_TR6_F6_42_dup | TR6_six571_dup | 3 | 0 | customer
1268 | Load_TR6_F6_43 | TR6_six583 | 1 | 0 | customer
1270 | Load_TR6_F6_43_tri | TR6_six583_tri | 1 | 0 | customer
1273 | Load_TR6_F6_44_tri | TR6_six591_tri | 3 | 0 | customer
1274 | Load_TR6_F6_45 | TR6_six595 | 2 | 0 | customer
1275 | Load_TR6_F6_45_dup | TR6_six595_dup | 2 | 0 | customer
1278 | Load_TR6_F6_46_dup | TR6_six625_dup | 1 | 0 | customer
1279 | Load_TR6_F6_46_tri | TR6_six625_tri | 1 | 0 | customer
1281 | Load_TR6_F6_47_dup | TR6_six643_dup | 1 | 0 | customer
1282 | Load_TR6_F6_47_tri | TR6_six643_tri | 1 | 0 | customer
1285 | Load_TR6_F6_48_tri | TR6_six646_tri | 2 | 0 | customer
1286 | Load_TR6_F6_49 | TR6_six651 | 3 | 0 | customer
1258 | Load_TR6_F6_4_tri | TR6_six82_tri | 1 | 0 | customer
1289 | Load_TR6_F6_5 | TR6_six87 | 1 | 0 | customer
1292 | Load_TR6_F6_50 | TR6_six652 | 1 | 0 | customer
1295 | Load_TR6_F6_51 | TR6_six665 | 2 | 0 | customer
1296 | Load_TR6_F6_51_dup | TR6_six665_dup | 2 | 0 | customer
1299 | Load_TR6_F6_52_dup | TR6_six667_dup | 1 | 0 | customer
1304 | Load_TR6_F6_54 | TR6_six718 | 3 | 0 | customer
1305 | Load_TR6_F6_54_dup | TR6_six718_dup | 3 | 0 | customer
1306 | Load_TR6_F6_54_tri | TR6_six718_tri | 3 | 0 | customer
1308 | Load_TR6_F6_55_dup | TR6_six721_dup | 1 | 0 | customer
1309 | Load_TR6_F6_55_tri | TR6_six721_tri | 1 | 0 | customer
1312 | Load_TR6_F6_56_tri | TR6_six723_tri | 2 | 0 | customer
1318 | Load_TR6_F6_58_tri | TR6_six758_tri | 2 | 0 | customer
1319 | Load_TR6_F6_59 | TR6_six784 | 2 | 0 | customer
1291 | Load_TR6_F6_5_tri | TR6_six87_tri | 1 | 0 | customer
1325 | Load_TR6_F6_60 | TR6_six799 | 2 | 0 | customer
1326 | Load_TR6_F6_60_dup | TR6_six799_dup | 2 | 0 | customer
1332 | Load_TR6_F6_62_dup | TR6_six807_dup | 1 | 0 | customer
1333 | Load_TR6_F6_62_tri | TR6_six807_tri | 1 | 0 | customer
1338 | Load_TR6_F6_64_dup | TR6_six852_dup | 2 | 0 | customer
1339 | Load_TR6_F6_64_tri | TR6_six852_tri | 2 | 0 | customer
1342 | Load_TR6_F6_65_tri | TR6_six860_tri | 3 | 0 | customer
1344 | Load_TR6_F6_66_dup | TR6_six869_dup | 3 | 0 | customer
1347 | Load_TR6_F6_67_dup | TR6_six885_dup | 1 | 0 | customer
1350 | Load_TR6_F6_68_dup | TR6_six894_dup | 2 | 0 | customer
1352 | Load_TR6_F6_69 | TR6_six909 | 3 | 0 | customer
1353 | Load_TR6_F6_69_dup | TR6_six909_dup | 3 | 0 | customer
1354 | Load_TR6_F6_69_tri | TR6_six909_tri | 3 | 0 | customer
1324 | Load_TR6_F6_6_tri | TR6_six90_tri | 2 | 0 | customer
1355 | Load_TR6_F6_7 | TR6_six105 | 1 | 0 | customer
1359 | Load_TR6_F6_70_dup | TR6_six914_dup | 1 | 0 | customer
1362 | Load_TR6_F6_71_dup | TR6_six921_dup | 2 | 0 | customer
1363 | Load_TR6_F6_71_tri | TR6_six921_tri | 2 | 0 | customer
1364 | Load_TR6_F6_72 | TR6_six929 | 1 | 0 | customer
1365 | Load_TR6_F6_72_dup | TR6_six929_dup | 1 | 0 | customer
1367 | Load_TR6_F6_73 | TR6_six938 | 1 | 0 | customer
1370 | Load_TR6_F6_74 | TR6_six945 | 3 | 0 | customer
1372 | Load_TR6_F6_74_tri | TR6_six945_tri | 3 | 0 | customer
1375 | Load_TR6_F6_75_tri | TR6_six952_tri | 1 | 0 | customer
1377 | Load_TR6_F6_76_dup | TR6_six967_dup | 2 | 0 | customer
1379 | Load_TR6_F6_77 | TR6_six974 | 3 | 0 | customer
1383 | Load_TR6_F6_78_dup | TR6_six979_dup | 1 | 0 | customer
1384 | Load_TR6_F6_78_tri | TR6_six979_tri | 1 | 0 | customer
1388 | Load_TR6_F6_8 | TR6_six111 | 3 | 0 | customer
1393 | Load_TR6_F6_80_tri | TR6_six1006_tri | 3 | 0 | customer
1398 | Load_TR6_F6_82_dup | TR6_six1025_dup | 2 | 0 | customer
1399 | Load_TR6_F6_82_tri | TR6_six1025_tri | 2 | 0 | customer
1401 | Load_TR6_F6_83_dup | TR6_six1064_dup | 3 | 0 | customer
1403 | Load_TR6_F6_9 | TR6_six128 | 2 | 0 | customer
1404 | Load_TR6_F6_9_dup | TR6_six128_dup | 2 | 0 | customer
1405 | Load_TR6_F6_9_tri | TR6_six128_tri | 2 | 0 | customer
872 | Load_TR6_F1_1 | TR6_one38 | 2 | 3 | prosumer
876 | Load_TR6_F1_13 | TR6_one242 | 2 | 3 | prosumer
877 | Load_TR6_F1_14 | TR6_one252 | 3 | 2 | prosumer
878 | Load_TR6_F1_15 | TR6_one260 | 3 | 2 | prosumer
879 | Load_TR6_F1_16 | TR6_one280 | 1 | 2.5 | prosumer
880 | Load_TR6_F1_17 | TR6_one287 | 2 | 3 | prosumer
881 | Load_TR6_F1_18 | TR6_one299 | 2 | 2.5 | prosumer
882 | Load_TR6_F1_19 | TR6_one313 | 1 | 3.5 | prosumer
884 | Load_TR6_F1_20 | TR6_one320 | 2 | 3.5 | prosumer
888 | Load_TR6_F1_24 | TR6_one346 | 3 | 3 | prosumer
895 | Load_TR6_F1_30 | TR6_one416 | 3 | 4 | prosumer
897 | Load_TR6_F1_32 | TR6_one446 | 2 | 4 | prosumer
899 | Load_TR6_F1_34 | TR6_one477 | 1 | 2 | prosumer
900 | Load_TR6_F1_35 | TR6_one480 | 1 | 4 | prosumer
901 | Load_TR6_F1_36 | TR6_one482 | 2 | 3.5 | prosumer
902 | Load_TR6_F1_37 | TR6_one521 | 3 | 2.5 | prosumer
904 | Load_TR6_F1_39 | TR6_one537 | 1 | 3.5 | prosumer
908 | Load_TR6_F1_42 | TR6_one559 | 3 | 3 | prosumer
910 | Load_TR6_F1_44 | TR6_one570 | 2 | 4 | prosumer
912 | Load_TR6_F1_46 | TR6_one590 | 1 | 2.5 | prosumer
913 | Load_TR6_F1_47 | TR6_one605 | 1 | 2 | prosumer
914 | Load_TR6_F1_48 | TR6_one614 | 2 | 2.5 | prosumer
916 | Load_TR6_F1_5 | TR6_one73 | 1 | 2 | prosumer
917 | Load_TR6_F1_6 | TR6_one76 | 1 | 4 | prosumer
919 | Load_TR6_F1_8 | TR6_one137 | 1 | 4 | prosumer
920 | Load_TR6_F1_9 | TR6_one176 | 1 | 3 | prosumer
922 | Load_TR6_F4_10 | TR6_four149 | 2 | 3.5 | prosumer
924 | Load_TR6_F4_11 | TR6_four163 | 3 | 2 | prosumer
925 | Load_TR6_F4_12 | TR6_four171 | 1 | 4 | prosumer
928 | Load_TR6_F4_15 | TR6_four184 | 2 | 2.5 | prosumer
929 | Load_TR6_F4_16 | TR6_four200 | 1 | 2.5 | prosumer
930 | Load_TR6_F4_17 | TR6_four239 | 1 | 2 | prosumer
931 | Load_TR6_F4_18 | TR6_four259 | 2 | 4 | prosumer
935 | Load_TR6_F4_21 | TR6_four288 | 2 | 2 | prosumer
936 | Load_TR6_F4_22 | TR6_four289 | 2 | 3.5 | prosumer
938 | Load_TR6_F4_24 | TR6_four301 | 3 | 3 | prosumer
939 | Load_TR6_F4_25 | TR6_four317 | 2 | 2.5 | prosumer
942 | Load_TR6_F4_28 | TR6_four354 | 2 | 3.5 | prosumer
943 | Load_TR6_F4_29 | TR6_four358 | 3 | 4 | prosumer
944 | Load_TR6_F4_3 | TR6_four65 | 2 | 4 | prosumer
948 | Load_TR6_F4_33 | TR6_four384 | 2 | 2.5 | prosumer
949 | Load_TR6_F4_34 | TR6_four385 | 1 | 2.5 | prosumer
950 | Load_TR6_F4_35 | TR6_four396 | 2 | 1.5 | prosumer
951 | Load_TR6_F4_36 | TR6_four423 | 3 | 3 | prosumer
953 | Load_TR6_F4_38 | TR6_four446 | 2 | 3.5 | prosumer
954 | Load_TR6_F4_39 | TR6_four451 | 3 | 2 | prosumer
958 | Load_TR6_F4_42 | TR6_four466 | 3 | 2 | prosumer
964 | Load_TR6_F4_48 | TR6_four558 | 3 | 2 | prosumer
966 | Load_TR6_F4_5 | TR6_four70 | 2 | 4 | prosumer
967 | Load_TR6_F4_50 | TR6_four573 | 1 | 3 | prosumer
973 | Load_TR6_F4_56 | TR6_four664 | 1 | 3 | prosumer
974 | Load_TR6_F4_57 | TR6_four675 | 3 | 4 | prosumer
976 | Load_TR6_F4_59 | TR6_four710 | 3 | 4 | prosumer
978 | Load_TR6_F4_60 | TR6_four727 | 2 | 3.5 | prosumer
979 | Load_TR6_F4_61 | TR6_four732 | 2 | 4 | prosumer
983 | Load_TR6_F4_65 | TR6_four818 | 2 | 4 | prosumer
984 | Load_TR6_F4_66 | TR6_four821 | 1 | 2.5 | prosumer
986 | Load_TR6_F4_68 | TR6_four832 | 1 | 3 | prosumer
987 | Load_TR6_F4_69 | TR6_four840 | 1 | 2 | prosumer
995 | Load_TR6_F4_76 | TR6_four957 | 1 | 1.5 | prosumer
998 | Load_TR6_F4_79 | TR6_four978 | 1 | 3.5 | prosumer
1000 | Load_TR6_F4_80 | TR6_four988 | 1 | 2 | prosumer
1001 | Load_TR6_F4_81 | TR6_four1013 | 2 | 2 | prosumer
1002 | Load_TR6_F4_82 | TR6_four1027 | 1 | 1.5 | prosumer
1003 | Load_TR6_F4_83 | TR6_four1063 | 3 | 1.5 | prosumer
1005 | Load_TR6_F4_85 | TR6_four1103 | 3 | 2.5 | prosumer
1009 | Load_TR6_F4_89 | TR6_four1140 | 1 | 2 | prosumer
1011 | Load_TR6_F4_90 | TR6_four1152 | 2 | 2.5 | prosumer
1016 | Load_TR6_F4_95 | TR6_four1220 | 3 | 4 | prosumer
1024 | Load_TR6_F5_10_dup | TR6_five147_dup | 3 | 4 | prosumer
1025 | Load_TR6_F5_11 | TR6_five149 | 1 | 3.5 | prosumer
1029 | Load_TR6_F5_13 | TR6_five168 | 1 | 4 | prosumer
1031 | Load_TR6_F5_14 | TR6_five170 | 1 | 4 | prosumer
1032 | Load_TR6_F5_14_dup | TR6_five170_dup | 1 | 4 | prosumer
1035 | Load_TR6_F5_16 | TR6_five186 | 3 | 3 | prosumer
1036 | Load_TR6_F5_16_dup | TR6_five186_dup | 3 | 1.5 | prosumer
1037 | Load_TR6_F5_17 | TR6_five194 | 3 | 3 | prosumer
1040 | Load_TR6_F5_18_dup | TR6_five199_dup | 3 | 2.5 | prosumer
1043 | Load_TR6_F5_2 | TR6_five67 | 3 | 4 | prosumer
1045 | Load_TR6_F5_20 | TR6_five223 | 1 | 1.5 | prosumer
1046 | Load_TR6_F5_20_dup | TR6_five223_dup | 1 | 4 | prosumer
1048 | Load_TR6_F5_21_dup | TR6_five242_dup | 1 | 3.5 | prosumer
1049 | Load_TR6_F5_22 | TR6_five243 | 2 | 2 | prosumer
1050 | Load_TR6_F5_22_dup | TR6_five243_dup | 2 | 2 | prosumer
1051 | Load_TR6_F5_23 | TR6_five284 | 3 | 3.5 | prosumer
1052 | Load_TR6_F5_23_dup | TR6_five284_dup | 3 | 3.5 | prosumer
1053 | Load_TR6_F5_24 | TR6_five285 | 2 | 2 | prosumer
1054 | Load_TR6_F5_24_dup | TR6_five285_dup | 2 | 2 | prosumer
1055 | Load_TR6_F5_25 | TR6_five303 | 2 | 3 | prosumer
1044 | Load_TR6_F5_2_dup | TR6_five67_dup | 3 | 4 | prosumer
1065 | Load_TR6_F5_3 | TR6_five78 | 1 | 2.5 | prosumer
1067 | Load_TR6_F5_30 | TR6_five394 | 3 | 4 | prosumer
1068 | Load_TR6_F5_30_dup | TR6_five394_dup | 3 | 2.5 | prosumer
1069 | Load_TR6_F5_31 | TR6_five421 | 1 | 3 | prosumer
1072 | Load_TR6_F5_32_dup | TR6_five445_dup | 3 | 3.5 | prosumer
1075 | Load_TR6_F5_34 | TR6_five457 | 2 | 3 | prosumer
1083 | Load_TR6_F5_38 | TR6_five494 | 2 | 2 | prosumer
1085 | Load_TR6_F5_39 | TR6_five499 | 2 | 3 | prosumer
1066 | Load_TR6_F5_3_dup | TR6_five78_dup | 1 | 4 | prosumer
1090 | Load_TR6_F5_40_dup | TR6_five512_dup | 1 | 4 | prosumer
1091 | Load_TR6_F5_41 | TR6_five513 | 2 | 4 | prosumer
1092 | Load_TR6_F5_41_dup | TR6_five513_dup | 2 | 4 | prosumer
1093 | Load_TR6_F5_42 | TR6_five520 | 3 | 4 | prosumer
1094 | Load_TR6_F5_42_dup | TR6_five520_dup | 3 | 3 | prosumer
1095 | Load_TR6_F5_43 | TR6_five537 | 3 | 2 | prosumer
1096 | Load_TR6_F5_43_dup | TR6_five537_dup | 3 | 4 | prosumer
1101 | Load_TR6_F5_46 | TR6_five551 | 3 | 4 | prosumer
1103 | Load_TR6_F5_47 | TR6_five585 | 1 | 4 | prosumer
1106 | Load_TR6_F5_48_dup | TR6_five588_dup | 1 | 2 | prosumer
1088 | Load_TR6_F5_4_dup | TR6_five92_dup | 1 | 4 | prosumer
1111 | Load_TR6_F5_50 | TR6_five649 | 1 | 1 | prosumer
1113 | Load_TR6_F5_51 | TR6_five663 | 3 | 3.5 | prosumer
1114 | Load_TR6_F5_51_dup | TR6_five663_dup | 3 | 4 | prosumer
1116 | Load_TR6_F5_52_dup | TR6_five670_dup | 3 | 3 | prosumer
1121 | Load_TR6_F5_55 | TR6_five704 | 1 | 3 | prosumer
1125 | Load_TR6_F5_57 | TR6_five733 | 3 | 2.5 | prosumer
1127 | Load_TR6_F5_58 | TR6_five735 | 1 | 4 | prosumer
1128 | Load_TR6_F5_58_dup | TR6_five735_dup | 1 | 1.5 | prosumer
1129 | Load_TR6_F5_59 | TR6_five748 | 2 | 3 | prosumer
1110 | Load_TR6_F5_5_dup | TR6_five108_dup | 2 | 2 | prosumer
1133 | Load_TR6_F5_60 | TR6_five750 | 2 | 1.5 | prosumer
1136 | Load_TR6_F5_61_dup | TR6_five778_dup | 2 | 4 | prosumer
1137 | Load_TR6_F5_62 | TR6_five793 | 1 | 4 | prosumer
1147 | Load_TR6_F5_67 | TR6_five881 | 3 | 3 | prosumer
1149 | Load_TR6_F5_68 | TR6_five905 | 2 | 2.5 | prosumer
1132 | Load_TR6_F5_6_dup | TR6_five117_dup | 2 | 4 | prosumer
1151 | Load_TR6_F5_7 | TR6_five118 | 2 | 3.5 | prosumer
1152 | Load_TR6_F5_7_dup | TR6_five118_dup | 2 | 2.5 | prosumer
1153 | Load_TR6_F5_8 | TR6_five123 | 2 | 2.5 | prosumer
1154 | Load_TR6_F5_8_dup | TR6_five123_dup | 2 | 4 | prosumer
1155 | Load_TR6_F5_9 | TR6_five129 | 3 | 2 | prosumer
1157 | Load_TR6_F6_1 | TR6_six64 | 1 | 3.5 | prosumer
1161 | Load_TR6_F6_10_dup | TR6_six154_dup | 3 | 3 | prosumer
1162 | Load_TR6_F6_10_tri | TR6_six154_tri | 3 | 3 | prosumer
1163 | Load_TR6_F6_11 | TR6_six173 | 3 | 4 | prosumer
1164 | Load_TR6_F6_11_dup | TR6_six173_dup | 3 | 2.5 | prosumer
1169 | Load_TR6_F6_13 | TR6_six191 | 2 | 4 | prosumer
1170 | Load_TR6_F6_13_dup | TR6_six191_dup | 2 | 4 | prosumer
1172 | Load_TR6_F6_14 | TR6_six203 | 1 | 4 | prosumer
1173 | Load_TR6_F6_14_dup | TR6_six203_dup | 1 | 3 | prosumer
1174 | Load_TR6_F6_14_tri | TR6_six203_tri | 1 | 4 | prosumer
1175 | Load_TR6_F6_15 | TR6_six232 | 3 | 4 | prosumer
1178 | Load_TR6_F6_16 | TR6_six238 | 1 | 4 | prosumer
1180 | Load_TR6_F6_16_tri | TR6_six238_tri | 1 | 2 | prosumer
1182 | Load_TR6_F6_17_dup | TR6_six249_dup | 2 | 4 | prosumer
1189 | Load_TR6_F6_19_tri | TR6_six269_tri | 3 | 4 | prosumer
1158 | Load_TR6_F6_1_dup | TR6_six64_dup | 1 | 1.5 | prosumer
1190 | Load_TR6_F6_2 | TR6_six68 | 3 | 3 | prosumer
1193 | Load_TR6_F6_20 | TR6_six289 | 3 | 4 | prosumer
1195 | Load_TR6_F6_20_tri | TR6_six289_tri | 3 | 4 | prosumer
1197 | Load_TR6_F6_21_dup | TR6_six317_dup | 3 | 3 | prosumer
1198 | Load_TR6_F6_21_tri | TR6_six317_tri | 3 | 2.5 | prosumer
1201 | Load_TR6_F6_22_tri | TR6_six326_tri | 1 | 1.5 | prosumer
1202 | Load_TR6_F6_23 | TR6_six329 | 1 | 3 | prosumer
1204 | Load_TR6_F6_23_tri | TR6_six329_tri | 1 | 2 | prosumer
1205 | Load_TR6_F6_24 | TR6_six342 | 1 | 1.5 | prosumer
1209 | Load_TR6_F6_25_dup | TR6_six349_dup | 1 | 4 | prosumer
1210 | Load_TR6_F6_25_tri | TR6_six349_tri | 1 | 2 | prosumer
1212 | Load_TR6_F6_26_dup | TR6_six350_dup | 2 | 3 | prosumer
1213 | Load_TR6_F6_26_tri | TR6_six350_tri | 2 | 2.5 | prosumer
1216 | Load_TR6_F6_27_tri | TR6_six362_tri | 3 | 1.5 | prosumer
1219 | Load_TR6_F6_28_tri | TR6_six365_tri | 3 | 2.5 | prosumer
1221 | Load_TR6_F6_29_dup | TR6_six378_dup | 1 | 1.5 | prosumer
1222 | Load_TR6_F6_29_tri | TR6_six378_tri | 1 | 2 | prosumer
1191 | Load_TR6_F6_2_dup | TR6_six68_dup | 3 | 4 | prosumer
1192 | Load_TR6_F6_2_tri | TR6_six68_tri | 3 | 4 | prosumer
1226 | Load_TR6_F6_30 | TR6_six385 | 2 | 2 | prosumer
1228 | Load_TR6_F6_30_tri | TR6_six385_tri | 2 | 1.5 | prosumer
1230 | Load_TR6_F6_31_dup | TR6_six387_dup | 1 | 1.5 | prosumer
1232 | Load_TR6_F6_32 | TR6_six392 | 3 | 2.5 | prosumer
1237 | Load_TR6_F6_33_tri | TR6_six410_tri | 1 | 4 | prosumer
1239 | Load_TR6_F6_34_dup | TR6_six431_dup | 3 | 3 | prosumer
1240 | Load_TR6_F6_34_tri | TR6_six431_tri | 3 | 1.5 | prosumer
1242 | Load_TR6_F6_35_dup | TR6_six441_dup | 1 | 3 | prosumer
1243 | Load_TR6_F6_35_tri | TR6_six441_tri | 1 | 3.5 | prosumer
1245 | Load_TR6_F6_36_dup | TR6_six484_dup | 2 | 4 | prosumer
1248 | Load_TR6_F6_37_dup | TR6_six501_dup | 1 | 1.5 | prosumer
1251 | Load_TR6_F6_38_dup | TR6_six512_dup | 2 | 3 | prosumer
1252 | Load_TR6_F6_38_tri | TR6_six512_tri | 2 | 4 | prosumer
1225 | Load_TR6_F6_3_tri | TR6_six75_tri | 1 | 2 | prosumer
1256 | Load_TR6_F6_4 | TR6_six82 | 1 | 3.5 | prosumer
1260 | Load_TR6_F6_40_dup | TR6_six523_dup | 3 | 4 | prosumer
1265 | Load_TR6_F6_42 | TR6_six571 | 3 | 4 | prosumer
1267 | Load_TR6_F6_42_tri | TR6_six571_tri | 3 | 1.5 | prosumer
1269 | Load_TR6_F6_43_dup | TR6_six583_dup | 1 | 3 | prosumer
1271 | Load_TR6_F6_44 | TR6_six591 | 3 | 3.5 | prosumer
1272 | Load_TR6_F6_44_dup | TR6_six591_dup | 3 | 2 | prosumer
1276 | Load_TR6_F6_45_tri | TR6_six595_tri | 2 | 4 | prosumer
1277 | Load_TR6_F6_46 | TR6_six625 | 1 | 4 | prosumer
1280 | Load_TR6_F6_47 | TR6_six643 | 1 | 3 | prosumer
1283 | Load_TR6_F6_48 | TR6_six646 | 2 | 2.5 | prosumer
1284 | Load_TR6_F6_48_dup | TR6_six646_dup | 2 | 3 | prosumer
1287 | Load_TR6_F6_49_dup | TR6_six651_dup | 3 | 3 | prosumer
1288 | Load_TR6_F6_49_tri | TR6_six651_tri | 3 | 2.5 | prosumer
1257 | Load_TR6_F6_4_dup | TR6_six82_dup | 1 | 4 | prosumer
1293 | Load_TR6_F6_50_dup | TR6_six652_dup | 1 | 2.5 | prosumer
1294 | Load_TR6_F6_50_tri | TR6_six652_tri | 1 | 2 | prosumer
1297 | Load_TR6_F6_51_tri | TR6_six665_tri | 2 | 4 | prosumer
1298 | Load_TR6_F6_52 | TR6_six667 | 1 | 4 | prosumer
1300 | Load_TR6_F6_52_tri | TR6_six667_tri | 1 | 3 | prosumer
1301 | Load_TR6_F6_53 | TR6_six699 | 3 | 4 | prosumer
1302 | Load_TR6_F6_53_dup | TR6_six699_dup | 3 | 4 | prosumer
1303 | Load_TR6_F6_53_tri | TR6_six699_tri | 3 | 4 | prosumer
1307 | Load_TR6_F6_55 | TR6_six721 | 1 | 2 | prosumer
1310 | Load_TR6_F6_56 | TR6_six723 | 2 | 4 | prosumer
1311 | Load_TR6_F6_56_dup | TR6_six723_dup | 2 | 2.5 | prosumer
1313 | Load_TR6_F6_57 | TR6_six740 | 1 | 4 | prosumer
1314 | Load_TR6_F6_57_dup | TR6_six740_dup | 1 | 4 | prosumer
1315 | Load_TR6_F6_57_tri | TR6_six740_tri | 1 | 2.5 | prosumer
1316 | Load_TR6_F6_58 | TR6_six758 | 2 | 2.5 | prosumer
1317 | Load_TR6_F6_58_dup | TR6_six758_dup | 2 | 3 | prosumer
1320 | Load_TR6_F6_59_dup | TR6_six784_dup | 2 | 4 | prosumer
1321 | Load_TR6_F6_59_tri | TR6_six784_tri | 2 | 3 | prosumer
1290 | Load_TR6_F6_5_dup | TR6_six87_dup | 1 | 4 | prosumer
1322 | Load_TR6_F6_6 | TR6_six90 | 2 | 4 | prosumer
1327 | Load_TR6_F6_60_tri | TR6_six799_tri | 2 | 2.5 | prosumer
1328 | Load_TR6_F6_61 | TR6_six801 | 3 | 3 | prosumer
1329 | Load_TR6_F6_61_dup | TR6_six801_dup | 3 | 3.5 | prosumer
1330 | Load_TR6_F6_61_tri | TR6_six801_tri | 3 | 2.5 | prosumer
1331 | Load_TR6_F6_62 | TR6_six807 | 1 | 4 | prosumer
1334 | Load_TR6_F6_63 | TR6_six844 | 3 | 4 | prosumer
1335 | Load_TR6_F6_63_dup | TR6_six844_dup | 3 | 2 | prosumer
1336 | Load_TR6_F6_63_tri | TR6_six844_tri | 3 | 4 | prosumer
1337 | Load_TR6_F6_64 | TR6_six852 | 2 | 3 | prosumer
1340 | Load_TR6_F6_65 | TR6_six860 | 3 | 4 | prosumer
1341 | Load_TR6_F6_65_dup | TR6_six860_dup | 3 | 4 | prosumer
1343 | Load_TR6_F6_66 | TR6_six869 | 3 | 4 | prosumer
1345 | Load_TR6_F6_66_tri | TR6_six869_tri | 3 | 4 | prosumer
1346 | Load_TR6_F6_67 | TR6_six885 | 1 | 4 | prosumer
1348 | Load_TR6_F6_67_tri | TR6_six885_tri | 1 | 4 | prosumer
1349 | Load_TR6_F6_68 | TR6_six894 | 2 | 1 | prosumer
1351 | Load_TR6_F6_68_tri | TR6_six894_tri | 2 | 3 | prosumer
1323 | Load_TR6_F6_6_dup | TR6_six90_dup | 2 | 4 | prosumer
1358 | Load_TR6_F6_70 | TR6_six914 | 1 | 1.5 | prosumer
1360 | Load_TR6_F6_70_tri | TR6_six914_tri | 1 | 4 | prosumer
1361 | Load_TR6_F6_71 | TR6_six921 | 2 | 4 | prosumer
1366 | Load_TR6_F6_72_tri | TR6_six929_tri | 1 | 4 | prosumer
1368 | Load_TR6_F6_73_dup | TR6_six938_dup | 1 | 4 | prosumer
1369 | Load_TR6_F6_73_tri | TR6_six938_tri | 1 | 2 | prosumer
1371 | Load_TR6_F6_74_dup | TR6_six945_dup | 3 | 2.5 | prosumer
1373 | Load_TR6_F6_75 | TR6_six952 | 1 | 1.5 | prosumer
1374 | Load_TR6_F6_75_dup | TR6_six952_dup | 1 | 3 | prosumer
1376 | Load_TR6_F6_76 | TR6_six967 | 2 | 2.5 | prosumer
1378 | Load_TR6_F6_76_tri | TR6_six967_tri | 2 | 2 | prosumer
1380 | Load_TR6_F6_77_dup | TR6_six974_dup | 3 | 3.5 | prosumer
1381 | Load_TR6_F6_77_tri | TR6_six974_tri | 3 | 2 | prosumer
1382 | Load_TR6_F6_78 | TR6_six979 | 1 | 3 | prosumer
1385 | Load_TR6_F6_79 | TR6_six990 | 2 | 4 | prosumer
1386 | Load_TR6_F6_79_dup | TR6_six990_dup | 2 | 4 | prosumer
1387 | Load_TR6_F6_79_tri | TR6_six990_tri | 2 | 3 | prosumer
1356 | Load_TR6_F6_7_dup | TR6_six105_dup | 1 | 4 | prosumer
1357 | Load_TR6_F6_7_tri | TR6_six105_tri | 1 | 4 | prosumer
1391 | Load_TR6_F6_80 | TR6_six1006 | 3 | 3.5 | prosumer
1392 | Load_TR6_F6_80_dup | TR6_six1006_dup | 3 | 2 | prosumer
1394 | Load_TR6_F6_81 | TR6_six1020 | 1 | 4 | prosumer
1395 | Load_TR6_F6_81_dup | TR6_six1020_dup | 1 | 4 | prosumer
1396 | Load_TR6_F6_81_tri | TR6_six1020_tri | 1 | 4 | prosumer
1397 | Load_TR6_F6_82 | TR6_six1025 | 2 | 4 | prosumer
1400 | Load_TR6_F6_83 | TR6_six1064 | 3 | 3 | prosumer
1402 | Load_TR6_F6_83_tri | TR6_six1064_tri | 3 | 2 | prosumer
1389 | Load_TR6_F6_8_dup | TR6_six111_dup | 3 | 4 | prosumer
1390 | Load_TR6_F6_8_tri | TR6_six111_tri | 3 | 2.5 | prosumer

## 3. Raw PV per load
Raw PV per load
Verbatim copy of PV_generation_kW (TR6_load_PV_48periods.xlsx). One row per connection, 48 half-hours (kW).
Load name | Type | p1 | p2 | p3 | p4 | p5 | p6 | p7 | p8 | p9 | p10 | p11 | p12 | p13 | p14 | p15 | p16 | p17 | p18 | p19 | p20 | p21 | p22 | p23 | p24 | p25 | p26 | p27 | p28 | p29 | p30 | p31 | p32 | p33 | p34 | p35 | p36 | p37 | p38 | p39 | p40 | p41 | p42 | p43 | p44 | p45 | p46 | p47 | p48
Load_TR6_F1_1 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_10 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_11 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_12 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_13 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_14 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_15 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_16 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_17 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_18 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_19 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_2 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_20 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_21 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_22 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_23 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_24 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_25 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_26 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_27 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_28 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_29 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_3 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_30 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_31 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_32 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_33 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_34 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_35 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_36 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_37 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_38 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_39 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_4 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_40 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_41 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_42 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_43 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_44 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_45 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_46 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_47 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_48 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_49 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_5 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_6 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_7 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_8 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F1_9 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_1 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_10 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_100 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_11 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_12 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_13 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_14 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_15 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_16 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_17 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_18 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_19 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_2 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_20 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_21 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_22 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_23 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_24 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_25 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_26 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_27 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_28 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_29 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_3 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_30 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_31 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_32 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_33 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_34 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_35 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_36 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_37 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_38 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_39 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_4 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_40 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_41 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_42 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_43 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_44 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_45 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_46 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_47 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_48 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_49 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_5 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_50 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_51 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_52 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_53 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_54 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_55 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_56 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_57 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_58 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_59 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_6 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_60 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_61 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_62 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_63 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_64 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_65 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_66 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_67 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_68 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_69 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_7 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_70 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_71 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_72 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_73 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_74 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_75 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_76 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_77 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_78 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_79 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_8 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_80 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_81 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_82 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_83 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_84 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_85 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_86 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_87 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_88 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_89 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_9 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_90 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_91 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_92 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_93 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_94 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_95 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_96 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_97 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_98 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F4_99 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_1 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_10 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_10_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_11 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_11_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_12 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_12_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_13 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_13_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_14 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_14_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_15 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_15_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_16 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_16_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_17 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_17_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_18 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_18_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_19 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_19_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_1_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_2 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_20 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_20_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_21 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_21_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_22 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_22_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_23 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_23_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_24 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_24_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_25 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_25_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_26 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_26_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_27 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_27_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_28 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_28_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_29 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_29_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_2_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_3 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_30 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_30_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_31 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_31_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_32 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_32_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_33 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_33_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_34 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_34_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_35 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_35_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_36 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_36_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_37 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_37_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_38 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_38_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_39 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_39_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_3_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_4 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_40 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_40_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_41 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_41_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_42 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_42_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_43 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_43_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_44 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_44_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_45 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_45_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_46 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_46_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_47 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_47_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_48 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_48_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_49 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_49_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_4_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_5 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_50 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0009 | 0.0124 | 0.0581 | 0.1153 | 0.1855 | 0.262 | 0.3394 | 0.4165 | 0.4937 | 0.5661 | 0.6342 | 0.6921 | 0.7416 | 0.785 | 0.8208 | 0.8462 | 0.8574 | 0.8606 | 0.8546 | 0.8343 | 0.8033 | 0.7664 | 0.7195 | 0.6698 | 0.6099 | 0.5425 | 0.461 | 0.3848 | 0.3065 | 0.2307 | 0.1577 | 0.0921 | 0.0268 | 0.0049 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_50_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_51 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_51_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_52 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_52_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_53 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_53_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_54 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_54_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_55 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_55_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_56 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_56_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_57 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_57_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_58 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_58_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_59 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_59_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_5_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_6 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_60 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_60_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_61 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_61_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_62 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_62_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_63 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_63_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_64 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_64_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_65 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_65_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_66 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_66_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_67 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_67_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_68 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_68_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_6_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_7 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_7_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_8 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_8_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_9 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F5_9_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_1 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_10 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_10_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_10_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_11 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_11_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_11_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_12 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_12_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_12_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_13 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_13_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_13_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_14 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_14_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_14_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_15 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_15_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_15_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_16 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_16_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_16_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_17 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_17_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_17_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_18 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_18_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_18_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_19 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_19_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_19_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_1_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_1_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_2 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_20 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_20_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_20_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_21 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_21_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_21_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_22 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_22_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_22_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_23 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_23_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_23_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_24 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_24_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_24_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_25 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_25_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_25_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_26 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_26_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_26_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_27 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_27_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_27_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_28 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_28_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_28_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_29 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_29_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_29_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_2_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_2_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_3 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_30 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_30_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_30_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_31 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_31_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_31_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_32 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_32_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_32_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_33 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_33_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_33_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_34 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_34_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_34_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_35 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_35_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_35_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_36 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_36_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_36_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_37 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_37_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_37_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_38 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_38_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_38_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_39 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_39_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_39_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_3_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_3_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_4 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_40 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_40_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_40_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_41 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_41_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_41_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_42 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_42_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_42_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_43 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_43_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_43_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_44 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_44_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_44_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_45 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_45_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_45_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_46 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_46_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_46_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_47 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_47_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_47_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_48 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_48_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_48_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_49 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_49_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_49_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_4_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_4_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_5 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_50 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_50_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_50_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_51 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_51_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_51_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_52 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_52_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_52_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_53 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_53_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_53_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_54 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_54_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_54_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_55 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_55_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_55_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_56 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_56_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_56_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_57 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_57_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_57_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_58 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_58_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_58_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_59 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_59_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_59_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_5_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_5_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_6 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_60 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_60_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_60_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_61 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_61_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_61_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_62 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_62_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_62_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_63 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_63_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_63_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_64 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_64_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_64_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_65 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_65_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_65_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_66 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_66_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_66_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_67 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_67_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_67_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_68 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0009 | 0.0124 | 0.0581 | 0.1153 | 0.1855 | 0.262 | 0.3394 | 0.4165 | 0.4937 | 0.5661 | 0.6342 | 0.6921 | 0.7416 | 0.785 | 0.8208 | 0.8462 | 0.8574 | 0.8606 | 0.8546 | 0.8343 | 0.8033 | 0.7664 | 0.7195 | 0.6698 | 0.6099 | 0.5425 | 0.461 | 0.3848 | 0.3065 | 0.2307 | 0.1577 | 0.0921 | 0.0268 | 0.0049 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_68_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_68_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_69 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_69_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_69_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_6_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_6_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_7 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_70 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_70_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_70_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_71 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_71_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_71_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_72 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_72_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_72_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_73 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_73_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_73_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_74 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_74_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_74_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_75 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_75_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_75_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_76 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_76_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_76_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_77 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_77_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_77_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_78 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_78_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_78_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_79 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_79_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_79_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_7_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_7_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_8 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_80 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_80_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_80_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_81 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_81_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_81_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_82 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_82_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_82_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_83 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_83_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_83_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_8_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_8_tri | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_9 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_9_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR6_F6_9_tri | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 4. Raw load per load
Raw load per load
Verbatim copy of Load_P_kW (TR6_load_PV_48periods.xlsx), tagged by type. One row per connection, 48 half-hours (kW).
Load name | Type | p1 | p2 | p3 | p4 | p5 | p6 | p7 | p8 | p9 | p10 | p11 | p12 | p13 | p14 | p15 | p16 | p17 | p18 | p19 | p20 | p21 | p22 | p23 | p24 | p25 | p26 | p27 | p28 | p29 | p30 | p31 | p32 | p33 | p34 | p35 | p36 | p37 | p38 | p39 | p40 | p41 | p42 | p43 | p44 | p45 | p46 | p47 | p48
Load_TR6_F1_1 | prosumer | 0.4934 | 0.5503 | 0.1502 | 0.2006 | 0.0804 | 0.2156 | 0.1626 | 0.053 | 0.1968 | 0.1813 | 0.0598 | 0.1968 | 0.053 | 0.2037 | 0.1563 | 1.2638 | 0.9174 | 1.3104 | 0.3169 | 1.2006 | 0.1407 | 0.2127 | 0.0804 | 0.2224 | 0.1557 | 0.1441 | 0.0834 | 0.053 | 0.3009 | 0.0773 | 0.2705 | 0.1181 | 0.2131 | 0.1833 | 0.0872 | 1.4302 | 0.1097 | 0.1994 | 0.3696 | 0.5816 | 1.0333 | 0.6636 | 0.7448 | 0.7112 | 0.6753 | 0.8728 | 0.7942 | 0.1745
Load_TR6_F1_10 | customer | 0.049 | 0.1493 | 0.049 | 0.1525 | 0.1337 | 0.049 | 0.2372 | 0.0539 | 0.1965 | 0.0897 | 0.1733 | 0.2789 | 0.049 | 0.1369 | 0.1493 | 0.1369 | 0.092 | 0.1063 | 0.049 | 0.0848 | 0.1867 | 0.0637 | 0.1125 | 0.1737 | 0.1152 | 0.1363 | 0.1499 | 0.049 | 0.2432 | 0.113 | 0.1962 | 0.1555 | 0.3451 | 0.2335 | 0.2083 | 0.3158 | 1.2965 | 2.925 | 2.2246 | 0.093 | 0.1932 | 0.1223 | 0.0851 | 0.3164 | 0.0783 | 0.1076 | 0.1571 | 0.1584
Load_TR6_F1_11 | customer | 0.2075 | 0.0613 | 0.1564 | 0.1125 | 0.054 | 0.1564 | 0.1125 | 0.054 | 0.054 | 0.2148 | 0.054 | 0.054 | 0.0686 | 1.2785 | 0.8059 | 1.4094 | 0.2674 | 0.1417 | 0.1271 | 0.054 | 0.1344 | 0.1344 | 0.0686 | 0.2002 | 0.4507 | 0.9136 | 0.1611 | 0.1092 | 1.6238 | 0.054 | 0.1929 | 0.0759 | 0.054 | 0.1783 | 0.0906 | 0.054 | 0.2148 | 0.054 | 0.1344 | 0.1344 | 0.0686 | 0.4615 | 0.1703 | 0.5771 | 0.5748 | 0.3317 | 0.2597 | 0.054
Load_TR6_F1_12 | customer | 0.056 | 0.2708 | 0.3491 | 0.4235 | 0.5238 | 0.3304 | 0.0627 | 0.1974 | 0.1294 | 0.2083 | 0.1253 | 0.1638 | 0.1698 | 0.056 | 0.1166 | 0.1436 | 0.1131 | 0.2205 | 0.056 | 0.1772 | 0.0993 | 0.1737 | 0.1436 | 0.1265 | 0.207 | 0.056 | 0.1772 | 0.1986 | 0.1655 | 0.212 | 0.1862 | 0.3676 | 0.198 | 0.1536 | 0.4975 | 0.0827 | 0.2665 | 0.1426 | 0.1485 | 0.4561 | 0.397 | 0.5112 | 0.4744 | 0.3414 | 0.2735 | 0.056 | 0.1301 | 0.1423
Load_TR6_F1_13 | prosumer | 0.1137 | 0.052 | 0.0767 | 0.1506 | 0.052 | 0.1753 | 0.052 | 0.052 | 0.1691 | 0.0582 | 0.052 | 0.204 | 0.1649 | 0.1075 | 0.1198 | 0.052 | 0.126 | 0.1013 | 0.0705 | 0.1568 | 0.0582 | 0.1691 | 0.052 | 0.1753 | 0.052 | 1.1966 | 0.179 | 0.282 | 0.4212 | 0.3033 | 0.3382 | 0.3052 | 0.1878 | 0.3063 | 0.1881 | 1.1062 | 0.1654 | 0.0639 | 0.2378 | 0.2105 | 0.2178 | 0.4339 | 0.3756 | 0.5496 | 0.5912 | 1.4764 | 0.2968 | 0.052
Load_TR6_F1_14 | prosumer | 0.058 | 0.058 | 0.3153 | 0.058 | 0.2895 | 0.0838 | 0.2121 | 0.1612 | 0.1261 | 0.2471 | 0.1261 | 0.058 | 0.0921 | 0.1093 | 0.264 | 0.0921 | 0.243 | 0.7208 | 2.8197 | 3.209 | 0.058 | 0.1268 | 0.251 | 0.0864 | 0.1054 | 0.1843 | 0.2494 | 0.1313 | 0.2787 | 0.1261 | 0.0838 | 0.2705 | 0.0769 | 0.2128 | 0.0924 | 0.2293 | 0.2165 | 0.2124 | 0.3641 | 0.9181 | 0.6759 | 0.5942 | 0.5366 | 0.4876 | 0.5803 | 0.6928 | 0.0731 | 0.3001
Load_TR6_F1_15 | prosumer | 0.1347 | 0.2534 | 0.114 | 0.1577 | 0.264 | 0.0804 | 0.2227 | 0.2284 | 0.0662 | 0.2859 | 0.1501 | 0.2934 | 0.1577 | 0.1224 | 0.0781 | 0.2408 | 0.1875 | 0.0586 | 0.2638 | 0.1041 | 0.2165 | 0.4375 | 1.4191 | 0.191 | 0.3426 | 0.051 | 1.1431 | 0.3049 | 0.3253 | 0.4013 | 0.2412 | 0.2215 | 0.1735 | 0.1915 | 0.4317 | 0.2467 | 0.7772 | 1.628 | 2.1621 | 0.2982 | 0.5995 | 0.527 | 0.4441 | 0.829 | 0.8827 | 2.0801 | 0.2974 | 0.093
Load_TR6_F1_16 | prosumer | 0.2334 | 0.1852 | 0.2129 | 0.055 | 0.1621 | 0.055 | 0.144 | 0.055 | 0.1621 | 0.144 | 0.1621 | 0.144 | 0.055 | 0.055 | 0.3055 | 0.2572 | 0.394 | 0.3684 | 0.1778 | 1.7553 | 0.2833 | 0.5318 | 0.3477 | 0.6459 | 0.6036 | 0.4101 | 0.1353 | 0.1121 | 0.055 | 0.2511 | 0.055 | 0.1949 | 0.173 | 0.1957 | 0.0743 | 0.4301 | 0.9264 | 0.9661 | 0.5346 | 0.3841 | 0.6193 | 0.701 | 1.045 | 0.8667 | 0.9262 | 0.9453 | 0.769 | 0.8348
Load_TR6_F1_17 | prosumer | 0.3081 | 0.053 | 0.1213 | 0.053 | 0.053 | 0.053 | 0.072 | 0.1023 | 0.053 | 0.1213 | 0.053 | 0.0872 | 0.0872 | 0.2733 | 0.2718 | 0.2262 | 0.4611 | 0.3559 | 0.3672 | 0.3342 | 0.8329 | 0.053 | 0.1213 | 0.053 | 0.053 | 0.8113 | 0.6323 | 0.3565 | 1.2115 | 0.3233 | 0.5684 | 0.2755 | 0.0867 | 0.2231 | 1.3347 | 2.3731 | 0.2823 | 0.1684 | 0.5374 | 0.3093 | 0.3344 | 0.1885 | 0.3435 | 0.5619 | 0.0606 | 0.0834 | 0.0909 | 0.0568
Load_TR6_F1_18 | prosumer | 0.2017 | 0.263 | 0.1933 | 0.0601 | 0.1922 | 0.1249 | 0.1476 | 0.1695 | 0.052 | 0.173 | 0.0711 | 0.1273 | 0.1898 | 0.0885 | 0.2168 | 1.8166 | 0.1249 | 1.0638 | 0.1516 | 1.8091 | 0.8484 | 0.7528 | 0.3446 | 0.1737 | 0.3748 | 0.088 | 0.2264 | 0.0814 | 1.0319 | 0.3617 | 0.1403 | 0.2451 | 0.1746 | 0.1953 | 1.0612 | 0.0693 | 0.052 | 0.2333 | 0.1704 | 0.2798 | 0.3059 | 0.3732 | 0.4402 | 0.356 | 0.2014 | 0.1157 | 0.0966 | 0.0995
Load_TR6_F1_19 | prosumer | 0.1035 | 0.2654 | 0.2306 | 0.3837 | 0.5359 | 0.4551 | 0.2618 | 0.2133 | 0.058 | 0.2481 | 0.1685 | 0.0694 | 0.3431 | 0.0621 | 0.1439 | 0.1982 | 0.0887 | 1.642 | 0.1375 | 0.1982 | 0.0934 | 0.2576 | 0.058 | 0.1262 | 0.1894 | 0.1704 | 0.1716 | 0.177 | 0.2396 | 0.1035 | 0.1881 | 0.183 | 0.0746 | 0.2126 | 0.1723 | 0.2102 | 0.2272 | 0.2632 | 0.3686 | 0.4571 | 0.4598 | 0.7487 | 0.4477 | 0.517 | 0.5884 | 0.5126 | 0.7127 | 0.8913
Load_TR6_F1_2 | customer | 0.3128 | 0.2138 | 0.1587 | 0.218 | 0.0641 | 0.0853 | 0.2416 | 0.114 | 0.0909 | 0.2431 | 0.1069 | 0.0853 | 0.1418 | 0.1283 | 0.2556 | 0.057 | 0.3872 | 0.3854 | 0.1717 | 0.5283 | 0.4852 | 0.1802 | 0.2679 | 1.4592 | 0.3151 | 0.5365 | 1.2532 | 0.6265 | 0.1904 | 0.5994 | 0.9086 | 0.2266 | 0.2481 | 1.274 | 0.0683 | 0.3352 | 1.272 | 0.581 | 0.6943 | 1.0124 | 0.9042 | 0.9644 | 0.9368 | 1.0715 | 0.9081 | 0.8938 | 0.7589 | 0.6599
Load_TR6_F1_20 | prosumer | 0.2434 | 0.048 | 0.3266 | 0.1512 | 0.1292 | 0.1422 | 0.0926 | 0.3345 | 0.0987 | 0.1219 | 0.3559 | 0.048 | 0.3454 | 1.3324 | 0.2595 | 0.3751 | 0.4032 | 0.1542 | 0.3525 | 0.1827 | 0.0627 | 0.2704 | 0.0555 | 1.0102 | 0.7943 | 0.048 | 0.3269 | 0.1468 | 0.2585 | 0.1219 | 0.2527 | 0.2 | 0.1306 | 0.3285 | 0.1822 | 0.1622 | 0.3958 | 0.1474 | 0.4719 | 1.5509 | 1.1202 | 0.7108 | 0.2451 | 0.048 | 0.222 | 0.1819 | 0.197 | 0.2519
Load_TR6_F1_21 | customer | 0.1178 | 0.048 | 0.0945 | 0.172 | 0.048 | 0.2185 | 0.048 | 0.141 | 0.1255 | 0.048 | 0.048 | 0.2185 | 0.048 | 0.1488 | 0.1178 | 0.295 | 1.2391 | 0.1437 | 0.3493 | 0.1692 | 2.5814 | 2.7154 | 0.9709 | 0.3105 | 0.2838 | 0.2111 | 0.3605 | 0.4489 | 0.3564 | 0.4553 | 0.5661 | 0.3627 | 1.3259 | 0.2798 | 0.2632 | 0.3048 | 1.9061 | 0.55 | 0.158 | 0.399 | 0.6094 | 0.6103 | 0.7121 | 0.4357 | 0.5659 | 0.4939 | 0.8949 | 0.6401
Load_TR6_F1_22 | customer | 0.2771 | 0.1214 | 0.042 | 0.1498 | 0.1166 | 0.0834 | 0.3151 | 0.042 | 0.2737 | 0.1248 | 0.1411 | 0.2574 | 0.1081 | 0.2904 | 0.179 | 0.1741 | 0.2244 | 0.1613 | 0.0684 | 0.1829 | 0.5711 | 1.435 | 0.5101 | 0.0999 | 1.2203 | 0.9486 | 1.2567 | 0.2652 | 0.1867 | 0.2759 | 0.9716 | 0.3352 | 1.6765 | 1.4487 | 0.5121 | 0.2196 | 0.1996 | 1.5021 | 1.1894 | 0.941 | 2.098 | 0.4672 | 0.4386 | 0.3271 | 0.5303 | 0.3665 | 0.5593 | 0.2375
Load_TR6_F1_23 | customer | 0.5747 | 0.4901 | 0.263 | 0.1803 | 0.3388 | 0.4291 | 0.1738 | 0.059 | 0.1967 | 0.0896 | 0.1355 | 0.1508 | 0.059 | 0.2273 | 0.059 | 0.0705 | 0.5642 | 1.2696 | 0.2566 | 0.1432 | 0.1432 | 0.059 | 0.212 | 0.0743 | 0.0896 | 0.3914 | 0.2205 | 0.2223 | 0.3504 | 0.1366 | 0.1126 | 0.1738 | 0.6006 | 0.1951 | 0.3453 | 0.2317 | 0.1992 | 0.2239 | 0.059 | 0.059 | 0.1967 | 0.0896 | 0.1432 | 0.3017 | 0.3122 | 0.3639 | 0.518 | 0.4149
Load_TR6_F1_24 | prosumer | 0.05 | 0.0948 | 0.1171 | 0.05 | 0.1395 | 0.0724 | 0.05 | 0.05 | 0.1451 | 0.0668 | 0.1339 | 0.078 | 0.05 | 0.1619 | 0.2218 | 0.9834 | 2.0744 | 3.048 | 0.0612 | 0.4452 | 0.05 | 0.1619 | 0.05 | 0.05 | 0.0524 | 0.0566 | 0.7504 | 0.8296 | 0.05 | 0.1003 | 0.1115 | 0.0668 | 0.1451 | 0.05 | 0.1563 | 0.0556 | 0.05 | 0.1619 | 0.05 | 0.1619 | 0.05 | 0.0724 | 0.1395 | 0.05 | 0.0892 | 0.1227 | 0.05 | 0.1619
Load_TR6_F1_25 | customer | 0.05 | 0.1643 | 0.0836 | 0.1172 | 0.1307 | 0.05 | 0.05 | 0.0903 | 0.1576 | 0.05 | 0.1979 | 0.05 | 0.1576 | 0.0903 | 0.0971 | 0.1508 | 0.05 | 0.0567 | 0.1912 | 0.05 | 0.1374 | 0.129 | 0.1728 | 0.2591 | 0.0724 | 0.1231 | 0.1763 | 0.1303 | 0.2217 | 0.0869 | 0.05 | 0.1576 | 0.0903 | 0.0903 | 0.1576 | 0.0592 | 0.2257 | 2.3679 | 2.9046 | 2.0784 | 0.3619 | 0.5011 | 0.4497 | 0.9089 | 0.4927 | 0.5324 | 0.1441 | 0.05
Load_TR6_F1_26 | customer | 0.218 | 0.052 | 0.052 | 0.052 | 0.218 | 0.052 | 0.1577 | 0.1124 | 0.052 | 0.1501 | 0.1199 | 0.0671 | 0.2029 | 0.052 | 0.1879 | 0.2417 | 0.6341 | 1.4671 | 1.3251 | 1.114 | 0.2456 | 0.0973 | 0.1728 | 0.052 | 0.218 | 0.052 | 0.052 | 0.5828 | 0.454 | 0.4898 | 0.3334 | 0.1816 | 0.3949 | 0.21 | 0.214 | 1.0438 | 1.1148 | 0.3446 | 0.5538 | 0.4559 | 0.8379 | 2.4272 | 0.7989 | 0.897 | 0.7193 | 0.9733 | 0.3807 | 0.3841
Load_TR6_F1_27 | customer | 0.055 | 0.2316 | 0.055 | 0.1834 | 0.1032 | 0.055 | 0.2155 | 0.0711 | 0.055 | 0.2316 | 0.055 | 0.1674 | 0.1192 | 0.055 | 0.1754 | 0.1112 | 0.055 | 0.1539 | 0.5012 | 0.3226 | 0.9054 | 0.3347 | 0.1167 | 0.0805 | 0.249 | 0.063 | 0.1353 | 0.1513 | 0.055 | 0.1834 | 0.1439 | 0.1425 | 0.2288 | 0.0624 | 0.0711 | 0.2155 | 0.0701 | 0.1822 | 0.3335 | 0.1957 | 0.5111 | 0.4719 | 0.7711 | 0.7476 | 1.5851 | 0.055 | 0.055 | 0.055
Load_TR6_F1_28 | customer | 0.0682 | 0.2331 | 0.0855 | 0.1128 | 0.1504 | 0.1028 | 0.044 | 0.1132 | 0.1881 | 0.044 | 0.2504 | 0.0509 | 0.2024 | 0.1532 | 0.1307 | 0.2243 | 0.0514 | 0.1464 | 0.4333 | 0.1011 | 0.2349 | 0.1274 | 0.1077 | 0.2013 | 0.044 | 0.0577 | 0.1813 | 0.0717 | 0.2296 | 0.044 | 0.1475 | 0.1538 | 0.044 | 0.1089 | 0.3378 | 0.5472 | 0.3856 | 0.3489 | 0.4418 | 0.2697 | 0.1744 | 0.1269 | 0.044 | 0.1881 | 0.1132 | 0.092 | 0.147 | 0.139
Load_TR6_F1_29 | customer | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.1016 | 0.2327 | 0.4364 | 0.2645 | 0.343 | 0.2226 | 0.1272 | 0.055 | 0.055 | 0.055 | 0.4955 | 0.055 | 0.0722 | 0.3536 | 0.287 | 0.095 | 0.194 | 0.2001 | 0.1563 | 0.4094 | 0.3639 | 0.2079 | 0.2359 | 0.3194 | 0.5836 | 0.432 | 0.5798 | 0.5744 | 0.5624 | 0.8024 | 0.5482 | 0.6909
Load_TR6_F1_3 | customer | 0.2234 | 0.1051 | 0.1032 | 0.2253 | 0.041 | 0.1948 | 0.1337 | 0.041 | 0.2721 | 0.0565 | 0.041 | 0.218 | 0.1105 | 0.1048 | 0.3362 | 2.2701 | 1.4907 | 0.2933 | 0.269 | 0.2729 | 0.0876 | 0.1923 | 0.2008 | 0.21 | 0.1283 | 0.2384 | 0.1059 | 0.1514 | 0.7393 | 0.5852 | 0.0691 | 0.3555 | 0.2514 | 0.2359 | 0.349 | 0.9924 | 0.1155 | 1.4291 | 1.4199 | 0.9379 | 0.5124 | 0.6149 | 1.3501 | 0.5897 | 0.3887 | 0.5868 | 0.7037 | 0.4766
Load_TR6_F1_30 | prosumer | 0.051 | 0.1126 | 0.1249 | 0.051 | 0.1865 | 0.051 | 0.1372 | 0.1003 | 0.051 | 0.0572 | 0.1803 | 0.051 | 0.1311 | 0.1064 | 0.3639 | 0.9156 | 0.4669 | 0.4018 | 0.4831 | 0.9434 | 0.1372 | 0.1003 | 0.0818 | 0.1557 | 0.051 | 0.051 | 1.1588 | 0.1496 | 0.662 | 1.1655 | 1.2044 | 0.3422 | 0.2047 | 1.3954 | 1.7776 | 2.0805 | 0.5673 | 1.3007 | 1.3132 | 2.4669 | 2.8604 | 1.6454 | 0.3859 | 1.2263 | 0.6663 | 1.0205 | 0.8458 | 0.0695
Load_TR6_F1_31 | customer | 0.3492 | 0.226 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.2673 | 0.2034 | 0.2321 | 0.476 | 0.2957 | 0.2946 | 2.1645 | 0.5285 | 0.4299 | 0.582 | 0.2528 | 0.3341 | 0.461 | 0.4138 | 0.049 | 0.049
Load_TR6_F1_32 | prosumer | 0.3145 | 0.466 | 0.048 | 0.1189 | 0.0569 | 0.1189 | 0.0569 | 0.1278 | 0.048 | 0.0879 | 0.0879 | 0.048 | 0.048 | 0.0835 | 0.0923 | 0.048 | 0.2065 | 0.1875 | 0.3263 | 0.9811 | 0.1278 | 0.4515 | 1.1272 | 0.2695 | 0.2319 | 0.5951 | 0.2753 | 0.079 | 0.048 | 0.1278 | 0.048 | 0.048 | 0.1342 | 0.1278 | 0.0657 | 0.1101 | 0.0524 | 0.1233 | 0.048 | 0.0923 | 0.0835 | 0.048 | 0.1056 | 0.0702 | 0.1189 | 0.0569 | 0.1278 | 0.048
Load_TR6_F1_33 | customer | 0.053 | 0.206 | 0.053 | 0.1712 | 0.0878 | 0.053 | 0.053 | 0.1921 | 0.0669 | 0.053 | 0.206 | 0.053 | 0.1573 | 0.1661 | 0.114 | 0.1781 | 0.1064 | 0.1017 | 0.1573 | 0.053 | 0.1723 | 0.0918 | 0.0763 | 0.9907 | 0.0836 | 0.1486 | 1.3712 | 0.4428 | 0.339 | 1.0622 | 0.5487 | 0.3439 | 0.1812 | 0.3266 | 1.9669 | 0.2304 | 1.5076 | 0.1212 | 0.1847 | 0.5172 | 0.3282 | 0.4958 | 0.5974 | 1.7737 | 1.7627 | 1.4644 | 0.1573 | 0.053
Load_TR6_F1_34 | prosumer | 1.1444 | 0.537 | 0.1649 | 0.1199 | 0.2015 | 0.1969 | 0.1509 | 0.2475 | 0.06 | 0.3084 | 0.09 | 0.1736 | 0.2098 | 0.1545 | 0.3437 | 0.3138 | 0.2389 | 1.1518 | 0.2494 | 0.1274 | 0.1915 | 0.1395 | 0.06 | 0.06 | 0.4398 | 0.293 | 0.556 | 0.3643 | 0.3307 | 0.2443 | 0.2892 | 0.1893 | 1.5484 | 1.0534 | 0.6396 | 0.3067 | 1.1302 | 0.762 | 0.2908 | 0.3261 | 0.3857 | 0.5013 | 0.4759 | 0.4506 | 0.1285 | 0.1736 | 0.06 | 0.3309
Load_TR6_F1_35 | prosumer | 2.2812 | 0.6863 | 0.6692 | 1.0275 | 0.1195 | 0.2535 | 0.0718 | 0.2937 | 0.083 | 0.1852 | 0.1082 | 0.1998 | 0.0643 | 1.9601 | 0.2113 | 0.0569 | 0.677 | 1.1568 | 1.0178 | 0.6775 | 0.4057 | 0.6492 | 1.4586 | 1.6302 | 0.2869 | 0.194 | 0.2764 | 3.753 | 1.2256 | 1.8032 | 0.1235 | 0.1984 | 0.0797 | 0.042 | 0.9991 | 1.197 | 0.193 | 2.3836 | 0.2841 | 0.0643 | 0.093 | 0.1947 | 0.2055 | 0.0923 | 0.197 | 0.124 | 0.8454 | 0.3402
Load_TR6_F1_36 | prosumer | 0.1076 | 0.0896 | 0.058 | 0.058 | 0.058 | 0.058 | 0.1392 | 0.058 | 0.058 | 0.1302 | 0.067 | 0.1031 | 0.0941 | 0.1766 | 0.3283 | 0.2804 | 1.1175 | 0.3005 | 0.3978 | 0.2425 | 0.2494 | 0.588 | 0.1738 | 0.1392 | 0.058 | 0.1392 | 0.058 | 0.058 | 0.1392 | 0.058 | 0.1392 | 0.058 | 0.279 | 1.3159 | 1.1293 | 0.2243 | 0.198 | 0.3401 | 0.6002 | 0.2503 | 0.2725 | 0.2882 | 0.3374 | 0.3078 | 0.3166 | 0.4457 | 0.3959 | 0.4751
Load_TR6_F1_37 | prosumer | 0.1898 | 0.1568 | 0.196 | 0.06 | 0.1926 | 0.1602 | 0.0923 | 0.2605 | 0.06 | 0.2355 | 0.1173 | 0.06 | 0.1353 | 0.1172 | 0.2482 | 0.3396 | 0.2174 | 0.0958 | 0.6365 | 2.3979 | 2.749 | 2.6551 | 0.06 | 0.18 | 1.0127 | 0.9674 | 0.4596 | 1.2428 | 0.489 | 0.2609 | 2.0236 | 1.9919 | 1.4934 | 0.8504 | 0.1046 | 0.3972 | 2.2796 | 0.4287 | 0.3338 | 0.3564 | 0.474 | 0.2877 | 1.272 | 0.1362 | 0.2894 | 1.4553 | 0.8677 | 0.0815
Load_TR6_F1_38 | customer | 0.172 | 0.1882 | 0.049 | 0.2313 | 0.1289 | 0.1647 | 0.1822 | 0.0623 | 0.2313 | 0.1289 | 0.049 | 0.2582 | 0.1019 | 0.049 | 0.049 | 0.1647 | 0.1955 | 0.1647 | 0.049 | 0.1691 | 0.1911 | 0.3271 | 0.4785 | 0.069 | 0.5753 | 0.3466 | 0.0718 | 0.506 | 0.1253 | 0.0956 | 0.1969 | 0.1165 | 0.341 | 0.3042 | 0.1506 | 0.501 | 0.3751 | 0.5773 | 0.0756 | 0.2845 | 0.049 | 0.2822 | 0.0779 | 0.2009 | 0.1592 | 0.049 | 0.2579 | 0.1023
Load_TR6_F1_39 | prosumer | 0.4529 | 0.045 | 0.2622 | 0.2358 | 0.045 | 0.334 | 0.0518 | 0.1004 | 0.3975 | 0.0585 | 0.1829 | 0.3015 | 0.1262 | 0.1792 | 0.2713 | 0.2966 | 1.3189 | 2.6932 | 2.0985 | 0.3889 | 0.1804 | 0.2855 | 0.3549 | 0.3968 | 1.8306 | 0.104 | 0.437 | 0.0978 | 0.0574 | 0.2144 | 0.497 | 0.1783 | 0.3538 | 0.1571 | 0.2207 | 0.5686 | 0.1119 | 0.3716 | 0.3054 | 0.2281 | 0.6167 | 0.5756 | 0.2109 | 0.2783 | 0.1331 | 0.069 | 0.1804 | 0.2104
Load_TR6_F1_4 | customer | 0.1926 | 0.0903 | 0.05 | 0.1549 | 0.1047 | 0.0733 | 0.229 | 0.0539 | 0.0889 | 0.1941 | 0.07 | 0.1027 | 0.1927 | 0.1289 | 0.05 | 0.163 | 0.1699 | 0.0625 | 0.1707 | 0.1135 | 0.058 | 0.5279 | 0.2285 | 0.3086 | 0.2661 | 0.4227 | 1.0323 | 0.4599 | 0.447 | 0.2168 | 0.3297 | 0.1578 | 0.2134 | 1.6161 | 1.2102 | 1.903 | 1.8564 | 0.5304 | 0.4994 | 0.6486 | 0.5376 | 0.7332 | 1.5315 | 1.1824 | 1.6321 | 0.2782 | 0.1307 | 0.1199
Load_TR6_F1_40 | customer | 0.2446 | 0.2935 | 0.1236 | 0.1845 | 0.1096 | 0.237 | 0.1595 | 0.117 | 0.2155 | 0.2329 | 0.1435 | 0.2171 | 0.1716 | 0.2207 | 0.2158 | 0.1555 | 0.2856 | 0.1618 | 0.1364 | 0.1944 | 0.2726 | 0.0555 | 0.5192 | 0.0648 | 0.1724 | 0.3486 | 0.0916 | 0.2293 | 0.1807 | 0.2329 | 0.1174 | 0.2892 | 0.1581 | 0.5401 | 0.34 | 0.3163 | 0.3718 | 0.3033 | 0.4408 | 0.5134 | 0.4266 | 0.174 | 0.2831 | 0.153 | 0.6311 | 1.4176 | 0.7322 | 0.6788
Load_TR6_F1_41 | customer | 0.1775 | 0.2202 | 0.053 | 0.2459 | 0.1518 | 0.0758 | 0.3219 | 0.053 | 0.0779 | 0.1526 | 0.1898 | 0.0834 | 0.1775 | 0.3344 | 1.2595 | 0.0655 | 0.1651 | 0.2202 | 0.1775 | 0.1898 | 0.1332 | 0.1277 | 0.205 | 0.0869 | 0.3021 | 0.5655 | 0.3495 | 0.2915 | 0.1588 | 0.1933 | 0.0986 | 0.0986 | 0.2991 | 0.053 | 0.2453 | 0.4931 | 0.085 | 0.1153 | 0.1153 | 0.053 | 0.1214 | 0.1518 | 0.053 | 0.0655 | 0.2335 | 0.3596 | 0.1771 | 0.2915
Load_TR6_F1_42 | prosumer | 0.3807 | 0.1706 | 1.1761 | 0.2725 | 0.0715 | 0.1518 | 0.038 | 0.1318 | 0.0916 | 0.0581 | 0.1652 | 0.038 | 0.0849 | 0.1385 | 0.038 | 0.038 | 1.1389 | 0.038 | 0.3167 | 0.3457 | 0.9703 | 0.4012 | 0.0559 | 0.4236 | 0.155 | 0.4206 | 1.415 | 0.7508 | 0.2797 | 0.2879 | 0.25 | 0.3313 | 0.4842 | 0.4175 | 0.1934 | 0.1767 | 0.1621 | 0.1513 | 0.2298 | 0.5772 | 0.6164 | 1.463 | 0.4584 | 0.3759 | 0.4748 | 0.2271 | 0.1853 | 0.038
Load_TR6_F1_43 | customer | 0.1348 | 0.1123 | 0.1574 | 0.0804 | 0.2623 | 0.052 | 0.1574 | 0.1852 | 0.052 | 0.0885 | 0.2542 | 0.052 | 0.1916 | 0.1511 | 0.128 | 0.2542 | 0.1128 | 0.2223 | 0.0595 | 0.1325 | 0.2102 | 0.052 | 0.2102 | 0.0595 | 0.1685 | 0.1951 | 0.5484 | 0.2139 | 0.1982 | 0.3629 | 0.2206 | 0.3265 | 0.1249 | 0.0594 | 0.2305 | 0.1834 | 1.4684 | 1.294 | 0.6439 | 0.3584 | 0.3274 | 0.2192 | 0.2635 | 0.052 | 0.1585 | 0.1841 | 0.052 | 0.2258
Load_TR6_F1_44 | prosumer | 0.9288 | 0.5227 | 0.0755 | 0.2257 | 0.057 | 0.057 | 0.2072 | 0.0941 | 0.1404 | 0.1609 | 0.1404 | 0.057 | 0.1312 | 0.0867 | 0.1404 | 0.1609 | 0.0802 | 1.2766 | 1.6762 | 0.1488 | 0.1386 | 0.057 | 0.1404 | 0.1609 | 0.1636 | 0.1969 | 0.5526 | 0.2461 | 0.2517 | 0.2085 | 0.057 | 0.1609 | 0.057 | 0.1404 | 0.1609 | 0.1033 | 0.2486 | 0.5651 | 0.3693 | 0.6724 | 0.3965 | 0.3681 | 0.3169 | 0.4123 | 0.7287 | 0.5134 | 0.4348 | 0.3843
Load_TR6_F1_45 | customer | 0.1222 | 0.1566 | 0.1003 | 0.1073 | 0.2208 | 0.051 | 0.2534 | 0.0747 | 0.113 | 0.2151 | 0.051 | 0.1997 | 0.1284 | 0.1104 | 0.6844 | 0.5139 | 0.3824 | 0.1057 | 0.8432 | 1.824 | 0.0867 | 0.6991 | 1.8965 | 0.1779 | 0.1606 | 0.3166 | 0.2087 | 0.2545 | 0.2874 | 0.1918 | 0.0866 | 0.0866 | 0.1848 | 0.0761 | 0.1324 | 0.1918 | 0.0617 | 0.1877 | 0.2154 | 0.1934 | 0.3929 | 0.7741 | 0.463 | 0.5629 | 0.757 | 0.5528 | 0.4218 | 0.1222
Load_TR6_F1_46 | prosumer | 0.043 | 0.1254 | 0.0655 | 0.0507 | 0.205 | 0.1029 | 0.1651 | 0.1356 | 0.0661 | 0.1896 | 0.1329 | 0.2277 | 0.043 | 0.0954 | 0.2651 | 0.043 | 0.1479 | 0.1279 | 0.2327 | 0.0672 | 0.3293 | 1.1495 | 0.9326 | 0.3669 | 0.2187 | 0.3059 | 0.3809 | 0.3055 | 0.4038 | 0.3384 | 0.3307 | 0.2049 | 0.5014 | 1.2094 | 0.492 | 0.5019 | 1.1298 | 0.3708 | 1.6177 | 0.4234 | 0.518 | 1.2572 | 0.5203 | 0.5712 | 0.3578 | 0.2173 | 0.2049 | 0.6776
Load_TR6_F1_47 | prosumer | 0.1401 | 0.2059 | 0.038 | 0.1143 | 0.1296 | 0.0533 | 0.1906 | 0.038 | 0.1906 | 0.0533 | 0.1143 | 0.1296 | 0.038 | 0.2059 | 0.038 | 0.2464 | 0.286 | 0.0444 | 1.1549 | 0.1813 | 0.038 | 0.0533 | 0.1906 | 0.038 | 0.8544 | 0.19 | 0.2135 | 0.0533 | 0.1946 | 0.065 | 0.212 | 0.1941 | 0.0481 | 0.2185 | 0.038 | 0.1645 | 0.142 | 0.038 | 0.1983 | 0.0456 | 0.1372 | 0.1067 | 0.0914 | 0.1525 | 0.1401 | 0.1479 | 0.0953 | 0.2023
Load_TR6_F1_48 | prosumer | 0.1138 | 0.052 | 0.1215 | 0.052 | 0.052 | 0.1215 | 0.052 | 0.1215 | 0.052 | 0.052 | 0.1176 | 0.0559 | 0.1215 | 1.0417 | 0.052 | 0.1215 | 0.3083 | 0.9176 | 1.1866 | 0.1129 | 0.1024 | 0.052 | 0.0867 | 0.0867 | 0.106 | 0.0674 | 0.0597 | 0.1138 | 0.052 | 0.1176 | 0.0559 | 0.9754 | 0.6237 | 0.1384 | 0.1343 | 0.5628 | 2.181 | 1.8019 | 0.5572 | 0.3942 | 0.4805 | 0.4244 | 0.5614 | 0.5899 | 0.565 | 1.4724 | 0.5001 | 0.4007
Load_TR6_F1_49 | customer | 0.3638 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.2048 | 1.5439 | 0.6316 | 1.2876 | 1.1209 | 2.547 | 3.7376 | 1.3533 | 1.4907 | 1.6298 | 0.4907 | 0.2042 | 0.2198 | 0.233 | 0.4977 | 0.2266 | 0.2919 | 0.448 | 0.6757 | 0.4818 | 0.4266 | 0.2415 | 0.048 | 0.048 | 0.048 | 0.048 | 0.4092 | 0.7365 | 0.5595 | 0.4171 | 0.2238
Load_TR6_F1_5 | prosumer | 0.1732 | 0.1364 | 0.1143 | 0.1437 | 0.048 | 0.21 | 0.1364 | 0.21 | 0.048 | 0.048 | 0.21 | 0.1364 | 0.1879 | 0.0701 | 0.0848 | 0.224 | 0.1259 | 0.1551 | 0.1337 | 2.4113 | 1.3717 | 0.1119 | 0.102 | 0.2395 | 0.107 | 0.21 | 0.1364 | 0.048 | 0.21 | 0.0873 | 0.0971 | 0.4643 | 0.3196 | 0.2785 | 0.2229 | 0.2743 | 0.5869 | 0.2588 | 2.1137 | 0.3385 | 0.3772 | 0.4397 | 0.4021 | 0.5002 | 0.4437 | 0.6506 | 0.7978 | 0.5122
Load_TR6_F1_6 | prosumer | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.083 | 1.3593 | 0.086 | 0.2216 | 0.074 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.047 | 0.2301 | 0.035 | 0.4025 | 0.7193 | 0.3755 | 0.2031 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
Load_TR6_F1_7 | customer | 0.048 | 0.0828 | 0.1664 | 0.048 | 0.048 | 0.048 | 0.1315 | 0.1176 | 0.048 | 0.0731 | 0.2386 | 0.048 | 0.1664 | 0.0828 | 0.1246 | 0.1246 | 0.1319 | 0.2356 | 1.0658 | 1.0628 | 1.5866 | 0.1937 | 0.1794 | 0.2887 | 0.048 | 0.2012 | 0.048 | 0.1037 | 0.2846 | 0.2127 | 0.3659 | 0.186 | 0.1794 | 0.2056 | 0.048 | 0.1872 | 0.0619 | 0.0758 | 0.1733 | 0.048 | 0.1983 | 0.562 | 0.906 | 0.7087 | 0.5049 | 0.0843 | 0.2012 | 0.048
Load_TR6_F1_8 | prosumer | 0.062 | 0.2217 | 0.054 | 0.1498 | 0.1339 | 0.078 | 0.2057 | 0.054 | 0.1578 | 0.1259 | 0.054 | 0.0939 | 0.1898 | 0.054 | 0.054 | 0.2297 | 0.054 | 0.1419 | 0.1419 | 0.054 | 0.1498 | 0.1339 | 0.0939 | 0.1898 | 0.054 | 0.2217 | 3.0672 | 0.8424 | 0.1818 | 0.054 | 0.2217 | 0.062 | 0.054 | 0.1179 | 0.1658 | 0.054 | 0.1578 | 0.1259 | 0.062 | 0.2217 | 0.054 | 0.1658 | 0.1179 | 0.054 | 0.054 | 0.2347 | 0.104 | 0.054
Load_TR6_F1_9 | prosumer | 0.5031 | 0.2782 | 0.6064 | 0.2842 | 0.1906 | 0.174 | 0.1643 | 0.2147 | 0.055 | 0.1557 | 0.2706 | 0.0869 | 0.2227 | 0.2354 | 0.055 | 0.067 | 0.1485 | 0.1015 | 0.3499 | 0.2146 | 0.59 | 0.7575 | 0.3419 | 0.1995 | 0.4694 | 0.2532 | 0.0869 | 0.3312 | 0.095 | 0.2102 | 0.32 | 0.2727 | 0.9088 | 2.7733 | 2.9006 | 0.51 | 0.2219 | 0.9778 | 0.4739 | 1.3734 | 3.057 | 3.1187 | 2.5403 | 1.4018 | 0.9834 | 0.7514 | 0.8998 | 0.8217
Load_TR6_F4_1 | customer | 0.049 | 0.1157 | 0.1453 | 0.049 | 0.2045 | 0.0564 | 0.1231 | 0.1379 | 0.049 | 0.2119 | 0.049 | 0.1971 | 0.0638 | 0.1082 | 0.1527 | 0.0583 | 0.0769 | 2.9464 | 0.5623 | 0.049 | 0.0786 | 0.1823 | 0.049 | 0.049 | 0.1601 | 0.1008 | 0.077 | 0.1852 | 0.1213 | 0.7257 | 0.664 | 0.2519 | 0.3027 | 0.2603 | 0.1429 | 0.2522 | 0.3445 | 0.4854 | 0.2905 | 0.3118 | 0.5148 | 0.2889 | 0.7198 | 0.4147 | 0.2347 | 0.3031 | 0.2119 | 0.049
Load_TR6_F4_10 | prosumer | 0.046 | 0.1338 | 0.1575 | 0.0519 | 0.1575 | 0.1279 | 0.134 | 0.1482 | 0.0903 | 0.2101 | 0.046 | 0.1125 | 0.1788 | 0.348 | 0.4438 | 0.4319 | 0.4809 | 0.3176 | 0.2087 | 0.2863 | 0.1865 | 0.2727 | 0.1151 | 0.481 | 3.0019 | 0.9435 | 1.5746 | 1.3809 | 0.9221 | 0.1959 | 0.2751 | 0.4229 | 0.2015 | 0.3656 | 0.5651 | 1.5634 | 1.8219 | 0.3759 | 0.4881 | 0.4375 | 1.6911 | 1.7017 | 0.6037 | 1.3001 | 0.3172 | 0.8124 | 0.52 | 0.2791
Load_TR6_F4_100 | customer | 0.3718 | 0.0761 | 0.048 | 0.2494 | 0.0594 | 0.2208 | 0.2729 | 0.048 | 0.2379 | 0.1633 | 0.1748 | 0.2334 | 0.2603 | 0.1281 | 0.1464 | 0.1828 | 0.3109 | 0.048 | 0.1905 | 0.3032 | 0.048 | 0.2968 | 0.1968 | 0.238 | 0.1572 | 0.1464 | 0.2329 | 0.2397 | 0.2456 | 0.0793 | 0.2151 | 0.2671 | 0.1509 | 0.2737 | 0.2199 | 0.0648 | 0.3515 | 0.1253 | 0.3163 | 0.1502 | 0.3882 | 0.58 | 0.5284 | 0.3872 | 0.203 | 0.4902 | 0.1113 | 0.1656
Load_TR6_F4_11 | prosumer | 0.2344 | 0.1426 | 0.058 | 0.1223 | 0.2548 | 0.058 | 0.1916 | 0.1854 | 0.1223 | 0.2548 | 0.058 | 0.1994 | 0.0939 | 0.1932 | 0.1839 | 0.1482 | 1.2709 | 0.6121 | 0.2452 | 0.3264 | 0.1683 | 0.2114 | 0.1657 | 0.2718 | 0.2787 | 0.1768 | 0.4881 | 2.0105 | 0.8144 | 1.2218 | 0.2879 | 0.6534 | 0.6284 | 0.3958 | 0.4851 | 0.2679 | 0.2557 | 0.3955 | 0.3693 | 0.6382 | 0.5959 | 0.508 | 0.792 | 0.586 | 0.8555 | 0.7985 | 0.8718 | 0.8382
Load_TR6_F4_12 | prosumer | 0.052 | 0.052 | 0.1681 | 0.1323 | 0.052 | 0.2484 | 0.052 | 0.2038 | 0.0966 | 0.1056 | 0.1948 | 0.052 | 0.052 | 0.1145 | 0.1859 | 0.052 | 0.0877 | 0.2127 | 0.3176 | 1.3694 | 1.1884 | 0.1193 | 0.1011 | 0.4903 | 0.3329 | 0.659 | 0.1715 | 0.4626 | 1.52 | 0.3265 | 0.3071 | 0.052 | 0.1681 | 0.1774 | 0.1071 | 0.1974 | 0.4659 | 0.411 | 0.4208 | 0.4585 | 0.5068 | 0.5998 | 0.8461 | 0.6004 | 0.9185 | 1.4175 | 0.8857 | 0.2409
Load_TR6_F4_13 | customer | 0.049 | 0.1455 | 0.1158 | 0.049 | 0.101 | 0.1603 | 0.049 | 0.2123 | 0.049 | 0.0787 | 0.1826 | 0.049 | 0.049 | 0.2123 | 0.0938 | 0.049 | 0.1966 | 0.2394 | 0.2368 | 0.1603 | 0.049 | 0.2123 | 0.049 | 0.049 | 0.0787 | 0.1826 | 0.049 | 0.2123 | 0.049 | 0.0861 | 0.3205 | 0.2942 | 0.4303 | 0.2617 | 0.0916 | 0.1683 | 0.2257 | 0.0817 | 1.4274 | 0.3995 | 0.5587 | 0.6953 | 0.3249 | 0.8693 | 0.5774 | 0.7963 | 0.5328 | 0.2123
Load_TR6_F4_14 | customer | 0.8062 | 0.5962 | 0.1895 | 0.1208 | 0.0382 | 0.2221 | 0.0851 | 0.1184 | 0.1351 | 0.0854 | 0.1915 | 0.1093 | 0.0508 | 0.2721 | 0.0382 | 0.1602 | 0.1155 | 0.359 | 0.3933 | 0.2153 | 0.1531 | 0.2167 | 0.1015 | 0.3472 | 2.1317 | 0.2021 | 0.3287 | 0.5731 | 0.5217 | 0.7803 | 0.2763 | 0.3472 | 0.5495 | 0.8101 | 0.4012 | 0.1456 | 0.3722 | 0.2748 | 0.3582 | 0.3671 | 1.6636 | 0.7298 | 0.4521 | 0.2436 | 0.6524 | 0.3849 | 0.2102 | 0.1
Load_TR6_F4_15 | prosumer | 0.108 | 0.2648 | 0.021 | 0.0941 | 0.2022 | 0.0974 | 0.021 | 0.2717 | 0.1011 | 0.021 | 0.2787 | 0.0332 | 0.291 | 0.0696 | 0.0956 | 0.2772 | 0.751 | 0.7928 | 0.1466 | 0.9127 | 0.2817 | 0.1771 | 0.1359 | 0.9379 | 1.5555 | 0.3405 | 0.219 | 0.0679 | 0.27 | 0.137 | 0.1503 | 0.2686 | 0.1481 | 0.0332 | 0.1258 | 0.2105 | 0.11 | 0.122 | 0.4263 | 1.3671 | 0.3241 | 0.3971 | 0.5699 | 0.5895 | 1.2694 | 0.6279 | 0.6855 | 0.2453
Load_TR6_F4_16 | prosumer | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.1025 | 0.1876 | 0.1794 | 0.0746 | 0.0625 | 0.053 | 0.053 | 0.2452 | 0.2445 | 0.0537 | 1.0102 | 0.0537 | 0.0779 | 0.0635 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.0645 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053
Load_TR6_F4_17 | prosumer | 0.1591 | 0.1218 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.8835 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043
Load_TR6_F4_18 | prosumer | 0.674 | 0.1227 | 0.2604 | 0.1315 | 0.1424 | 0.2166 | 0.0899 | 0.1337 | 0.2417 | 0.1665 | 0.057 | 0.1344 | 0.2739 | 0.057 | 0.2417 | 0.057 | 0.1337 | 0.1067 | 0.2414 | 0.1501 | 0.057 | 0.1611 | 0.2472 | 0.057 | 0.2925 | 0.2938 | 0.3017 | 0.3672 | 1.5838 | 0.906 | 0.6473 | 0.2746 | 0.2199 | 0.4694 | 1.5775 | 0.8752 | 1.365 | 2.8553 | 0.1788 | 0.6061 | 0.5065 | 0.9283 | 0.8105 | 0.9439 | 0.8047 | 0.7351 | 0.2213 | 0.1377
Load_TR6_F4_19 | customer | 0.5148 | 0.3698 | 0.043 | 0.1778 | 0.0913 | 0.145 | 0.1241 | 0.043 | 0.1866 | 0.0825 | 0.043 | 0.1471 | 0.0605 | 0.1862 | 0.2926 | 0.0492 | 0.1796 | 0.0913 | 0.261 | 0.2092 | 1.4504 | 0.9201 | 1.1149 | 0.1281 | 0.2081 | 0.183 | 0.1324 | 0.1745 | 0.0649 | 0.043 | 0.1471 | 0.043 | 0.0687 | 0.216 | 0.0794 | 0.4441 | 0.1019 | 0.3498 | 0.206 | 0.4001 | 0.4652 | 0.1612 | 0.3444 | 0.1276 | 0.1963 | 0.0728 | 0.043 | 0.1471
Load_TR6_F4_2 | customer | 0.2129 | 0.05 | 0.1759 | 0.087 | 0.05 | 0.2129 | 0.05 | 0.1611 | 0.1018 | 0.0648 | 0.1981 | 0.05 | 0.1685 | 0.0944 | 0.1166 | 0.5153 | 0.1119 | 0.2985 | 0.1437 | 0.3414 | 0.1592 | 0.2501 | 0.2474 | 0.2788 | 0.0678 | 0.1981 | 0.0724 | 0.1981 | 0.0648 | 0.05 | 0.1537 | 0.1922 | 0.2393 | 0.4641 | 0.1679 | 0.2959 | 0.2625 | 0.3318 | 0.4805 | 0.6397 | 0.4823 | 0.3928 | 0.5915 | 0.6388 | 0.7658 | 0.7731 | 0.552 | 0.1092
Load_TR6_F4_20 | customer | 0.19 | 0.046 | 0.22 | 0.0853 | 0.1076 | 0.1847 | 0.1053 | 0.0691 | 0.1669 | 0.1384 | 0.046 | 0.4619 | 0.1377 | 0.0845 | 0.0768 | 0.1045 | 0.7981 | 1.3996 | 1.1607 | 1.2283 | 0.095 | 0.3272 | 0.2405 | 0.141 | 0.2079 | 0.046 | 0.096 | 0.2093 | 0.1089 | 0.1314 | 0.1361 | 0.1037 | 0.0902 | 0.1983 | 0.2175 | 0.1414 | 0.2029 | 0.1217 | 0.0772 | 0.1159 | 0.3626 | 0.2252 | 0.4288 | 0.6286 | 1.479 | 0.2054 | 0.0614 | 0.0999
Load_TR6_F4_21 | prosumer | 0.1474 | 0.047 | 0.2974 | 0.0757 | 0.2095 | 0.1636 | 0.1039 | 0.1689 | 0.047 | 0.2042 | 0.1689 | 0.1092 | 0.3754 | 0.3639 | 0.1851 | 0.1163 | 0.1837 | 0.1608 | 0.0685 | 0.2559 | 0.0958 | 1.4875 | 0.408 | 0.1992 | 0.3261 | 0.047 | 0.0828 | 0.1115 | 0.2258 | 0.1402 | 0.0542 | 0.112 | 0.2611 | 0.0551 | 0.275 | 0.2478 | 0.3844 | 0.3815 | 0.2694 | 0.5889 | 0.5708 | 0.564 | 0.6155 | 0.2693 | 0.2884 | 0.0848 | 0.047 | 0.047
Load_TR6_F4_22 | prosumer | 0.2128 | 0.1034 | 0.053 | 0.053 | 0.1482 | 0.0698 | 0.137 | 0.081 | 0.053 | 0.165 | 0.053 | 0.1482 | 0.0698 | 0.1482 | 0.0698 | 0.0922 | 0.1258 | 0.053 | 0.053 | 0.053 | 0.165 | 0.053 | 0.053 | 0.053 | 0.1258 | 0.0922 | 0.053 | 0.1723 | 0.0662 | 0.0645 | 0.1626 | 0.1934 | 0.5802 | 1.3362 | 1.4831 | 2.6136 | 2.1771 | 0.1903 | 0.2822 | 0.3444 | 0.4163 | 0.4035 | 0.3133 | 0.2721 | 0.3313 | 0.2697 | 0.3709 | 0.0586
Load_TR6_F4_23 | customer | 0.055 | 0.2932 | 0.0995 | 0.1511 | 0.1495 | 0.2121 | 0.1215 | 0.2188 | 0.1149 | 0.2255 | 0.2397 | 0.12 | 0.2578 | 0.1424 | 0.1519 | 0.2409 | 0.2913 | 1.776 | 0.33 | 0.2604 | 0.5486 | 0.3376 | 1.0493 | 0.3235 | 0.1718 | 0.1989 | 0.218 | 0.1298 | 0.2338 | 0.134 | 0.3307 | 0.1427 | 0.2244 | 0.3156 | 0.3679 | 0.8989 | 2.636 | 1.76 | 0.3175 | 0.5571 | 0.5498 | 0.7616 | 0.7816 | 0.3777 | 0.5554 | 0.4226 | 0.7088 | 0.7629
Load_TR6_F4_24 | prosumer | 0.0703 | 0.0703 | 0.1945 | 0.047 | 0.2177 | 0.047 | 0.1168 | 0.1479 | 0.047 | 0.047 | 0.1246 | 0.1401 | 0.047 | 0.1557 | 0.1091 | 0.0751 | 0.0634 | 0.444 | 0.2158 | 0.4533 | 1.3475 | 1.83 | 3.0439 | 2.3373 | 0.3553 | 1.6824 | 0.047 | 0.2177 | 0.047 | 0.1246 | 0.1401 | 1.1379 | 2.2151 | 0.2471 | 0.1532 | 0.3163 | 0.2622 | 0.3031 | 0.2929 | 0.5106 | 0.4296 | 0.6424 | 0.4108 | 0.4342 | 0.4427 | 0.5065 | 0.4782 | 0.5574
Load_TR6_F4_25 | prosumer | 0.0628 | 0.039 | 0.039 | 0.1104 | 0.039 | 0.039 | 0.0628 | 0.0866 | 0.039 | 0.0509 | 0.0985 | 0.039 | 0.1104 | 0.039 | 0.2763 | 0.2173 | 1.0711 | 0.2405 | 0.3302 | 0.2795 | 0.2107 | 0.094 | 0.1397 | 0.5173 | 0.6648 | 0.3131 | 0.2487 | 0.2527 | 0.1353 | 0.0747 | 0.0747 | 0.039 | 0.0835 | 0.1936 | 0.2992 | 0.4589 | 0.3016 | 0.3368 | 0.3826 | 0.4728 | 2.3855 | 0.6477 | 0.6509 | 0.5821 | 0.039 | 0.039 | 0.039 | 0.1104
Load_TR6_F4_26 | customer | 0.1193 | 0.039 | 0.1193 | 0.0568 | 0.1014 | 0.039 | 0.0925 | 0.0658 | 0.0435 | 0.1148 | 0.039 | 0.039 | 0.039 | 0.1716 | 0.1209 | 0.5214 | 0.4841 | 0.2156 | 0.119 | 0.039 | 0.0996 | 0.1722 | 0.1014 | 0.0568 | 0.061 | 0.1683 | 1.3009 | 0.1469 | 0.2309 | 0.1937 | 0.3009 | 0.0568 | 0.1014 | 0.039 | 0.1014 | 0.0568 | 0.1598 | 0.085 | 0.0976 | 0.5849 | 0.2155 | 0.2637 | 0.3135 | 0.4361 | 0.3254 | 0.4119 | 0.3243 | 0.1781
Load_TR6_F4_27 | customer | 0.4496 | 0.1907 | 0.0732 | 0.186 | 0.052 | 0.1226 | 0.1367 | 0.052 | 0.052 | 0.2072 | 0.052 | 0.186 | 0.0732 | 0.0943 | 0.3474 | 0.3146 | 0.5965 | 0.5683 | 0.3958 | 0.2851 | 0.2072 | 0.222 | 0.3105 | 0.3069 | 0.4671 | 0.3205 | 0.4188 | 0.563 | 0.2096 | 0.1515 | 0.325 | 0.4275 | 0.0966 | 0.2168 | 0.1057 | 0.2667 | 0.2538 | 0.1819 | 0.3621 | 0.5965 | 0.6203 | 0.6075 | 0.537 | 0.4768 | 0.3316 | 0.6026 | 0.8924 | 0.6924
Load_TR6_F4_28 | prosumer | 0.5 | 0.1566 | 0.197 | 0.049 | 0.049 | 0.1835 | 0.0625 | 0.123 | 0.123 | 0.049 | 0.197 | 0.049 | 0.0692 | 0.1768 | 0.049 | 0.049 | 0.1634 | 0.0826 | 0.3998 | 0.3114 | 0.142 | 0.4294 | 0.0961 | 0.1791 | 0.2392 | 0.2884 | 0.1424 | 0.3347 | 0.3693 | 0.2481 | 0.346 | 0.3619 | 0.3649 | 0.4553 | 2.0886 | 2.6007 | 0.1189 | 0.0801 | 0.2173 | 0.0933 | 0.049 | 0.197 | 0.049 | 0.218 | 0.2645 | 0.1095 | 0.1365 | 0.049
Load_TR6_F4_29 | prosumer | 0.0686 | 0.267 | 0.6134 | 0.7057 | 0.5208 | 0.337 | 0.5751 | 0.4228 | 0.2053 | 0.1104 | 0.1884 | 0.042 | 0.2604 | 0.0753 | 0.1223 | 0.216 | 0.0753 | 0.1925 | 0.2448 | 0.3849 | 0.7177 | 2.1259 | 0.3275 | 0.32 | 0.1641 | 0.1296 | 0.5087 | 0.5629 | 0.6247 | 0.5685 | 0.5585 | 0.472 | 0.2599 | 0.1615 | 0.2568 | 0.2742 | 0.0873 | 0.2175 | 0.6055 | 1.0709 | 0.9618 | 1.8964 | 0.9453 | 0.7362 | 0.8801 | 0.667 | 0.8511 | 0.8339
Load_TR6_F4_3 | prosumer | 0.2088 | 0.155 | 0.0988 | 0.2289 | 0.1926 | 0.1829 | 0.0798 | 0.2232 | 0.1984 | 0.1132 | 0.3084 | 0.041 | 0.2774 | 0.1442 | 0.197 | 0.3596 | 0.1768 | 0.0456 | 0.1797 | 0.2419 | 0.041 | 0.303 | 0.1186 | 0.041 | 0.3589 | 0.0627 | 0.0582 | 0.2169 | 0.1875 | 0.0641 | 0.2544 | 0.1442 | 0.2309 | 0.1045 | 0.1658 | 0.3503 | 0.4571 | 0.2515 | 0.5385 | 0.4989 | 0.6099 | 0.535 | 0.7584 | 0.6245 | 0.7672 | 1.2051 | 0.0926 | 0.2514
Load_TR6_F4_30 | customer | 0.0818 | 0.1862 | 0.1903 | 0.052 | 0.216 | 0.135 | 0.1222 | 0.2011 | 0.1073 | 0.217 | 0.134 | 0.1903 | 0.2011 | 0.0669 | 0.2798 | 0.1266 | 0.0596 | 0.2369 | 0.1884 | 0.0797 | 0.3267 | 0.0797 | 0.338 | 0.0853 | 0.2685 | 0.2101 | 0.2223 | 0.0797 | 0.216 | 0.1952 | 0.2596 | 0.1228 | 0.2845 | 0.1611 | 0.2828 | 1.2929 | 0.2713 | 0.131 | 0.2563 | 0.2936 | 0.3267 | 0.3701 | 0.6465 | 0.6648 | 0.573 | 0.4992 | 0.2628 | 0.4894
Load_TR6_F4_31 | customer | 0.057 | 0.057 | 0.1586 | 0.057 | 0.057 | 0.1586 | 0.057 | 0.1296 | 0.086 | 0.057 | 0.1586 | 0.057 | 0.2501 | 0.3316 | 0.3316 | 1.2942 | 0.2167 | 0.2238 | 0.3641 | 0.2087 | 0.1504 | 0.1928 | 0.0753 | 0.0757 | 0.4215 | 0.1654 | 0.1389 | 0.0933 | 0.057 | 0.057 | 0.1586 | 0.057 | 0.4272 | 0.2813 | 0.3121 | 0.3103 | 0.2507 | 0.3751 | 0.5937 | 0.3749 | 1.1502 | 1.0708 | 0.2866 | 0.3179 | 0.2431 | 0.1158 | 0.1586 | 0.057
Load_TR6_F4_32 | customer | 0.1206 | 0.053 | 0.0928 | 0.0848 | 0.053 | 0.053 | 0.053 | 0.0769 | 0.1007 | 0.053 | 0.053 | 0.1007 | 0.0769 | 0.1087 | 1.1878 | 0.18 | 0.1246 | 0.0633 | 0.1474 | 0.0773 | 1.5009 | 1.2036 | 0.053 | 0.1246 | 0.061 | 0.1166 | 0.053 | 0.053 | 0.1246 | 0.053 | 0.053 | 0.1498 | 0.0727 | 0.2381 | 0.2162 | 0.4375 | 0.0769 | 0.1047 | 0.0729 | 0.2112 | 0.2091 | 0.9003 | 0.3994 | 0.1817 | 1.174 | 0.2686 | 0.3463 | 0.3534
Load_TR6_F4_33 | prosumer | 0.1174 | 0.044 | 0.1908 | 0.0766 | 0.044 | 0.2153 | 0.0522 | 0.1664 | 0.1011 | 0.0848 | 0.1827 | 0.044 | 0.0522 | 0.2153 | 0.044 | 0.2713 | 0.1873 | 0.3736 | 0.537 | 1.0499 | 0.0677 | 0.2345 | 0.1737 | 0.3696 | 0.1052 | 0.097 | 0.3166 | 0.1053 | 0.1782 | 0.1064 | 0.2214 | 0.3707 | 0.1664 | 0.044 | 0.1982 | 0.093 | 0.044 | 0.1827 | 0.0848 | 0.044 | 0.2235 | 0.044 | 0.1112 | 0.2334 | 0.4049 | 0.1093 | 0.1582 | 0.0914
Load_TR6_F4_34 | prosumer | 0.097 | 0.1117 | 0.053 | 0.1558 | 0.053 | 0.1264 | 0.0824 | 0.053 | 0.1558 | 0.053 | 0.053 | 0.1044 | 0.2273 | 0.053 | 0.053 | 0.1793 | 0.053 | 0.6468 | 2.6571 | 2.4078 | 0.1117 | 0.053 | 0.075 | 0.1338 | 0.053 | 0.1558 | 0.053 | 0.097 | 0.1117 | 0.053 | 0.1558 | 0.053 | 0.1044 | 0.4101 | 0.1044 | 0.1622 | 0.1018 | 0.2973 | 0.7098 | 0.1502 | 0.3898 | 0.3423 | 0.4628 | 0.3528 | 0.6091 | 0.3747 | 0.6669 | 0.4644
Load_TR6_F4_35 | prosumer | 0.1172 | 0.4023 | 0.0971 | 0.052 | 0.1423 | 0.0746 | 0.052 | 0.1028 | 0.114 | 0.052 | 0.052 | 0.052 | 0.0633 | 0.2029 | 0.4182 | 0.1167 | 1.4192 | 0.7466 | 0.1815 | 0.3059 | 1.1668 | 2.6374 | 2.6533 | 0.1836 | 0.052 | 0.1648 | 0.052 | 0.052 | 0.24 | 0.5028 | 0.3877 | 0.3667 | 0.3401 | 0.6555 | 1.6435 | 1.4528 | 0.926 | 0.2502 | 0.484 | 0.5148 | 0.7841 | 0.2084 | 0.6825 | 0.5298 | 0.531 | 0.1648 | 0.052 | 0.1648
Load_TR6_F4_36 | prosumer | 0.098 | 0.053 | 0.1026 | 0.0845 | 0.053 | 0.053 | 0.053 | 0.1341 | 0.053 | 0.1071 | 0.08 | 0.08 | 0.1071 | 0.1559 | 0.1912 | 0.053 | 1.5152 | 2.8785 | 1.5028 | 0.201 | 0.1229 | 1.5246 | 0.9158 | 1.2335 | 0.071 | 0.098 | 0.089 | 0.053 | 0.053 | 0.1341 | 0.053 | 0.1341 | 0.053 | 0.053 | 0.053 | 0.1341 | 0.1124 | 0.2086 | 0.1972 | 0.4225 | 0.4487 | 0.3778 | 0.4511 | 0.4694 | 0.6501 | 0.4219 | 0.133 | 0.089
Load_TR6_F4_37 | customer | 0.1337 | 0.056 | 0.056 | 0.1337 | 0.056 | 0.1035 | 0.0862 | 0.056 | 0.056 | 0.0646 | 0.1251 | 0.056 | 0.1337 | 0.056 | 0.056 | 1.0465 | 1.6918 | 0.2775 | 0.2912 | 0.4334 | 0.2768 | 0.8948 | 0.2437 | 0.3201 | 1.6496 | 0.3834 | 1.5108 | 0.8231 | 0.3029 | 0.3687 | 0.4663 | 0.3593 | 0.2514 | 0.2404 | 1.1149 | 1.3079 | 0.2017 | 0.198 | 0.4635 | 0.4542 | 0.5794 | 0.3982 | 0.4812 | 0.4853 | 0.7241 | 0.2459 | 0.1766 | 0.3277
Load_TR6_F4_38 | prosumer | 0.054 | 0.1873 | 0.0836 | 0.0836 | 0.1873 | 0.054 | 0.0762 | 0.1947 | 0.054 | 0.0984 | 0.1725 | 0.054 | 0.054 | 0.2169 | 0.7845 | 0.4585 | 0.2219 | 0.4158 | 0.2975 | 0.2209 | 0.4371 | 3.3156 | 0.5786 | 0.4534 | 0.7757 | 1.7205 | 0.304 | 0.7264 | 0.9828 | 0.9595 | 0.2759 | 0.5328 | 0.4492 | 0.3156 | 0.5811 | 0.4567 | 0.2652 | 0.2271 | 0.4484 | 0.666 | 0.5968 | 0.533 | 0.4547 | 0.7206 | 0.6394 | 0.5103 | 0.5859 | 0.3719
Load_TR6_F4_39 | prosumer | 0.2278 | 0.1253 | 0.03 | 0.2958 | 0.0572 | 0.1918 | 0.0796 | 0.1117 | 0.1199 | 0.2332 | 0.03 | 0.2032 | 0.1498 | 0.03 | 0.255 | 0.0981 | 0.132 | 1.7816 | 0.03 | 0.1806 | 0.1724 | 0.03 | 0.2623 | 0.0907 | 0.03 | 0.3051 | 0.048 | 0.1253 | 0.2128 | 0.1274 | 0.1831 | 0.1605 | 0.1379 | 0.2224 | 0.1921 | 0.4667 | 0.3482 | 0.2805 | 0.269 | 0.3287 | 0.6158 | 0.3828 | 0.4824 | 0.44 | 0.206 | 0.2972 | 0.066 | 0.1918
Load_TR6_F4_4 | customer | 0.043 | 0.1925 | 0.2787 | 0.1518 | 0.0838 | 0.043 | 0.0634 | 0.1721 | 0.043 | 0.1789 | 0.0566 | 0.043 | 0.1925 | 0.043 | 0.1314 | 0.1042 | 0.0498 | 0.1857 | 0.043 | 0.1366 | 0.3607 | 0.392 | 0.2434 | 0.1832 | 0.1228 | 1.5936 | 0.7493 | 1.397 | 1.3002 | 0.7191 | 0.046 | 1.1394 | 1.0017 | 1.7533 | 0.335 | 0.8378 | 1.4658 | 1.8368 | 0.5111 | 0.1179 | 0.1518 | 0.0838 | 0.043 | 0.1925 | 0.043 | 0.145 | 0.0906 | 0.043
Load_TR6_F4_40 | customer | 0.9537 | 0.9369 | 0.1423 | 0.048 | 0.1356 | 0.0547 | 0.048 | 0.1423 | 0.048 | 0.048 | 0.1423 | 0.048 | 0.048 | 0.1716 | 0.2989 | 0.1194 | 0.3369 | 0.0724 | 0.1043 | 0.1713 | 0.3258 | 0.4159 | 0.2955 | 0.213 | 0.4499 | 1.5412 | 0.246 | 0.3277 | 0.2894 | 0.7777 | 1.2395 | 0.2049 | 0.5251 | 0.4667 | 0.2665 | 0.5858 | 0.1014 | 0.048 | 0.3177 | 0.4839 | 0.6542 | 0.6336 | 0.9344 | 0.7511 | 1.7386 | 0.7179 | 0.048 | 0.1423
Load_TR6_F4_41 | customer | 0.2416 | 0.1097 | 0.1119 | 0.2393 | 0.041 | 0.2277 | 0.1236 | 0.041 | 0.041 | 0.1921 | 0.1592 | 0.041 | 0.1783 | 0.1559 | 0.304 | 0.2421 | 0.1145 | 0.0649 | 0.1569 | 0.1921 | 0.0608 | 0.1267 | 0.2689 | 2.1051 | 3.146 | 1.0206 | 0.106 | 0.1903 | 0.0959 | 0.2013 | 0.1499 | 0.1119 | 0.2325 | 0.1188 | 0.1099 | 0.208 | 0.1061 | 0.358 | 0.2372 | 0.3046 | 0.6258 | 0.4053 | 0.3909 | 0.2877 | 0.2709 | 0.385 | 0.1624 | 0.0528
Load_TR6_F4_42 | prosumer | 0.047 | 0.2446 | 0.2583 | 0.3698 | 0.5984 | 0.1159 | 0.0511 | 0.2143 | 0.0835 | 0.0835 | 0.0592 | 0.2751 | 0.047 | 0.047 | 0.047 | 0.2797 | 0.0546 | 0.0673 | 1.1101 | 1.4947 | 0.0875 | 0.2143 | 0.12 | 0.1307 | 0.2036 | 0.047 | 0.2184 | 0.7482 | 0.1783 | 0.1302 | 0.2364 | 0.2687 | 0.2206 | 0.4743 | 0.1953 | 0.3099 | 0.3218 | 0.564 | 1.9752 | 0.2873 | 0.5471 | 0.4078 | 0.3977 | 0.7012 | 0.5545 | 0.2102 | 0.1078 | 0.0713
Load_TR6_F4_43 | customer | 0.5221 | 0.6788 | 0.3255 | 0.2989 | 0.1786 | 0.0911 | 0.3005 | 0.0655 | 0.05 | 0.3493 | 0.0577 | 0.05 | 0.22 | 0.058 | 1.5404 | 1.3141 | 0.7346 | 0.2566 | 0.3473 | 1.4907 | 1.36 | 0.1973 | 0.2303 | 0.232 | 0.1477 | 0.1048 | 0.0964 | 0.5944 | 1.2544 | 1.6393 | 0.3507 | 2.3126 | 0.3858 | 0.3496 | 0.119 | 0.3746 | 1.3128 | 0.9198 | 1.7773 | 0.607 | 0.4781 | 0.7327 | 0.7341 | 0.6956 | 0.8601 | 0.8683 | 0.7639 | 0.7654
Load_TR6_F4_44 | customer | 0.6385 | 0.3275 | 0.2823 | 0.1154 | 0.2907 | 0.1384 | 0.1907 | 0.1899 | 0.2204 | 0.1972 | 0.0975 | 0.2176 | 0.2617 | 0.059 | 0.1969 | 0.2823 | 0.129 | 0.176 | 0.1808 | 0.3198 | 1.4824 | 1.2659 | 0.2828 | 0.3679 | 0.6184 | 1.0152 | 1.8356 | 0.4508 | 0.3539 | 0.3678 | 0.4275 | 0.6463 | 0.2173 | 0.26 | 0.2569 | 0.3253 | 0.5054 | 0.2656 | 0.3581 | 0.8877 | 0.3803 | 0.2534 | 0.7062 | 0.6699 | 0.8827 | 1.0927 | 0.3681 | 0.1822
Load_TR6_F4_45 | customer | 0.0979 | 0.043 | 0.1803 | 0.043 | 0.0499 | 0.1735 | 0.043 | 0.1185 | 0.1048 | 0.043 | 0.043 | 0.1803 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.1597 | 0.0748 | 0.1709 | 0.0636 | 0.043 | 0.1185 | 0.1048 | 0.0979 | 0.1254 | 0.0705 | 0.1529 | 0.043 | 0.043 | 0.043 | 0.043 | 0.1323 | 0.0911 | 0.043 | 0.1803 | 0.043 | 0.0773 | 0.146 | 0.043 | 0.1803 | 0.043 | 0.1666 | 0.0567 | 0.2834 | 1.8167 | 0.5643 | 0.693
Load_TR6_F4_46 | customer | 0.3848 | 0.686 | 0.6559 | 0.2426 | 0.1181 | 0.056 | 0.056 | 0.1181 | 0.056 | 0.1181 | 0.056 | 0.1181 | 0.056 | 0.0801 | 0.0939 | 0.0974 | 0.1392 | 0.2239 | 0.2366 | 0.2438 | 0.2135 | 0.1992 | 0.3855 | 0.4846 | 0.2153 | 0.2531 | 0.3075 | 1.1973 | 0.0685 | 0.1256 | 0.1411 | 0.2444 | 0.212 | 0.3949 | 0.3715 | 0.4396 | 0.6372 | 0.3588 | 0.5049 | 0.6015 | 0.7672 | 0.842 | 0.8197 | 0.6168 | 0.5187 | 1.0013 | 1.6087 | 0.056
Load_TR6_F4_47 | customer | 0.6492 | 0.2578 | 0.048 | 0.1323 | 0.1765 | 0.0714 | 0.1089 | 0.1906 | 0.1182 | 0.1874 | 0.1617 | 0.246 | 0.048 | 0.1451 | 0.1637 | 0.1323 | 0.048 | 0.1701 | 0.0919 | 0.1374 | 0.138 | 0.048 | 0.1387 | 0.2165 | 0.7474 | 0.9249 | 0.2259 | 0.2645 | 0.0907 | 0.2561 | 0.0527 | 0.295 | 0.048 | 0.0579 | 0.44 | 0.3594 | 1.5254 | 0.4058 | 0.3801 | 0.4612 | 0.3404 | 0.6095 | 0.3957 | 0.6477 | 0.5799 | 0.4556 | 0.1323 | 0.048
Load_TR6_F4_48 | prosumer | 0.049 | 0.2386 | 0.049 | 0.2041 | 0.0835 | 0.049 | 0.1352 | 0.1524 | 0.049 | 0.2386 | 0.049 | 0.1266 | 0.161 | 0.049 | 0.1869 | 0.1007 | 0.1179 | 0.1697 | 0.049 | 0.0835 | 0.2041 | 0.049 | 0.2386 | 0.049 | 0.0921 | 0.1998 | 0.4071 | 0.7305 | 0.1793 | 0.1018 | 0.3206 | 0.149 | 0.648 | 0.0662 | 0.2125 | 0.3044 | 0.0662 | 0.2214 | 0.049 | 0.0576 | 0.23 | 0.049 | 0.2041 | 0.0835 | 0.049 | 0.049 | 0.2386 | 0.049
Load_TR6_F4_49 | customer | 0.059 | 0.0908 | 0.1864 | 0.051 | 0.2262 | 0.051 | 0.051 | 0.2262 | 0.051 | 0.051 | 0.1227 | 0.1545 | 0.051 | 0.051 | 0.1784 | 0.0988 | 0.0908 | 0.2603 | 0.0836 | 0.1882 | 1.2359 | 4.996 | 2.6535 | 0.7891 | 0.051 | 0.1147 | 0.1625 | 0.051 | 0.0765 | 0.2222 | 0.3101 | 0.3166 | 0.3343 | 0.1354 | 0.4772 | 0.1398 | 0.1057 | 0.1944 | 0.1213 | 0.7084 | 0.7746 | 0.809 | 0.842 | 0.8902 | 1.321 | 1.3209 | 2.8959 | 3.5458
Load_TR6_F4_5 | prosumer | 0.0546 | 0.1263 | 0.063 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.0643 | 0.0606 | 0.0555 | 0.066 | 0.051 | 0.051 | 0.051 | 0.051 | 0.9924 | 0.1175 | 0.051 | 0.051 | 0.0546 | 0.0546 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.1022 | 0.051 | 0.051 | 0.051 | 0.051
Load_TR6_F4_50 | prosumer | 0.043 | 0.2252 | 0.043 | 0.0844 | 0.1838 | 0.043 | 0.1589 | 0.1092 | 0.0761 | 0.192 | 0.043 | 0.1506 | 0.1175 | 0.2137 | 0.0981 | 0.2086 | 0.0596 | 0.1341 | 0.2985 | 0.446 | 0.3738 | 0.0538 | 0.2334 | 0.2711 | 0.4528 | 0.2305 | 0.214 | 0.2252 | 0.043 | 0.1755 | 0.5208 | 0.3695 | 0.4531 | 0.214 | 0.4202 | 0.3303 | 0.2642 | 0.2626 | 0.3386 | 0.6433 | 0.4406 | 0.5417 | 0.765 | 0.4494 | 0.5387 | 0.5744 | 0.043 | 0.1424
Load_TR6_F4_51 | customer | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.114 | 0.2521 | 0.8453 | 0.4833 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.1081 | 0.1428 | 0.0689 | 0.0852 | 0.0622 | 0.051 | 0.051 | 0.0748 | 0.2926 | 0.4251 | 0.8624 | 1.013 | 0.8493 | 0.8506 | 0.8378 | 0.943 | 0.7243 | 0.5742 | 0.5885
Load_TR6_F4_52 | customer | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.5567 | 0.5627 | 1.7257 | 0.452 | 1.1208 | 0.0688 | 2.0651 | 4.6403 | 0.5566 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.063 | 0.2246 | 0.6629 | 0.6212 | 0.5872 | 0.551 | 0.059 | 0.059 | 0.059 | 0.059
Load_TR6_F4_53 | customer | 0.0827 | 0.1832 | 0.054 | 0.054 | 0.054 | 0.1473 | 0.1186 | 0.0684 | 0.1976 | 0.054 | 0.0755 | 0.1904 | 0.054 | 0.2119 | 0.054 | 0.0971 | 0.1688 | 0.3106 | 0.4862 | 0.2434 | 1.7953 | 0.2356 | 0.2627 | 0.2833 | 1.1008 | 0.3436 | 0.2584 | 0.2143 | 0.1942 | 0.2929 | 0.4988 | 0.2229 | 0.1831 | 0.2064 | 0.1997 | 0.0863 | 0.1831 | 0.3724 | 0.183 | 0.2462 | 0.3063 | 0.4221 | 0.5006 | 0.422 | 0.5368 | 0.3342 | 0.9358 | 0.6568
Load_TR6_F4_54 | customer | 0.3075 | 0.1481 | 0.0865 | 0.3125 | 0.1195 | 0.2422 | 0.1438 | 0.055 | 0.1172 | 0.3462 | 0.055 | 0.3073 | 0.1561 | 0.076 | 0.1389 | 0.3035 | 0.0917 | 0.1662 | 0.3007 | 0.0645 | 0.2257 | 0.2634 | 0.334 | 0.2645 | 0.3937 | 0.1506 | 0.1483 | 0.2101 | 0.1778 | 0.2483 | 0.1006 | 0.1913 | 0.2292 | 0.2722 | 1.4376 | 0.2261 | 1.9316 | 0.3763 | 0.374 | 0.6881 | 0.6298 | 1.232 | 0.7653 | 0.892 | 0.7135 | 0.7014 | 0.9692 | 0.867
Load_TR6_F4_55 | customer | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 1.3337 | 0.047 | 0.047 | 0.047 | 0.0921 | 0.0698 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.0904 | 0.3006 | 0.047 | 0.047 | 0.047 | 0.0525 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.3566 | 0.214 | 0.3509 | 0.531 | 0.358 | 0.047 | 0.047 | 0.047
Load_TR6_F4_56 | prosumer | 0.0808 | 0.261 | 0.056 | 0.1305 | 0.2114 | 0.056 | 0.056 | 0.2528 | 0.3763 | 0.1999 | 0.142 | 0.085 | 0.1015 | 0.2114 | 0.1222 | 0.1278 | 0.1685 | 0.1098 | 0.2777 | 0.265 | 0.2605 | 0.3497 | 0.2696 | 0.2173 | 0.3845 | 0.0614 | 0.1702 | 0.1931 | 0.4882 | 0.311 | 0.3144 | 0.4335 | 0.2432 | 0.4269 | 0.6001 | 0.2398 | 0.5507 | 0.2043 | 0.3333 | 0.2349 | 0.2157 | 0.5118 | 0.4583 | 0.3333 | 0.1305 | 0.056 | 0.2511 | 0.0908
Load_TR6_F4_57 | prosumer | 0.1504 | 0.1078 | 0.0977 | 0.108 | 0.1556 | 0.2063 | 0.051 | 0.3109 | 0.051 | 0.1547 | 0.0581 | 0.2001 | 0.0873 | 0.2533 | 0.1086 | 0.1539 | 0.1769 | 0.1495 | 0.4997 | 0.3538 | 0.1504 | 0.1337 | 0.1714 | 0.1646 | 0.1547 | 0.2072 | 0.0666 | 0.1391 | 0.2072 | 0.1547 | 0.051 | 0.2001 | 0.1618 | 0.1078 | 0.2541 | 0.051 | 0.2825 | 0.1594 | 0.2679 | 0.3194 | 0.5475 | 2.0546 | 0.3039 | 0.3449 | 0.2355 | 0.1757 | 0.108 | 0.051
Load_TR6_F4_58 | customer | 0.1914 | 0.03 | 0.1181 | 0.0594 | 0.096 | 0.143 | 0.1299 | 0.03 | 0.2414 | 0.0975 | 0.096 | 0.2429 | 0.03 | 0.3089 | 0.03 | 1.0561 | 0.4944 | 0.1035 | 1.5583 | 0.473 | 1.8534 | 0.2859 | 0.4622 | 0.1755 | 0.4719 | 0.1295 | 0.2282 | 0.2548 | 0.0458 | 0.2246 | 0.5954 | 0.0575 | 0.4251 | 0.2072 | 0.3424 | 1.2728 | 0.1959 | 0.2598 | 0.3316 | 0.5032 | 0.4258 | 0.6419 | 0.4875 | 0.4493 | 0.3908 | 0.4022 | 0.3354 | 0.269
Load_TR6_F4_59 | prosumer | 0.1549 | 0.05 | 0.05 | 0.05 | 0.1496 | 0.0552 | 0.05 | 0.0762 | 0.1286 | 0.05 | 0.1549 | 0.05 | 0.1391 | 0.0657 | 0.1024 | 0.1024 | 0.05 | 0.1077 | 0.9919 | 0.0801 | 0.186 | 0.1015 | 0.1086 | 0.1161 | 0.05 | 0.1549 | 0.1949 | 0.257 | 0.2424 | 0.2883 | 0.2361 | 0.3203 | 0.1956 | 0.129 | 0.0713 | 0.2223 | 0.2303 | 0.1623 | 1.2804 | 2.7603 | 2.8947 | 0.5147 | 1.4847 | 0.199 | 0.186 | 0.3197 | 0.4122 | 0.1077
Load_TR6_F4_6 | customer | 0.09 | 0.0979 | 0.058 | 0.058 | 0.1299 | 0.058 | 0.1299 | 0.058 | 0.1299 | 0.058 | 0.058 | 0.058 | 0.1299 | 0.058 | 0.1299 | 0.058 | 0.1139 | 0.074 | 0.058 | 0.1219 | 0.066 | 0.1259 | 0.062 | 0.09 | 0.0979 | 0.082 | 0.1059 | 0.058 | 0.058 | 0.1441 | 0.1848 | 0.2415 | 0.3034 | 0.1751 | 0.16 | 0.2996 | 0.6085 | 1.6758 | 0.099 | 0.3068 | 0.5126 | 0.632 | 0.8572 | 0.7085 | 0.1259 | 0.058 | 0.1299 | 0.058
Load_TR6_F4_60 | prosumer | 0.1501 | 0.1214 | 0.057 | 0.2002 | 0.0713 | 0.1286 | 0.1429 | 0.057 | 0.1859 | 0.0856 | 0.057 | 0.057 | 0.2145 | 0.057 | 0.0713 | 0.2002 | 0.0765 | 1.2815 | 0.2295 | 0.0842 | 0.0805 | 0.3453 | 0.3098 | 0.2306 | 0.296 | 0.1756 | 0.1917 | 0.3378 | 0.3143 | 0.3224 | 0.5965 | 0.1768 | 0.2182 | 0.057 | 0.057 | 0.2238 | 0.2571 | 0.8684 | 1.2055 | 0.5252 | 1.4659 | 1.0177 | 0.9015 | 0.5698 | 0.7884 | 0.7988 | 0.7963 | 0.057
Load_TR6_F4_61 | prosumer | 0.1319 | 0.2435 | 0.053 | 0.1813 | 0.1941 | 0.0569 | 0.1189 | 0.2526 | 0.053 | 0.2006 | 0.1748 | 0.053 | 0.053 | 0.2124 | 0.163 | 0.053 | 0.0621 | 0.2435 | 0.053 | 0.1708 | 0.2046 | 0.1073 | 0.2681 | 0.0903 | 0.2789 | 0.2348 | 2.642 | 1.0236 | 1.4475 | 0.1502 | 0.1709 | 0.3098 | 0.1749 | 0.2514 | 0.2872 | 0.097 | 0.3159 | 0.1822 | 0.3003 | 0.5351 | 0.4918 | 2.5086 | 0.8463 | 0.4639 | 0.5619 | 0.3413 | 0.6119 | 0.1915
Load_TR6_F4_62 | customer | 0.2552 | 0.031 | 0.031 | 0.1676 | 0.1425 | 0.1055 | 0.125 | 0.1106 | 0.1055 | 0.2046 | 0.031 | 0.1676 | 0.0549 | 0.4686 | 0.0868 | 0.7159 | 1.8122 | 0.056 | 0.1479 | 0.2544 | 0.4779 | 1.928 | 0.3262 | 0.097 | 0.3008 | 0.1739 | 0.1296 | 0.5776 | 0.0751 | 0.031 | 0.031 | 0.1425 | 0.1304 | 0.1095 | 0.1674 | 0.1701 | 0.2488 | 0.2886 | 0.1504 | 0.3273 | 0.3338 | 0.2439 | 0.6525 | 0.5887 | 0.4127 | 0.1969 | 0.1426 | 0.0867
Load_TR6_F4_63 | customer | 0.6091 | 0.4927 | 0.034 | 0.2046 | 0.1054 | 0.1015 | 0.2086 | 0.1015 | 0.1372 | 0.1579 | 0.0807 | 0.1768 | 0.034 | 0.1015 | 0.2006 | 0.1019 | 0.0415 | 0.4669 | 0.126 | 0.1182 | 0.2351 | 0.3171 | 0.4561 | 0.3788 | 0.4908 | 0.4595 | 2.1187 | 2.593 | 1.4259 | 0.1294 | 0.4192 | 0.2815 | 0.37 | 0.085 | 0.2965 | 0.3407 | 0.1387 | 0.4091 | 0.2574 | 0.3108 | 0.511 | 0.3901 | 0.5439 | 0.2211 | 0.2607 | 0.3046 | 0.2583 | 0.1768
Load_TR6_F4_64 | customer | 0.1784 | 0.1768 | 0.0813 | 0.1784 | 0.054 | 0.2906 | 0.0919 | 0.1993 | 0.1832 | 0.054 | 0.3285 | 0.054 | 0.0975 | 0.285 | 0.0664 | 0.1659 | 0.2256 | 0.6269 | 0.2178 | 0.1977 | 0.1784 | 0.2041 | 0.1637 | 0.3634 | 0.4752 | 0.3426 | 0.3168 | 0.2048 | 0.6416 | 0.3641 | 0.054 | 0.3217 | 0.0608 | 0.0745 | 0.3555 | 0.1505 | 0.1308 | 0.287 | 0.0971 | 0.5404 | 0.5895 | 0.8039 | 0.5984 | 0.7031 | 0.5002 | 0.277 | 0.3879 | 0.5057
Load_TR6_F4_65 | prosumer | 0.159 | 0.051 | 0.178 | 0.051 | 0.0764 | 0.1526 | 0.0574 | 0.1717 | 0.051 | 0.178 | 0.051 | 0.051 | 0.178 | 0.051 | 0.178 | 0.051 | 0.1717 | 0.0574 | 0.2781 | 0.2656 | 0.4177 | 0.2247 | 0.3051 | 0.5204 | 0.5198 | 0.0701 | 0.159 | 0.051 | 0.0764 | 0.1526 | 0.3568 | 0.5164 | 0.301 | 0.574 | 0.4453 | 0.3403 | 0.3973 | 0.5077 | 0.471 | 0.7243 | 1.1031 | 0.7238 | 0.6469 | 0.5006 | 0.5036 | 0.8195 | 0.2945 | 0.1526
Load_TR6_F4_66 | prosumer | 0.1656 | 0.048 | 0.1656 | 0.048 | 0.048 | 0.048 | 0.1656 | 0.048 | 0.048 | 0.048 | 0.1303 | 0.0833 | 0.048 | 0.1656 | 0.0614 | 0.0662 | 0.3088 | 0.1244 | 0.0902 | 0.1244 | 0.2623 | 0.1656 | 0.048 | 0.0892 | 0.1244 | 0.048 | 0.1244 | 0.0892 | 0.1127 | 0.1009 | 0.048 | 0.1656 | 0.048 | 0.048 | 0.1918 | 0.0598 | 0.048 | 0.1656 | 0.2259 | 0.3573 | 0.1538 | 0.1266 | 0.2588 | 0.1526 | 0.1926 | 0.2247 | 0.2081 | 0.2117
Load_TR6_F4_67 | customer | 0.2226 | 0.1848 | 0.047 | 0.0929 | 0.1695 | 0.047 | 0.047 | 0.0966 | 0.1771 | 0.047 | 0.2154 | 0.047 | 0.047 | 0.0626 | 0.2197 | 0.1006 | 0.0547 | 0.2077 | 0.047 | 0.7102 | 1.1559 | 1.585 | 1.3018 | 0.5585 | 0.1541 | 0.047 | 0.047 | 0.2154 | 0.047 | 0.047 | 0.2001 | 0.0623 | 0.1541 | 0.1082 | 0.111 | 1.7135 | 0.0865 | 0.2452 | 0.1662 | 1.5487 | 1.623 | 1.054 | 0.6658 | 0.4311 | 0.1465 | 0.047 | 0.1848 | 0.0776
Load_TR6_F4_68 | prosumer | 0.5301 | 0.7267 | 0.1286 | 0.152 | 0.1976 | 0.129 | 0.3727 | 0.5032 | 0.1696 | 0.1034 | 0.2206 | 0.052 | 0.272 | 0.0777 | 0.1286 | 0.144 | 0.0827 | 0.267 | 0.1255 | 0.2066 | 0.2331 | 0.6298 | 0.1996 | 1.5655 | 0.6805 | 0.555 | 0.2206 | 0.764 | 0.2547 | 0.3936 | 0.0734 | 0.123 | 0.2053 | 1.7737 | 0.7039 | 0.3421 | 0.2453 | 0.4088 | 0.5171 | 0.2473 | 0.5477 | 0.6596 | 0.2116 | 0.3193 | 0.4694 | 0.1518 | 0.2431 | 0.1065
Load_TR6_F4_69 | prosumer | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.0847 | 0.0797 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.0679 | 1.3656 | 0.2005 | 0.2959 | 0.3052 | 0.5478 | 0.2682 | 0.262 | 0.175 | 0.116 | 0.102 | 0.0655 | 0.1008 | 0.104 | 0.1108 | 0.0919 | 0.1542 | 0.3146 | 0.2937 | 0.5233 | 0.3005 | 0.3103 | 0.4634 | 0.2601 | 0.106
Load_TR6_F4_7 | customer | 0.1799 | 0.045 | 0.2196 | 0.1208 | 0.045 | 0.1482 | 0.1164 | 0.1516 | 0.1888 | 0.1082 | 0.0576 | 0.045 | 0.3959 | 0.2039 | 0.2974 | 0.0892 | 0.5306 | 0.045 | 0.1208 | 0.0849 | 0.2916 | 0.045 | 0.1444 | 0.196 | 0.045 | 0.2711 | 0.0693 | 0.0619 | 0.104 | 0.193 | 0.1474 | 0.2532 | 0.2812 | 0.9835 | 0.0535 | 0.2887 | 0.3123 | 0.5957 | 0.6604 | 0.6206 | 0.5051 | 0.5635 | 0.4014 | 0.5395 | 0.876 | 0.5849 | 0.2954 | 0.045
Load_TR6_F4_70 | customer | 0.4295 | 0.7923 | 0.045 | 0.045 | 0.1431 | 0.1405 | 0.0896 | 0.0641 | 0.1659 | 0.045 | 0.1532 | 0.0768 | 0.0896 | 0.1405 | 0.045 | 0.1659 | 0.0641 | 0.045 | 0.045 | 0.0896 | 0.1938 | 0.154 | 0.154 | 0.2517 | 0.045 | 0.185 | 0.045 | 0.0705 | 0.1596 | 0.045 | 0.1961 | 0.3254 | 1.6161 | 0.3354 | 0.1086 | 0.045 | 0.1596 | 0.13 | 0.045 | 0.185 | 0.1515 | 0.5479 | 0.5013 | 0.4422 | 0.5618 | 0.7565 | 0.8811 | 0.9499
Load_TR6_F4_71 | customer | 0.302 | 0.1409 | 0.169 | 0.053 | 0.1173 | 0.0714 | 0.0576 | 0.1311 | 0.053 | 0.1127 | 0.076 | 0.0622 | 0.1265 | 0.0686 | 0.0576 | 0.5405 | 0.5188 | 0.3519 | 0.2409 | 1.187 | 0.189 | 0.1475 | 0.0943 | 0.0943 | 0.053 | 0.1127 | 0.076 | 0.053 | 0.0668 | 0.1219 | 0.0576 | 0.2707 | 0.053 | 0.1356 | 0.2458 | 0.3176 | 0.2236 | 0.3755 | 0.3049 | 0.2131 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.1356 | 0.053 | 0.1356
Load_TR6_F4_72 | customer | 1.0939 | 0.732 | 1.6231 | 0.1854 | 0.1044 | 0.2769 | 0.2162 | 0.047 | 0.1393 | 0.1239 | 0.047 | 0.2162 | 0.047 | 0.1701 | 0.1542 | 0.0642 | 0.0877 | 0.2415 | 0.2426 | 0.05 | 0.0529 | 0.1175 | 0.2459 | 0.1039 | 0.1032 | 0.2395 | 0.0498 | 0.3723 | 0.4298 | 0.1648 | 0.3926 | 0.9439 | 0.3699 | 0.3691 | 0.2102 | 0.381 | 0.3295 | 0.3406 | 0.2284 | 0.2374 | 0.3679 | 0.2067 | 0.3269 | 0.3863 | 0.2769 | 0.4058 | 0.3235 | 0.1278
Load_TR6_F4_73 | customer | 0.0753 | 0.1308 | 0.1744 | 0.13 | 0.1674 | 0.1333 | 0.0799 | 0.1885 | 0.1441 | 0.048 | 0.2705 | 0.062 | 0.0662 | 0.2172 | 0.143 | 0.0709 | 1.362 | 0.1675 | 1.405 | 0.3899 | 0.0951 | 0.3136 | 1.6801 | 0.1852 | 0.3536 | 0.1392 | 0.1162 | 0.2576 | 0.305 | 1.7963 | 0.1552 | 0.3372 | 0.7947 | 0.8484 | 0.062 | 0.2295 | 0.2993 | 0.259 | 0.1838 | 0.3382 | 0.4034 | 0.1613 | 0.4839 | 0.3876 | 0.0691 | 0.2635 | 0.048 | 0.2025
Load_TR6_F4_74 | customer | 0.1129 | 0.1129 | 0.0813 | 0.1445 | 0.055 | 0.1709 | 0.055 | 0.055 | 0.0655 | 0.1603 | 0.055 | 0.055 | 0.2086 | 0.1241 | 0.3019 | 0.3977 | 1.126 | 0.7782 | 2.1133 | 0.1024 | 0.1235 | 0.3246 | 0.2457 | 0.2949 | 0.1919 | 0.2753 | 0.2536 | 0.3701 | 0.4133 | 0.2416 | 0.408 | 3.5595 | 0.4872 | 0.3499 | 0.1929 | 0.077 | 0.1969 | 0.1554 | 0.1897 | 0.3806 | 0.3771 | 0.4759 | 1.1061 | 0.4238 | 0.667 | 1.2154 | 0.0919 | 0.134
Load_TR6_F4_75 | customer | 0.593 | 0.3835 | 0.5586 | 0.2621 | 0.0942 | 0.2436 | 0.046 | 0.2317 | 0.1061 | 0.1183 | 0.1504 | 0.1193 | 1.4831 | 0.4236 | 0.2904 | 0.1817 | 1.5841 | 0.2512 | 0.1528 | 0.3624 | 0.5651 | 2.1664 | 0.2643 | 1.6785 | 0.3664 | 1.7572 | 0.4756 | 0.4886 | 0.5411 | 0.225 | 0.3986 | 0.3447 | 0.3165 | 0.4029 | 0.2034 | 0.255 | 0.2985 | 0.2182 | 0.2537 | 0.4237 | 0.6294 | 0.494 | 0.5565 | 0.6854 | 0.734 | 0.8995 | 0.7701 | 0.1633
Load_TR6_F4_76 | prosumer | 0.127 | 0.036 | 0.1056 | 0.0628 | 0.036 | 0.0521 | 0.1163 | 0.036 | 0.036 | 0.1002 | 0.0681 | 0.036 | 0.1324 | 0.036 | 0.2196 | 0.036 | 0.1324 | 0.036 | 0.1324 | 0.036 | 0.036 | 0.297 | 1.1652 | 0.8426 | 1.3369 | 0.036 | 0.1324 | 0.036 | 0.1056 | 0.0628 | 0.1324 | 0.036 | 0.0521 | 0.1163 | 0.036 | 0.127 | 0.0414 | 0.036 | 0.036 | 0.1404 | 0.2555 | 1.0564 | 1.0472 | 0.5366 | 0.7841 | 0.4022 | 0.129 | 0.036
Load_TR6_F4_77 | customer | 0.9612 | 0.8189 | 0.6701 | 0.3593 | 0.5278 | 0.39 | 0.3084 | 1.1998 | 0.1033 | 0.054 | 0.1156 | 0.0663 | 0.0704 | 0.2039 | 0.0745 | 0.1074 | 0.091 | 0.091 | 0.054 | 0.054 | 0.054 | 0.128 | 0.3158 | 0.3438 | 0.7308 | 0.1554 | 0.1699 | 0.054 | 0.0871 | 0.2262 | 0.2522 | 0.1782 | 1.0596 | 0.8014 | 0.3948 | 0.2006 | 0.2999 | 0.2105 | 0.2376 | 0.4538 | 1.3285 | 1.8638 | 0.4247 | 0.3753 | 0.5699 | 0.5371 | 0.3613 | 0.1746
Load_TR6_F4_78 | customer | 0.05 | 0.171 | 0.1635 | 0.2309 | 0.4734 | 0.2205 | 0.4287 | 0.1489 | 0.1774 | 0.0627 | 0.2373 | 0.1264 | 0.1736 | 0.1995 | 1.1793 | 1.6956 | 1.5696 | 0.5972 | 0.6179 | 0.2868 | 0.3996 | 1.3549 | 0.1873 | 0.2376 | 0.1715 | 0.2824 | 0.2572 | 0.4234 | 0.5057 | 0.2763 | 0.4694 | 0.1527 | 1.6656 | 1.2487 | 0.9829 | 1.1827 | 0.3055 | 0.2487 | 0.3406 | 0.2394 | 0.3375 | 0.0882 | 0.3205 | 0.2412 | 0.423 | 0.4348 | 0.371 | 0.312
Load_TR6_F4_79 | prosumer | 0.1317 | 0.1765 | 0.2385 | 0.1055 | 0.0777 | 0.2965 | 0.0675 | 0.245 | 0.2225 | 0.053 | 0.2995 | 0.0892 | 0.0653 | 0.3846 | 0.0705 | 0.212 | 0.2248 | 0.2029 | 1.8478 | 0.2478 | 0.2683 | 0.4512 | 0.1459 | 0.1181 | 0.2706 | 0.053 | 0.053 | 0.0898 | 0.2618 | 0.1688 | 0.053 | 0.1503 | 0.1579 | 0.1181 | 0.2258 | 0.053 | 0.0924 | 0.3751 | 0.053 | 0.053 | 0.3342 | 0.1333 | 0.1317 | 0.2489 | 0.188 | 0.0836 | 0.2427 | 0.2248
Load_TR6_F4_8 | customer | 0.1272 | 0.209 | 0.1443 | 0.1076 | 0.166 | 0.1237 | 0.1291 | 0.046 | 0.1153 | 0.046 | 0.2835 | 0.151 | 0.0671 | 0.2981 | 0.2687 | 0.3353 | 0.1753 | 0.1838 | 0.2268 | 0.2938 | 0.7008 | 0.6363 | 0.422 | 0.3624 | 0.071 | 0.3092 | 0.2845 | 0.2524 | 0.1807 | 0.0697 | 0.2735 | 0.1373 | 0.1917 | 0.3526 | 0.5486 | 2.7269 | 2.7342 | 0.6982 | 0.3114 | 0.2122 | 0.4059 | 0.5449 | 0.2537 | 0.578 | 0.4061 | 0.5303 | 0.1955 | 0.2179
Load_TR6_F4_80 | prosumer | 0.2136 | 0.043 | 0.043 | 0.0973 | 0.1593 | 0.043 | 0.0895 | 0.1671 | 0.043 | 0.043 | 0.0973 | 0.1593 | 0.043 | 0.2136 | 0.043 | 0.0726 | 0.2824 | 0.2212 | 0.0878 | 0.3477 | 0.1941 | 0.1276 | 0.2956 | 0.2705 | 0.1394 | 0.1671 | 0.043 | 0.2176 | 0.043 | 0.0708 | 0.1206 | 0.1361 | 0.3357 | 0.3195 | 0.49 | 0.1147 | 0.2926 | 0.6207 | 0.6928 | 0.5272 | 0.7303 | 1.0217 | 0.9061 | 0.6009 | 0.6705 | 0.831 | 0.9995 | 0.6507
Load_TR6_F4_81 | prosumer | 0.1728 | 0.1488 | 0.1515 | 0.2622 | 0.1579 | 0.1852 | 0.1683 | 0.053 | 0.1215 | 0.1709 | 0.1807 | 0.1728 | 0.2473 | 0.053 | 0.3006 | 0.3354 | 1.2371 | 0.3016 | 0.3932 | 0.3972 | 0.3368 | 1.0621 | 0.6625 | 0.3886 | 0.0929 | 0.232 | 0.1743 | 0.3792 | 0.1691 | 0.3555 | 0.1618 | 0.2703 | 0.3229 | 0.2858 | 0.3273 | 0.1983 | 1.6876 | 0.2883 | 0.2392 | 0.7353 | 1.6555 | 2.2482 | 0.915 | 0.6569 | 1.542 | 0.7453 | 0.6293 | 0.6921
Load_TR6_F4_82 | prosumer | 0.2614 | 0.1504 | 0.0916 | 0.3191 | 0.0588 | 0.347 | 0.0685 | 0.2293 | 0.1861 | 0.124 | 0.2538 | 0.1279 | 0.1937 | 0.1854 | 0.2156 | 1.0153 | 0.3903 | 0.146 | 0.1504 | 0.054 | 0.1675 | 0.2953 | 0.1856 | 0.4612 | 0.119 | 0.1229 | 0.3951 | 0.054 | 0.2549 | 0.5166 | 0.6905 | 0.3861 | 0.7 | 0.6783 | 1.6196 | 4.291 | 2.5453 | 0.1406 | 0.4521 | 0.7723 | 0.5788 | 1.4949 | 0.5698 | 0.2831 | 0.1677 | 0.0948 | 0.3207 | 0.054
Load_TR6_F4_83 | prosumer | 0.1833 | 0.2404 | 0.1517 | 0.223 | 0.1409 | 0.1484 | 0.2789 | 0.046 | 0.1445 | 0.2129 | 0.0693 | 0.2821 | 0.1218 | 0.1522 | 0.2674 | 0.3476 | 0.4452 | 1.1229 | 0.3797 | 0.3114 | 0.4319 | 1.1413 | 0.4484 | 0.0771 | 0.2982 | 0.098 | 0.0536 | 0.3154 | 0.1042 | 0.1311 | 0.2961 | 0.046 | 0.4704 | 0.1786 | 0.1123 | 0.249 | 0.2829 | 0.1967 | 0.2577 | 0.4576 | 1.0054 | 0.7273 | 0.9693 | 0.5957 | 1.725 | 0.708 | 0.5263 | 0.5321
Load_TR6_F4_84 | customer | 0.1863 | 0.1472 | 0.1732 | 0.2747 | 0.052 | 0.0857 | 0.2497 | 0.0877 | 0.2684 | 0.1795 | 0.1597 | 0.1607 | 0.1795 | 0.2257 | 0.1568 | 0.1444 | 0.25 | 0.052 | 0.2001 | 0.0639 | 0.3198 | 0.1162 | 0.171 | 0.1866 | 0.1785 | 0.058 | 0.266 | 0.1819 | 0.052 | 0.3959 | 1.2573 | 0.6164 | 0.9556 | 1.5565 | 1.9744 | 1.5019 | 0.437 | 0.2018 | 0.1848 | 0.2093 | 0.1866 | 0.1966 | 0.2513 | 0.0904 | 0.2094 | 0.2262 | 0.1027 | 0.0563
Load_TR6_F4_85 | prosumer | 0.6131 | 0.2 | 0.047 | 0.2566 | 0.0612 | 0.115 | 0.047 | 0.1717 | 0.1461 | 0.1075 | 0.1395 | 0.1858 | 0.047 | 0.1929 | 0.1249 | 0.047 | 0.2304 | 0.3872 | 0.2434 | 0.2359 | 0.3124 | 0.2529 | 0.1873 | 0.1787 | 0.0966 | 0.2446 | 1.2986 | 0.2547 | 0.1046 | 0.2979 | 0.2664 | 0.047 | 0.1292 | 0.1886 | 0.0699 | 0.121 | 0.0651 | 0.349 | 0.1189 | 0.3787 | 0.2406 | 0.6588 | 0.3029 | 0.3207 | 0.1461 | 0.047 | 0.1075 | 0.0546
Load_TR6_F4_86 | customer | 0.0727 | 0.1196 | 0.0915 | 0.1683 | 0.1515 | 0.1383 | 0.204 | 0.1346 | 0.1702 | 0.1215 | 0.1065 | 0.1665 | 0.054 | 0.2115 | 0.0615 | 0.0727 | 0.2958 | 0.4877 | 0.2519 | 0.2744 | 0.3749 | 1.6141 | 0.3934 | 0.5864 | 1.4142 | 0.8744 | 0.4191 | 0.3119 | 0.2326 | 0.3471 | 0.1149 | 0.2377 | 0.2125 | 0.2375 | 0.19 | 0.1365 | 0.1149 | 0.2124 | 0.8871 | 0.4017 | 0.4929 | 0.4979 | 0.5161 | 0.4558 | 0.7765 | 2.1796 | 0.4599 | 0.1324
Load_TR6_F4_87 | customer | 0.1648 | 0.0568 | 0.026 | 0.2317 | 0.0672 | 0.026 | 0.026 | 0.2343 | 0.0646 | 0.026 | 0.026 | 0.1879 | 0.111 | 0.1262 | 0.4975 | 0.146 | 0.6465 | 0.5299 | 0.5584 | 0.7484 | 0.5453 | 0.4157 | 0.234 | 0.3272 | 0.2128 | 0.3512 | 1.7433 | 1.2534 | 0.1956 | 0.026 | 0.1872 | 0.1117 | 0.099 | 0.1999 | 0.026 | 0.122 | 0.1769 | 0.0475 | 0.2514 | 0.0732 | 0.056 | 0.2437 | 0.1697 | 0.2222 | 1.3685 | 0.6312 | 0.4549 | 0.142
Load_TR6_F4_88 | customer | 0.2336 | 0.1361 | 0.059 | 0.2004 | 0.059 | 0.1104 | 0.149 | 0.059 | 0.2004 | 0.059 | 0.1875 | 0.0719 | 0.059 | 0.059 | 0.2443 | 0.2996 | 0.2433 | 0.3589 | 0.2322 | 0.2923 | 0.9015 | 0.5465 | 0.1683 | 0.0911 | 0.1297 | 0.1297 | 0.059 | 0.059 | 0.2329 | 0.2898 | 0.0738 | 0.3493 | 0.3378 | 0.1805 | 0.2218 | 0.4635 | 0.4438 | 1.4101 | 0.5824 | 0.6825 | 0.4531 | 0.3283 | 0.6732 | 0.9685 | 0.1757 | 0.3037 | 0.0847 | 0.1747
Load_TR6_F4_89 | prosumer | 0.1091 | 0.1519 | 0.052 | 0.209 | 0.052 | 0.052 | 0.052 | 0.2019 | 0.0591 | 0.1519 | 0.1091 | 0.1091 | 0.1519 | 0.052 | 0.2068 | 0.3638 | 0.2762 | 0.1131 | 0.455 | 0.0882 | 0.2776 | 1.0528 | 1.5006 | 0.2141 | 0.4982 | 0.0597 | 0.5093 | 0.1108 | 0.2361 | 0.0892 | 0.236 | 0.0966 | 0.1608 | 0.3327 | 0.1347 | 0.3078 | 0.052 | 0.209 | 0.052 | 0.052 | 0.5694 | 0.4466 | 1.0521 | 1.1626 | 0.9625 | 0.6937 | 0.0591 | 0.2019
Load_TR6_F4_9 | customer | 0.05 | 0.2314 | 0.05 | 0.1489 | 0.1324 | 0.083 | 0.1984 | 0.05 | 0.2314 | 0.05 | 0.05 | 0.05 | 0.1902 | 0.0912 | 0.05 | 0.0747 | 0.4134 | 0.2076 | 0.2184 | 0.1162 | 0.1394 | 0.1823 | 0.2149 | 0.05 | 0.1984 | 0.083 | 0.1491 | 0.2584 | 0.4931 | 0.3075 | 0.3458 | 0.3415 | 0.3189 | 0.6418 | 0.2928 | 0.4345 | 0.2397 | 0.1353 | 0.4797 | 0.1718 | 0.3206 | 0.572 | 0.3459 | 0.6346 | 0.3421 | 0.4153 | 0.4146 | 0.5358
Load_TR6_F4_90 | prosumer | 0.0944 | 0.04 | 0.04 | 0.0944 | 0.1352 | 0.04 | 0.1897 | 0.04 | 0.1216 | 0.108 | 0.0468 | 0.1829 | 0.04 | 0.04 | 0.2704 | 0.2957 | 0.04 | 0.2431 | 0.27 | 0.2536 | 0.4267 | 0.2479 | 0.2079 | 0.4306 | 0.0902 | 0.1352 | 0.0944 | 0.074 | 0.1557 | 0.04 | 0.1625 | 0.0672 | 0.074 | 0.1557 | 0.04 | 0.04 | 0.04 | 0.1897 | 0.04 | 0.04 | 0.1897 | 0.04 | 0.04 | 0.0604 | 0.1693 | 0.04 | 0.1216 | 0.108
Load_TR6_F4_91 | customer | 0.2276 | 0.048 | 0.2272 | 0.1704 | 0.1701 | 0.2276 | 0.048 | 0.3089 | 0.0888 | 0.1133 | 0.2844 | 0.048 | 0.0643 | 0.315 | 0.0663 | 0.1906 | 0.2071 | 0.1029 | 0.2621 | 0.0807 | 2.9241 | 2.9344 | 0.4729 | 0.3192 | 0.0725 | 0.048 | 0.2276 | 0.1701 | 0.0888 | 0.1868 | 0.1701 | 0.2276 | 0.0602 | 0.3698 | 0.1464 | 0.1781 | 0.2289 | 0.1796 | 0.0863 | 0.445 | 0.586 | 0.3306 | 0.4188 | 0.696 | 0.2925 | 0.1051 | 0.048 | 0.1112
Load_TR6_F4_92 | customer | 0.05 | 0.1332 | 0.05 | 0.1332 | 0.05 | 0.0639 | 0.1193 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1332 | 0.05 | 0.05 | 0.0639 | 0.1193 | 0.05 | 0.05 | 0.1332 | 0.05 | 0.1332 | 0.1284 | 0.1332 | 0.05 | 0.2556 | 0.3439 | 0.516 | 0.2166 | 0.2529 | 0.1801 | 0.2704 | 0.4909 | 0.2861 | 0.1256 | 0.2225 | 0.0893 | 0.2708 | 0.2325 | 0.3736 | 1.3265 | 0.4714 | 0.5002 | 0.4069 | 0.4534 | 0.273 | 0.503 | 0.4559 | 0.311
Load_TR6_F4_93 | customer | 0.057 | 0.057 | 0.057 | 0.1755 | 0.057 | 0.1755 | 0.057 | 0.1636 | 0.0688 | 0.1636 | 0.0688 | 0.057 | 0.0985 | 0.134 | 0.057 | 0.0866 | 0.3122 | 0.7263 | 0.2819 | 0.3187 | 0.2665 | 0.2031 | 0.1201 | 0.2157 | 0.057 | 0.1755 | 0.1077 | 0.3644 | 0.3035 | 0.3673 | 0.3908 | 0.1453 | 0.1987 | 0.3021 | 0.057 | 0.2873 | 0.2249 | 0.0748 | 0.057 | 0.1636 | 0.0688 | 0.0925 | 0.1399 | 0.0925 | 0.1399 | 0.057 | 0.057 | 0.1399
Load_TR6_F4_94 | customer | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 1.4943 | 1.2897 | 0.0333 | 0.1516 | 0.321 | 0.3095 | 0.2275 | 0.2736 | 0.2683 | 0.1454 | 0.032 | 0.032 | 0.032 | 0.0789 | 0.032 | 0.1908 | 0.2482 | 0.0793 | 0.4764 | 0.4805 | 0.2702 | 0.3297 | 0.387 | 0.5936 | 0.1987 | 0.3812 | 0.3766 | 1.1606 | 0.4951 | 0.5389 | 0.0643 | 0.0452
Load_TR6_F4_95 | prosumer | 0.031 | 0.1267 | 0.0479 | 0.0816 | 0.0929 | 0.031 | 0.031 | 0.0816 | 0.0929 | 0.031 | 0.1435 | 0.031 | 0.1435 | 0.031 | 0.0985 | 0.076 | 0.031 | 0.031 | 0.1435 | 0.031 | 0.1041 | 0.0704 | 0.031 | 0.1223 | 0.0665 | 0.0873 | 0.0873 | 0.031 | 0.0929 | 0.0816 | 0.2816 | 0.185 | 0.031 | 0.1435 | 0.0395 | 0.3015 | 0.1736 | 0.1392 | 0.3241 | 0.4879 | 0.856 | 0.7266 | 0.6855 | 0.4137 | 0.1435 | 0.031 | 0.031 | 0.1435
Load_TR6_F4_96 | customer | 0.055 | 0.055 | 0.2143 | 0.055 | 0.1636 | 0.1057 | 0.0767 | 0.1925 | 0.055 | 0.055 | 0.055 | 0.1419 | 0.1274 | 0.0695 | 0.1998 | 0.055 | 0.1708 | 0.0984 | 0.055 | 0.055 | 0.2106 | 0.0622 | 0.055 | 0.0912 | 0.1781 | 0.055 | 0.055 | 0.1925 | 0.0767 | 0.055 | 0.055 | 0.2143 | 0.0655 | 0.207 | 0.0622 | 0.055 | 0.1636 | 0.1057 | 0.1057 | 0.1636 | 0.055 | 0.0622 | 0.207 | 0.055 | 0.2143 | 0.055 | 0.084 | 0.1853
Load_TR6_F4_97 | customer | 0.0643 | 0.1551 | 0.053 | 0.053 | 0.1664 | 0.053 | 0.104 | 0.1154 | 0.053 | 0.1664 | 0.053 | 0.1437 | 0.0757 | 0.156 | 0.9465 | 0.1374 | 0.087 | 0.0537 | 1.1198 | 0.1327 | 0.053 | 0.053 | 0.053 | 0.1381 | 0.3316 | 0.0828 | 0.1687 | 0.1296 | 0.0757 | 0.1437 | 0.053 | 0.1494 | 0.1054 | 0.0766 | 0.053 | 0.053 | 0.1505 | 0.1664 | 0.053 | 0.053 | 0.053 | 0.1267 | 0.0927 | 0.053 | 0.053 | 0.0927 | 0.1267 | 0.053
Load_TR6_F4_98 | customer | 0.1916 | 0.2179 | 0.0801 | 0.3056 | 0.1508 | 0.1487 | 0.3145 | 0.0946 | 0.2074 | 0.2153 | 0.054 | 0.2604 | 0.2028 | 0.1765 | 0.1379 | 0.2672 | 0.1637 | 0.2067 | 0.2951 | 0.1702 | 0.8387 | 0.2305 | 0.5731 | 0.3107 | 0.3269 | 0.5026 | 0.2903 | 0.4947 | 0.1534 | 0.3353 | 0.4569 | 0.3355 | 0.5833 | 0.4219 | 0.6359 | 0.7223 | 2.3691 | 0.4901 | 0.4187 | 0.7205 | 0.7747 | 1.2072 | 1.0811 | 0.8608 | 1.8941 | 0.7583 | 2.2278 | 0.2169
Load_TR6_F4_99 | customer | 0.1863 | 0.1271 | 0.05 | 0.1489 | 0.1043 | 0.172 | 0.1414 | 0.1102 | 0.186 | 0.1274 | 0.05 | 0.2387 | 0.0747 | 0.1167 | 0.1968 | 0.093 | 0.1091 | 0.1613 | 0.0738 | 0.6814 | 2.111 | 0.828 | 0.0586 | 0.186 | 0.1274 | 0.05 | 0.1831 | 0.6447 | 0.0751 | 0.1359 | 0.1228 | 0.1473 | 0.1489 | 0.05 | 0.2634 | 0.05 | 0.1299 | 0.388 | 0.3995 | 0.7943 | 0.7216 | 0.9126 | 0.3907 | 0.4241 | 0.4069 | 0.4719 | 0.5784 | 0.0586
Load_TR6_F5_1 | customer | 0.229 | 0.1078 | 0.111 | 0.2222 | 0.0749 | 0.147 | 0.1971 | 0.053 | 0.1783 | 0.1658 | 0.1 | 0.2441 | 0.053 | 0.1893 | 0.209 | 0.2233 | 0.4139 | 1.7158 | 0.2412 | 2.1624 | 0.053 | 0.1188 | 0.7776 | 1.7235 | 1.5585 | 1.6838 | 1.5139 | 0.2996 | 0.1104 | 0.1005 | 0.2018 | 0.1423 | 0.053 | 0.206 | 0.1381 | 0.1958 | 0.2714 | 0.3874 | 0.3959 | 0.7018 | 1.0668 | 0.5633 | 0.7202 | 0.5059 | 0.8987 | 0.6762 | 1.825 | 0.8563
Load_TR6_F5_10 | customer | 0.56 | 0.5335 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.1352 | 1.1912 | 0.055 | 0.1017 | 0.2 | 0.2265 | 0.2265 | 0.2265 | 0.2265 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.2265 | 0.2265 | 0.3133 | 0.4017 | 0.4663 | 0.1461 | 0.225 | 0.4191 | 1.6851 | 0.6053 | 0.7386 | 0.7765 | 0.5454 | 0.2193 | 0.055
Load_TR6_F5_10_dup | prosumer | 0.221 | 0.05 | 0.2132 | 0.0578 | 0.0889 | 0.1821 | 0.05 | 0.221 | 0.3393 | 0.1821 | 0.0889 | 0.1277 | 0.1433 | 0.05 | 0.221 | 0.05 | 0.1433 | 0.1277 | 0.3109 | 0.339 | 0.05 | 0.2744 | 0.1912 | 0.1355 | 0.0811 | 0.4143 | 0.05 | 0.2054 | 0.0655 | 0.1122 | 0.1588 | 0.05 | 0.05 | 0.221 | 0.05 | 0.1821 | 0.0889 | 0.05 | 0.221 | 0.05 | 0.05 | 0.1199 | 0.151 | 0.05 | 0.221 | 0.05 | 0.1199 | 0.151
Load_TR6_F5_11 | prosumer | 0.3783 | 0.3821 | 0.061 | 0.2249 | 0.061 | 0.061 | 0.21 | 0.0759 | 0.061 | 0.2249 | 0.061 | 0.061 | 0.2249 | 0.061 | 0.1727 | 0.1437 | 0.061 | 0.2975 | 0.2002 | 0.4308 | 0.5055 | 0.1985 | 0.3219 | 0.5737 | 0.2965 | 0.3256 | 0.3271 | 0.2582 | 0.7951 | 1.1037 | 0.061 | 0.2249 | 0.2501 | 0.3045 | 0.2174 | 0.061 | 0.5171 | 0.3732 | 0.649 | 0.821 | 1.4332 | 0.98 | 0.6961 | 1.7437 | 0.99 | 0.6726 | 0.061 | 0.1653
Load_TR6_F5_11_dup | customer | 0.058 | 0.1373 | 0.0627 | 0.142 | 0.058 | 0.142 | 0.058 | 0.128 | 0.072 | 0.058 | 0.142 | 0.058 | 0.0627 | 0.1373 | 0.058 | 0.0908 | 0.142 | 0.2954 | 0.2156 | 0.0828 | 0.1999 | 0.534 | 0.0627 | 0.0641 | 0.072 | 0.1589 | 0.1227 | 0.1002 | 0.1837 | 0.1168 | 0.2441 | 0.3115 | 0.3599 | 0.3927 | 0.2807 | 0.4207 | 0.4138 | 0.2512 | 0.1233 | 0.0767 | 0.058 | 0.1233 | 0.0767 | 0.1187 | 0.4802 | 0.4405 | 0.447 | 0.5337
Load_TR6_F5_12 | customer | 0.4844 | 0.5063 | 0.3843 | 0.1669 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.05 | 0.217 | 0.7582 | 0.5696 | 0.1607 | 0.068 | 0.0463 | 0.046 | 0.1815 | 1.2744 | 0.0904 | 0.0759 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.0743 | 0.1226 | 0.3169 | 0.3093 | 0.4761 | 0.438 | 0.4878 | 0.4053 | 0.3227 | 0.5936 | 0.504
Load_TR6_F5_12_dup | customer | 0.0599 | 0.3026 | 0.1009 | 0.1257 | 0.2997 | 0.038 | 0.3011 | 0.0894 | 0.0729 | 0.2341 | 0.1913 | 0.1481 | 0.2773 | 0.0459 | 0.2792 | 0.1389 | 0.1895 | 0.2734 | 0.1974 | 0.1993 | 0.2561 | 1.2573 | 0.7009 | 0.2147 | 0.2619 | 0.2508 | 0.0404 | 0.1481 | 0.4124 | 0.483 | 0.2716 | 0.1062 | 0.4256 | 0.359 | 0.3033 | 0.3018 | 0.2261 | 0.4661 | 0.5064 | 0.5268 | 0.0903 | 0.1742 | 0.1623 | 0.0746 | 0.2007 | 0.5902 | 0.0511 | 0.3114
Load_TR6_F5_13 | prosumer | 0.3531 | 0.5032 | 0.7105 | 0.3688 | 0.2348 | 0.1389 | 0.048 | 0.1758 | 0.2312 | 0.0571 | 0.3332 | 0.0646 | 0.1367 | 0.2703 | 0.1463 | 0.1804 | 0.1927 | 0.5406 | 0.869 | 0.2208 | 0.1331 | 1.0974 | 1.0414 | 0.5972 | 0.5768 | 0.0863 | 0.2299 | 0.1771 | 0.048 | 0.1423 | 0.1374 | 0.3222 | 0.3079 | 0.357 | 0.3128 | 1.6821 | 0.3752 | 2.7472 | 0.6287 | 0.421 | 0.4839 | 0.6307 | 0.6996 | 0.3016 | 0.2208 | 0.1862 | 0.394 | 0.6263
Load_TR6_F5_13_dup | customer | 0.1833 | 0.051 | 0.0666 | 0.2066 | 0.051 | 0.2066 | 0.0666 | 0.051 | 0.2222 | 0.051 | 0.1755 | 0.0977 | 0.051 | 0.1444 | 0.1288 | 0.0703 | 0.2613 | 1.3614 | 0.8029 | 1.2913 | 0.191 | 0.051 | 0.2066 | 0.0666 | 0.0588 | 0.2144 | 0.051 | 0.0952 | 0.1134 | 0.0586 | 0.2198 | 0.0859 | 0.0987 | 0.2774 | 0.063 | 0.2991 | 0.3931 | 0.2102 | 0.1848 | 0.2935 | 0.4482 | 0.6293 | 0.568 | 0.4366 | 0.4674 | 0.7617 | 0.3167 | 0.4343
Load_TR6_F5_14 | prosumer | 0.2288 | 0.0841 | 0.3192 | 0.052 | 0.0643 | 0.3309 | 0.06 | 0.1749 | 0.052 | 0.2163 | 0.2152 | 0.0806 | 0.239 | 0.1642 | 0.1073 | 0.3734 | 0.097 | 0.2056 | 0.2023 | 0.2206 | 0.1528 | 0.6213 | 0.2216 | 0.2859 | 1.0427 | 0.6753 | 0.1857 | 0.1787 | 0.1183 | 0.2104 | 0.1955 | 0.2186 | 0.5026 | 0.1627 | 0.2203 | 0.202 | 0.2019 | 0.3742 | 0.4082 | 0.1081 | 0.2951 | 0.052 | 0.2283 | 0.052 | 0.1749 | 0.1321 | 0.2711 | 0.068
Load_TR6_F5_14_dup | prosumer | 0.1298 | 0.1298 | 0.1122 | 0.1075 | 0.1521 | 0.048 | 0.0629 | 0.1967 | 0.048 | 0.1967 | 0.0629 | 0.048 | 0.0563 | 0.2115 | 0.048 | 0.048 | 0.2115 | 0.048 | 0.3706 | 0.4651 | 0.6609 | 1.5417 | 0.4666 | 0.103 | 0.5811 | 1.3936 | 0.8968 | 0.1042 | 0.7368 | 0.7937 | 0.5859 | 0.1225 | 0.4432 | 1.1144 | 0.7606 | 0.1975 | 0.6037 | 0.1973 | 0.8636 | 0.9282 | 1.5454 | 0.8636 | 0.4927 | 1.5617 | 0.3854 | 0.4005 | 0.8143 | 0.048
Load_TR6_F5_15 | customer | 0.045 | 0.045 | 0.0601 | 0.1964 | 0.045 | 0.0753 | 0.1812 | 0.045 | 0.2115 | 0.045 | 0.045 | 0.2115 | 0.045 | 0.045 | 0.0526 | 0.439 | 0.0812 | 1.5282 | 0.3212 | 0.3967 | 0.181 | 0.045 | 0.2115 | 0.045 | 0.045 | 0.427 | 0.1062 | 0.1033 | 0.2647 | 0.2087 | 0.3437 | 0.4961 | 0.2324 | 0.7845 | 2.0419 | 0.8337 | 0.5623 | 0.7237 | 0.481 | 0.3564 | 0.4851 | 1.6572 | 1.1879 | 0.867 | 0.9004 | 0.8109 | 0.1888 | 0.045
Load_TR6_F5_15_dup | customer | 0.0788 | 0.2877 | 0.05 | 0.05 | 0.2949 | 0.0716 | 0.1271 | 0.225 | 0.0644 | 0.158 | 0.2086 | 0.0963 | 0.2342 | 0.086 | 0.2012 | 0.1653 | 0.1487 | 1.3683 | 0.5546 | 0.1868 | 0.1797 | 0.1495 | 0.3951 | 1.2829 | 0.1992 | 0.3631 | 0.3585 | 0.2841 | 0.6485 | 0.1822 | 0.1661 | 0.2623 | 0.1699 | 0.2649 | 0.1589 | 0.158 | 0.2866 | 0.3471 | 0.1678 | 0.4162 | 1.8851 | 0.6092 | 0.7627 | 0.9286 | 0.7314 | 0.5498 | 0.4424 | 0.616
Load_TR6_F5_16 | prosumer | 0.3784 | 0.2161 | 0.054 | 0.054 | 0.054 | 0.1203 | 0.2685 | 0.054 | 0.2611 | 0.1277 | 0.0908 | 0.2979 | 0.054 | 0.2088 | 0.0614 | 0.1203 | 0.657 | 0.1499 | 0.2425 | 0.1246 | 0.8356 | 1.4714 | 1.6979 | 0.3299 | 0.3102 | 0.7518 | 0.2934 | 0.4144 | 0.5074 | 0.3516 | 0.2895 | 0.7752 | 0.6343 | 0.6631 | 0.2795 | 0.2934 | 0.3239 | 0.4042 | 0.1919 | 0.6453 | 0.3285 | 0.4375 | 0.7376 | 0.7242 | 0.6538 | 0.825 | 0.8264 | 0.6471
Load_TR6_F5_16_dup | prosumer | 0.1071 | 0.047 | 0.1596 | 0.0996 | 0.0515 | 0.1938 | 0.1596 | 0.047 | 0.2122 | 0.047 | 0.0921 | 0.1671 | 0.047 | 0.2122 | 0.047 | 0.1596 | 0.0996 | 0.077 | 0.1822 | 0.047 | 0.1596 | 0.0996 | 0.1071 | 0.1521 | 0.047 | 0.1296 | 0.1296 | 0.047 | 0.077 | 0.1822 | 0.047 | 0.1972 | 0.062 | 0.047 | 0.0845 | 0.1747 | 0.047 | 0.047 | 0.047 | 0.2122 | 0.047 | 0.0713 | 0.2126 | 0.4777 | 0.3264 | 0.2662 | 0.3623 | 0.557
Load_TR6_F5_17 | prosumer | 0.2199 | 0.104 | 0.2894 | 0.074 | 0.1317 | 0.2227 | 0.108 | 0.2812 | 0.166 | 0.1031 | 0.3352 | 0.049 | 0.237 | 0.2013 | 0.049 | 0.2183 | 0.223 | 0.8454 | 1.3558 | 1.4402 | 1.481 | 0.247 | 0.0767 | 0.1799 | 0.1878 | 0.1883 | 0.2038 | 0.2095 | 0.7275 | 0.6003 | 0.3049 | 0.5278 | 0.7545 | 1.3441 | 0.7779 | 0.423 | 0.5186 | 0.7902 | 0.074 | 0.3516 | 0.3454 | 0.9935 | 0.2812 | 0.0569 | 0.9337 | 0.1367 | 0.1511 | 0.1869
Load_TR6_F5_17_dup | customer | 0.1002 | 0.331 | 0.0577 | 0.2261 | 0.155 | 0.1737 | 0.2093 | 0.2479 | 0.1833 | 0.1983 | 0.1608 | 0.1241 | 0.2233 | 0.1269 | 0.1473 | 0.3186 | 0.049 | 0.4075 | 0.3749 | 0.9513 | 0.248 | 0.6482 | 1.412 | 2.511 | 0.4583 | 0.1531 | 0.1269 | 0.2101 | 0.307 | 1.4659 | 0.2629 | 0.2307 | 0.924 | 0.4799 | 0.3499 | 0.2429 | 0.192 | 0.2422 | 0.1254 | 0.4449 | 0.6123 | 0.5052 | 0.2167 | 0.3606 | 0.0577 | 0.3065 | 0.1507 | 0.062
Load_TR6_F5_18 | customer | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.2941 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.086 | 0.2021 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 1.0159 | 0.746 | 0.1788 | 0.1436 | 0.0942 | 0.1671 | 0.2453 | 0.28 | 0.4356 | 0.046 | 0.046 | 0.8458 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046
Load_TR6_F5_18_dup | prosumer | 0.1288 | 0.053 | 0.1204 | 0.0614 | 0.0951 | 0.0867 | 0.053 | 0.1288 | 0.053 | 0.053 | 0.1288 | 0.053 | 0.1288 | 0.053 | 0.053 | 0.1288 | 0.053 | 0.1907 | 0.1832 | 0.1314 | 0.061 | 0.3172 | 0.0658 | 0.1548 | 0.8675 | 0.1209 | 0.302 | 0.4523 | 3.429 | 0.9708 | 2.2582 | 0.3005 | 0.2095 | 0.1879 | 0.2237 | 0.2416 | 0.1331 | 0.3905 | 0.16 | 0.4427 | 0.5969 | 1.8317 | 0.5245 | 0.3211 | 0.462 | 0.6858 | 0.6828 | 0.3379
Load_TR6_F5_19 | customer | 0.049 | 0.0702 | 0.1836 | 0.049 | 0.1765 | 0.0773 | 0.0915 | 0.1623 | 0.049 | 0.1906 | 0.0632 | 0.1269 | 0.1269 | 0.049 | 0.2048 | 0.049 | 0.049 | 0.0702 | 0.3895 | 0.9502 | 0.0905 | 0.3638 | 0.5259 | 0.3746 | 1.4734 | 0.3041 | 0.1307 | 0.2198 | 0.0734 | 0.222 | 0.5341 | 0.2198 | 1.0425 | 0.1402 | 0.1233 | 0.1774 | 1.6912 | 0.1602 | 0.3059 | 0.5453 | 0.3927 | 0.6126 | 0.424 | 0.6492 | 0.5537 | 0.5627 | 0.6544 | 0.5395
Load_TR6_F5_19_dup | customer | 0.051 | 0.1678 | 0.1083 | 0.051 | 0.1837 | 0.0924 | 0.051 | 0.0796 | 0.1906 | 0.1014 | 0.0637 | 0.1019 | 0.0574 | 0.0765 | 0.1996 | 0.0858 | 1.0118 | 0.1005 | 0.4102 | 0.2595 | 0.1848 | 0.3693 | 0.2498 | 0.2554 | 0.1544 | 0.0696 | 0.2511 | 0.2124 | 0.4901 | 0.3685 | 0.2373 | 0.1678 | 0.0924 | 0.2264 | 1.4147 | 0.8254 | 1.5978 | 0.3525 | 0.124 | 0.316 | 0.3162 | 0.1083 | 0.1099 | 0.1661 | 0.051 | 0.1083 | 0.1094 | 0.1666
Load_TR6_F5_1_dup | customer | 0.2562 | 0.0946 | 0.051 | 0.2998 | 0.051 | 0.1019 | 0.2489 | 0.0957 | 0.2302 | 0.1206 | 0.1492 | 0.157 | 0.3337 | 0.1627 | 0.051 | 0.1403 | 0.1606 | 0.1009 | 0.0809 | 0.7083 | 0.923 | 0.5828 | 1.402 | 0.2109 | 0.2184 | 0.0822 | 0.051 | 0.1882 | 0.1571 | 0.0566 | 0.051 | 0.1741 | 0.1767 | 0.0845 | 0.2638 | 0.3175 | 0.4132 | 0.2051 | 0.2845 | 0.051 | 0.2886 | 0.0622 | 0.1754 | 0.2769 | 0.0822 | 0.2686 | 0.051 | 0.2309
Load_TR6_F5_2 | prosumer | 0.048 | 0.048 | 0.048 | 0.1304 | 0.048 | 0.048 | 0.0617 | 0.1167 | 0.0663 | 0.1121 | 0.048 | 0.048 | 0.048 | 0.0617 | 0.1167 | 0.048 | 0.048 | 0.0892 | 0.0892 | 0.048 | 0.048 | 0.08 | 0.0984 | 2.7837 | 1.6286 | 2.2629 | 0.8309 | 0.2277 | 0.201 | 0.048 | 0.048 | 0.1194 | 0.08 | 0.06 | 1.2096 | 0.633 | 1.6685 | 1.5145 | 1.3225 | 0.9576 | 0.1361 | 0.1075 | 0.0709 | 0.048 | 0.0873 | 0.0526 | 0.1258 | 0.048
Load_TR6_F5_20 | prosumer | 2.4385 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.0971 | 0.1954 | 0.1038 | 0.055 | 0.055 | 0.3915 | 0.214 | 0.3906 | 0.7517 | 0.4945 | 2.1865 | 2.649 | 0.723 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.3056 | 0.364 | 0.2595 | 0.055 | 0.055
Load_TR6_F5_20_dup | prosumer | 0.0951 | 0.1044 | 0.058 | 0.1323 | 0.0673 | 0.0998 | 0.0998 | 0.058 | 0.1416 | 0.058 | 0.058 | 0.058 | 0.1416 | 0.058 | 0.058 | 0.1974 | 0.26 | 0.1416 | 0.058 | 0.058 | 0.2079 | 0.1916 | 0.058 | 0.058 | 0.058 | 0.2989 | 0.2154 | 0.3109 | 0.2546 | 0.1339 | 0.1229 | 0.2014 | 0.0879 | 1.8224 | 0.4318 | 0.058 | 0.1416 | 0.058 | 0.0859 | 0.1145 | 0.1893 | 1.7806 | 1.4758 | 1.019 | 0.5096 | 0.3194 | 0.1416 | 0.058
Load_TR6_F5_21 | customer | 0.055 | 0.055 | 0.055 | 0.1307 | 0.055 | 0.055 | 0.1222 | 0.0634 | 0.055 | 0.1138 | 0.0718 | 0.055 | 0.1012 | 0.0844 | 0.1222 | 0.0634 | 0.055 | 0.4823 | 0.055 | 0.055 | 0.0718 | 0.1138 | 0.055 | 0.0844 | 0.1012 | 0.055 | 0.1307 | 0.1088 | 0.0881 | 0.3059 | 0.1676 | 0.6045 | 0.4782 | 0.3045 | 0.1918 | 0.225 | 0.217 | 0.1849 | 0.1428 | 0.2637 | 0.4868 | 0.3705 | 0.251 | 0.2337 | 0.7334 | 0.4665 | 0.2199 | 0.1332
Load_TR6_F5_21_dup | prosumer | 0.046 | 0.167 | 0.2109 | 0.046 | 0.046 | 0.225 | 0.153 | 0.046 | 0.2277 | 0.1503 | 0.046 | 0.2354 | 0.153 | 0.0948 | 0.1991 | 0.13 | 0.1541 | 0.2302 | 0.1707 | 0.046 | 0.6024 | 0.0907 | 0.1036 | 0.3007 | 0.046 | 0.0867 | 0.2913 | 0.1295 | 0.4629 | 0.2241 | 0.1226 | 0.3687 | 0.0818 | 0.1957 | 0.2607 | 0.1802 | 0.4885 | 0.1421 | 0.046 | 0.3319 | 0.046 | 0.046 | 0.153 | 0.0785 | 0.1924 | 0.153 | 0.046 | 0.1315
Load_TR6_F5_22 | prosumer | 0.04 | 0.1087 | 0.1648 | 0.0629 | 0.117 | 0.1412 | 0.1198 | 0.1461 | 0.1084 | 0.1651 | 0.04 | 0.2335 | 0.04 | 0.2804 | 0.2538 | 0.1444 | 0.1925 | 0.2438 | 0.9031 | 0.4368 | 1.701 | 2.046 | 0.8597 | 0.22 | 1.6621 | 0.2289 | 0.2701 | 0.3648 | 0.2923 | 0.3134 | 0.3005 | 0.3302 | 1.4295 | 0.2358 | 0.6111 | 0.3569 | 0.3541 | 1.4979 | 0.1011 | 0.1648 | 0.1087 | 0.04 | 0.1024 | 0.1024 | 0.04 | 0.0744 | 0.0931 | 0.1728
Load_TR6_F5_22_dup | prosumer | 0.5223 | 0.0966 | 0.1305 | 0.057 | 0.057 | 0.0683 | 0.1588 | 0.057 | 0.1701 | 0.057 | 0.1305 | 0.0966 | 0.057 | 0.057 | 0.0796 | 0.1475 | 0.3055 | 1.1964 | 0.6177 | 0.3622 | 0.3146 | 0.9811 | 0.9254 | 0.5585 | 0.9342 | 1.5169 | 0.2146 | 0.4951 | 0.2596 | 0.1362 | 0.0909 | 0.057 | 0.1701 | 0.057 | 0.057 | 0.057 | 0.3893 | 0.0627 | 0.1007 | 0.5277 | 0.8284 | 0.7352 | 0.5455 | 0.5535 | 0.969 | 0.6903 | 1.1789 | 0.704
Load_TR6_F5_23 | prosumer | 0.1331 | 0.05 | 0.0863 | 0.1175 | 0.05 | 0.1538 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0656 | 0.1383 | 0.05 | 0.05 | 0.0959 | 0.1678 | 0.054 | 0.351 | 1.2517 | 0.2931 | 0.2516 | 0.3053 | 0.2595 | 1.0785 | 0.3139 | 0.2308 | 0.4022 | 0.3127 | 0.0716 | 0.1742 | 0.1147 | 0.1846 | 0.1332 | 0.281 | 0.1586 | 0.082 | 0.1279 | 0.0649 | 0.2023 | 0.1953 | 0.1666 | 0.05 | 0.05 | 0.05 | 0.1486 | 0.0552 | 0.0656 | 0.1383
Load_TR6_F5_23_dup | prosumer | 0.1966 | 0.055 | 0.3883 | 0.0699 | 0.1073 | 0.2337 | 0.0998 | 0.1667 | 0.1855 | 0.0662 | 0.1222 | 0.2188 | 0.1222 | 0.1592 | 0.1706 | 0.0662 | 0.2449 | 0.0961 | 0.0848 | 0.2562 | 0.055 | 0.1369 | 0.1705 | 0.1184 | 0.2375 | 0.0737 | 0.0624 | 0.23 | 0.1036 | 0.055 | 0.2673 | 0.055 | 0.1183 | 0.2227 | 0.055 | 0.2972 | 0.2683 | 0.5726 | 0.4401 | 0.3699 | 0.6699 | 1.3253 | 3.0703 | 2.9746 | 0.3962 | 0.6128 | 0.4064 | 0.4471
Load_TR6_F5_24 | prosumer | 0.6549 | 0.6932 | 0.4794 | 0.0913 | 0.1602 | 0.05 | 0.208 | 0.1731 | 0.1946 | 0.1087 | 0.1277 | 0.05 | 0.3311 | 0.05 | 0.276 | 0.2023 | 0.3137 | 0.36 | 0.3193 | 0.0889 | 0.4905 | 0.3539 | 0.2993 | 0.4061 | 0.2898 | 0.2978 | 0.1584 | 0.2761 | 0.152 | 1.2395 | 2.8772 | 2.6168 | 0.5086 | 0.0839 | 0.3391 | 0.3943 | 1.565 | 3.5466 | 4.5369 | 1.5188 | 0.6124 | 0.6124 | 0.5621 | 0.7989 | 0.4681 | 0.7646 | 0.4991 | 0.0579
Load_TR6_F5_24_dup | prosumer | 0.2451 | 0.3883 | 0.2691 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.07 | 0.9204 | 1.5653 | 0.0632 | 0.248 | 0.4712 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 2.2341 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.0657 | 0.1466 | 0.103 | 0.1083 | 0.2444 | 0.2409 | 0.2989 | 0.2986 | 0.5995 | 0.3201 | 0.6654 | 0.054 | 0.054
Load_TR6_F5_25 | prosumer | 0.116 | 0.041 | 0.116 | 0.041 | 0.116 | 0.041 | 0.041 | 0.091 | 0.066 | 0.041 | 0.116 | 0.041 | 0.116 | 0.041 | 0.0785 | 0.0785 | 0.041 | 0.0952 | 0.0618 | 0.0785 | 0.0785 | 0.0493 | 0.1077 | 0.041 | 0.116 | 0.041 | 0.041 | 0.116 | 0.041 | 0.116 | 0.041 | 0.041 | 0.041 | 0.116 | 0.041 | 0.041 | 0.2949 | 0.2699 | 0.084 | 0.5874 | 0.3596 | 0.488 | 0.5402 | 0.5938 | 0.5592 | 0.3521 | 0.041 | 0.041
Load_TR6_F5_25_dup | customer | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.1754 | 0.9091 | 0.128 | 0.1516 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.1249 | 0.1877 | 0.1877 | 0.1896 | 0.2169 | 0.2169 | 0.1984 | 0.305 | 0.2968 | 0.3704 | 0.5255 | 0.4402 | 0.4572 | 1.7427 | 1.5248 | 1.1027
Load_TR6_F5_26 | customer | 0.1649 | 0.057 | 0.057 | 0.057 | 0.1739 | 0.1287 | 0.1829 | 0.1197 | 0.1649 | 0.1377 | 0.057 | 0.197 | 0.1056 | 0.1056 | 0.1164 | 0.0794 | 0.1153 | 0.1326 | 0.1656 | 0.0615 | 0.1458 | 0.1568 | 0.057 | 0.2053 | 0.0973 | 0.1434 | 0.1592 | 0.057 | 0.296 | 0.2903 | 0.2261 | 0.2494 | 0.3714 | 0.2375 | 0.3928 | 0.2414 | 0.1571 | 0.1643 | 0.1049 | 0.2445 | 0.3398 | 0.3748 | 0.2764 | 0.4521 | 0.4801 | 0.4501 | 0.2557 | 0.0929
Load_TR6_F5_26_dup | customer | 0.059 | 0.1728 | 0.1659 | 0.1728 | 0.059 | 0.2684 | 0.0704 | 0.0818 | 0.1501 | 0.059 | 0.1659 | 0.059 | 0.1659 | 0.1728 | 0.059 | 0.3551 | 0.2754 | 0.2009 | 0.5482 | 0.4078 | 1.3054 | 0.3288 | 0.5177 | 0.3119 | 0.2798 | 0.1125 | 0.1125 | 0.1728 | 0.1971 | 0.059 | 0.1349 | 0.2038 | 0.0932 | 0.2456 | 0.059 | 0.1793 | 0.1659 | 0.0761 | 0.1707 | 0.248 | 0.5725 | 0.6361 | 0.4945 | 0.6053 | 0.855 | 0.605 | 0.1506 | 0.1653
Load_TR6_F5_27 | customer | 0.147 | 0.1978 | 0.0955 | 0.0955 | 0.044 | 0.175 | 0.1698 | 0.0514 | 0.2655 | 0.072 | 0.0734 | 0.2714 | 0.044 | 0.3011 | 0.2293 | 1.1455 | 0.2575 | 0.1386 | 0.3082 | 0.0661 | 0.1768 | 0.168 | 0.072 | 0.1698 | 0.1977 | 0.2767 | 0.2345 | 0.3105 | 0.098 | 0.147 | 0.1978 | 0.125 | 0.2129 | 0.051 | 0.044 | 0.264 | 0.1458 | 0.1349 | 0.2228 | 0.4252 | 0.5776 | 0.6167 | 0.2431 | 0.6529 | 0.4526 | 0.4093 | 0.3121 | 0.1176
Load_TR6_F5_27_dup | customer | 0.1675 | 0.1166 | 0.1612 | 0.1606 | 0.1354 | 0.1675 | 0.1606 | 0.1241 | 0.204 | 0.06 | 0.06 | 0.2681 | 0.06 | 0.1424 | 0.1857 | 0.1332 | 0.1949 | 0.1332 | 0.1823 | 0.0765 | 0.0675 | 0.4693 | 0.0817 | 0.2328 | 0.1156 | 0.1698 | 0.186 | 0.1449 | 0.1844 | 0.3886 | 0.3396 | 0.2294 | 0.1925 | 0.1864 | 0.354 | 0.4428 | 0.4942 | 0.2 | 0.476 | 0.4319 | 0.4336 | 0.2989 | 0.3073 | 0.3172 | 0.2973 | 0.4081 | 0.1409 | 0.1424
Load_TR6_F5_28 | customer | 0.0698 | 0.3721 | 0.161 | 0.05 | 0.2084 | 0.05 | 0.2084 | 0.05 | 0.1652 | 0.0932 | 0.122 | 0.1364 | 0.05 | 0.0716 | 0.1901 | 0.1194 | 0.3798 | 1.5499 | 2.0568 | 1.1561 | 0.1976 | 0.2065 | 0.4008 | 0.4445 | 1.0176 | 0.3877 | 0.0613 | 0.4306 | 1.2279 | 0.4963 | 0.831 | 0.1277 | 0.1724 | 0.086 | 0.2679 | 0.2942 | 0.504 | 0.265 | 1.6119 | 0.9776 | 1.1909 | 0.2126 | 0.3154 | 0.423 | 0.2701 | 0.2495 | 0.1791 | 0.102
Load_TR6_F5_28_dup | customer | 0.0734 | 0.2983 | 0.1502 | 0.1656 | 0.2557 | 0.1004 | 0.3186 | 0.1452 | 0.1656 | 0.058 | 0.2195 | 0.1907 | 0.1115 | 0.1584 | 0.1964 | 0.9831 | 0.5016 | 0.334 | 1.2747 | 1.2457 | 0.4786 | 0.4621 | 0.0625 | 0.2107 | 0.1977 | 0.1089 | 0.4407 | 0.2204 | 0.2103 | 0.5849 | 0.0941 | 0.9327 | 0.4058 | 0.058 | 0.2677 | 0.1961 | 0.3731 | 0.26 | 0.3051 | 0.6243 | 0.9207 | 1.5458 | 1.0172 | 0.9556 | 1.3587 | 0.5728 | 0.8204 | 0.2857
Load_TR6_F5_29 | customer | 0.2692 | 0.2254 | 0.1806 | 0.1315 | 0.1835 | 0.2571 | 0.2234 | 0.1539 | 0.1251 | 0.2234 | 0.2102 | 0.1029 | 0.2154 | 0.1726 | 0.3079 | 0.1867 | 0.5289 | 1.4367 | 0.1027 | 0.275 | 0.3742 | 0.3813 | 0.9852 | 0.9036 | 0.3431 | 0.1795 | 0.6086 | 0.2328 | 0.8895 | 0.378 | 0.2561 | 0.4742 | 0.269 | 0.4906 | 1.6395 | 1.5404 | 0.4215 | 0.1103 | 0.3561 | 0.0621 | 0.2168 | 0.4161 | 0.2187 | 0.4064 | 0.0527 | 0.3079 | 0.1726 | 0.048
Load_TR6_F5_29_dup | customer | 0.1116 | 0.0822 | 0.048 | 0.1191 | 0.048 | 0.1191 | 0.1458 | 0.052 | 0.213 | 0.048 | 0.1458 | 0.048 | 0.048 | 0.2169 | 0.048 | 0.052 | 0.2825 | 0.2528 | 0.3712 | 1.4082 | 0.4229 | 0.7342 | 0.6534 | 0.4122 | 0.3706 | 0.5535 | 0.6936 | 0.3038 | 0.6514 | 0.3452 | 0.333 | 0.6286 | 0.7092 | 0.1786 | 0.5611 | 0.3853 | 0.194 | 0.3459 | 0.1925 | 0.5348 | 0.678 | 1.0413 | 1.1526 | 1.1736 | 1.0433 | 1.2753 | 1.2401 | 0.547
Load_TR6_F5_2_dup | prosumer | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1745 | 0.0843 | 0.0917 | 0.0791 | 0.1006 | 0.0864 | 0.1473 | 0.1786 | 0.0782 | 1.1199 | 0.2884 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1455 | 0.4832 | 0.5063 | 0.6141 | 0.1239 | 0.7021 | 0.4141 | 0.3408
Load_TR6_F5_3 | prosumer | 0.059 | 0.2931 | 0.059 | 0.2076 | 0.1445 | 0.059 | 0.1853 | 0.059 | 0.1726 | 0.1794 | 0.0779 | 0.1663 | 0.1437 | 0.4158 | 1.3566 | 0.3968 | 0.3164 | 0.2508 | 0.2047 | 0.059 | 0.2315 | 0.1206 | 0.1853 | 0.059 | 0.2757 | 0.4446 | 0.4024 | 0.2619 | 0.4132 | 0.5062 | 0.059 | 1.4441 | 0.1845 | 0.1955 | 0.2731 | 0.2912 | 0.2272 | 0.0997 | 0.16 | 0.1129 | 0.1129 | 0.1789 | 0.1731 | 0.1537 | 0.1753 | 0.0821 | 0.059 | 0.059
Load_TR6_F5_30 | prosumer | 0.526 | 0.4467 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.1007 | 0.052 | 0.052 | 0.052 | 0.052 | 0.1517 | 0.188 | 0.188 | 0.188 | 0.224 | 0.1638 | 0.0531 | 0.3255 | 0.9566 | 2.7955 | 3.0301 | 0.5762 | 0.2264 | 0.2181 | 0.4991 | 0.4115 | 0.2102 | 0.4005 | 0.1449 | 0.052 | 0.052 | 0.1615 | 0.4544 | 0.4366 | 0.9993 | 2.8233 | 4.3317 | 0.493 | 0.3743 | 0.2793
Load_TR6_F5_30_dup | prosumer | 0.053 | 0.1313 | 0.053 | 0.053 | 0.1313 | 0.053 | 0.1052 | 0.0791 | 0.053 | 0.0747 | 0.1095 | 0.053 | 0.1095 | 0.0747 | 0.053 | 0.1368 | 0.053 | 0.1446 | 0.087 | 0.134 | 0.3873 | 0.053 | 0.1008 | 0.0834 | 0.0965 | 0.0878 | 0.0965 | 0.0878 | 0.053 | 0.1313 | 0.053 | 0.1313 | 0.1116 | 0.213 | 0.2595 | 0.2491 | 0.2867 | 0.4966 | 0.2979 | 0.6647 | 0.5621 | 0.391 | 0.5151 | 0.5018 | 0.4486 | 0.2303 | 0.053 | 0.1313
Load_TR6_F5_31 | prosumer | 0.3651 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.2718 | 0.917 | 0.0632 | 0.0632 | 0.0438 | 0.0806 | 0.1668 | 0.1651 | 0.3721 | 0.1802 | 0.1625 | 0.156 | 0.2207 | 0.2668 | 0.4471 | 0.2006 | 0.3168 | 0.2551 | 0.0503 | 0.039 | 0.0457 | 0.1263 | 0.1071 | 0.1342 | 0.4198 | 0.618 | 0.588 | 0.7402 | 0.7013 | 0.498 | 0.4347 | 0.5577 | 0.2835 | 0.2792
Load_TR6_F5_31_dup | customer | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 1.4289 | 0.8769 | 0.2242 | 0.9648 | 0.043 | 0.043 | 1.0505 | 1.1066 | 0.8887 | 0.1043 | 0.1445 | 0.0476 | 0.1007 | 0.8849 | 0.079 | 0.5085 | 2.3571 | 0.1099 | 0.1458 | 0.1279 | 0.0918 | 0.055 | 0.0681 | 0.0673 | 0.4541 | 0.0946 | 0.345 | 0.7276 | 0.5411 | 0.7456 | 0.3214 | 0.3183 | 0.4386 | 0.5325 | 0.3739
Load_TR6_F5_32 | customer | 0.1419 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.6957 | 3.0721 | 2.5158 | 0.046 | 0.2272 | 0.2817 | 0.8045 | 0.7067 | 1.743 | 0.1505 | 0.1255 | 0.3696 | 0.2577 | 0.614 | 0.046 | 0.046 | 1.1148 | 1.2253 | 0.3624 | 0.3823 | 0.2686 | 0.2632 | 0.398 | 0.5812 | 0.4828 | 0.5795 | 0.7285 | 0.9078 | 0.5562 | 0.4085 | 0.201 | 0.046
Load_TR6_F5_32_dup | prosumer | 0.042 | 0.1268 | 0.1394 | 0.3507 | 0.4632 | 0.5421 | 0.2103 | 0.1398 | 0.0746 | 0.1138 | 0.1007 | 0.042 | 0.1333 | 0.0811 | 0.042 | 0.1268 | 0.0877 | 0.042 | 0.1725 | 0.042 | 0.042 | 0.0746 | 0.1543 | 0.0854 | 0.3145 | 0.2644 | 0.1893 | 0.3531 | 0.1492 | 0.3051 | 0.1744 | 0.072 | 0.2062 | 0.2566 | 0.2481 | 0.2943 | 0.042 | 0.0642 | 0.2297 | 0.6666 | 0.76 | 0.6093 | 0.6708 | 0.1545 | 0.4433 | 0.454 | 0.3599 | 0.3368
Load_TR6_F5_33 | customer | 0.1965 | 0.037 | 0.037 | 0.2049 | 0.0538 | 0.0454 | 0.2133 | 0.037 | 0.2217 | 0.037 | 0.1747 | 0.1126 | 0.037 | 0.2217 | 0.037 | 0.1126 | 0.1461 | 0.0622 | 0.1965 | 0.037 | 0.2217 | 0.037 | 0.037 | 0.1126 | 0.1461 | 0.1136 | 0.1055 | 0.1045 | 0.1629 | 0.037 | 0.1965 | 0.0622 | 0.0414 | 0.0471 | 0.239 | 0.0532 | 0.037 | 0.2298 | 0.0528 | 0.2498 | 0.1719 | 1.212 | 0.6396 | 0.4117 | 0.4693 | 0.1698 | 0.1965 | 0.037
Load_TR6_F5_33_dup | customer | 0.1157 | 0.248 | 0.04 | 0.1828 | 0.1808 | 0.04 | 0.1913 | 0.0551 | 0.1459 | 0.206 | 0.082 | 0.1762 | 0.1572 | 0.04 | 0.2181 | 0.1455 | 0.1157 | 0.2362 | 0.082 | 0.1762 | 0.1959 | 0.4203 | 0.6333 | 2.1077 | 0.2834 | 0.4991 | 1.8999 | 0.9846 | 0.0414 | 0.1364 | 0.2904 | 0.5936 | 0.1746 | 0.0693 | 0.2357 | 0.1279 | 0.0576 | 0.306 | 0.059 | 0.3328 | 0.558 | 2.3091 | 0.4268 | 0.2453 | 0.2401 | 0.2423 | 0.2588 | 0.2854
Load_TR6_F5_34 | prosumer | 0.1336 | 0.172 | 0.1121 | 0.0812 | 0.2163 | 0.0761 | 0.0721 | 0.2615 | 0.0961 | 0.056 | 0.1637 | 0.1458 | 0.0723 | 0.2573 | 0.0681 | 0.1001 | 0.184 | 0.0895 | 0.1121 | 0.2214 | 0.04 | 0.1826 | 0.151 | 0.04 | 0.2735 | 0.06 | 0.048 | 0.234 | 0.1361 | 0.1077 | 0.3348 | 0.1748 | 0.2873 | 0.139 | 0.0921 | 0.192 | 0.0895 | 0.0812 | 0.2283 | 0.064 | 0.2214 | 0.0921 | 0.2002 | 0.0812 | 0.1041 | 0.081 | 0.2606 | 0.04
Load_TR6_F5_34_dup | customer | 0.2179 | 0.0812 | 0.1277 | 0.1744 | 0.0679 | 0.1178 | 0.1564 | 0.0978 | 0.0956 | 0.1486 | 0.1377 | 0.0635 | 0.2156 | 0.063 | 0.049 | 0.159 | 0.1377 | 0.0604 | 0.3532 | 0.3178 | 1.0402 | 0.4127 | 0.3865 | 0.1254 | 0.1377 | 0.0635 | 0.2306 | 0.048 | 0.1852 | 0.1089 | 0.0829 | 0.1028 | 0.1254 | 0.2311 | 0.2432 | 0.3421 | 0.2759 | 0.3208 | 0.2201 | 0.4176 | 0.0879 | 0.2241 | 0.3504 | 0.4665 | 0.5227 | 0.5067 | 0.1553 | 0.1616
Load_TR6_F5_35 | customer | 0.3133 | 0.0813 | 0.2601 | 0.0551 | 0.1804 | 0.1569 | 0.1315 | 0.2098 | 0.1239 | 0.2023 | 0.1066 | 0.0834 | 0.1727 | 0.1796 | 0.1239 | 0.2174 | 0.1239 | 0.1569 | 0.2324 | 0.2273 | 1.6134 | 0.1723 | 0.3042 | 0.391 | 0.1982 | 0.2474 | 0.1017 | 0.201 | 0.3309 | 0.2633 | 0.3821 | 0.3011 | 0.1481 | 0.1134 | 0.4426 | 0.2289 | 0.2937 | 0.178 | 0.173 | 0.5644 | 0.3678 | 0.5943 | 0.6868 | 0.6629 | 0.1342 | 0.2575 | 0.274 | 0.0915
Load_TR6_F5_35_dup | customer | 0.03 | 0.1614 | 0.03 | 0.1614 | 0.03 | 0.1154 | 0.076 | 0.0826 | 0.1089 | 0.9876 | 0.2438 | 0.03 | 0.03 | 0.1286 | 0.0629 | 0.0694 | 0.122 | 0.03 | 0.1689 | 0.035 | 0.1027 | 0.1154 | 0.0629 | 0.1294 | 0.0308 | 0.3506 | 0.1815 | 0.03 | 0.1614 | 0.03 | 0.03 | 0.1614 | 0.03 | 0.1352 | 0.0563 | 0.0826 | 0.1089 | 0.03 | 0.0629 | 0.1286 | 0.0431 | 0.3232 | 0.3048 | 0.4303 | 0.4162 | 0.03 | 0.03 | 0.03
Load_TR6_F5_36 | customer | 0.1604 | 0.2423 | 0.1471 | 0.187 | 0.159 | 0.14 | 0.2131 | 0.225 | 0.0821 | 0.2569 | 0.1471 | 0.2282 | 0.1462 | 0.1263 | 0.2764 | 0.048 | 1.3635 | 3.5399 | 1.9137 | 1.6307 | 2.9215 | 2.3098 | 0.485 | 1.2514 | 0.2973 | 0.3079 | 0.0529 | 0.3852 | 0.048 | 0.269 | 0.169 | 0.0622 | 0.2741 | 0.1498 | 0.2459 | 0.4507 | 0.2666 | 0.4922 | 0.048 | 0.2994 | 0.2725 | 0.4762 | 0.8475 | 1.0006 | 1.0267 | 1.9568 | 0.5738 | 0.9264
Load_TR6_F5_36_dup | customer | 0.2932 | 0.0884 | 0.1978 | 0.0582 | 0.0913 | 0.3387 | 0.041 | 0.2212 | 0.1881 | 0.0617 | 0.128 | 0.302 | 0.041 | 0.3313 | 0.1792 | 0.1438 | 0.2088 | 0.1184 | 0.2357 | 0.117 | 0.3234 | 0.2181 | 0.1137 | 1.2677 | 1.3285 | 0.2468 | 1.5779 | 0.3558 | 0.4135 | 0.6021 | 0.9073 | 0.28 | 1.816 | 0.2338 | 1.1629 | 2.0586 | 0.562 | 0.4417 | 0.2052 | 0.4387 | 0.5516 | 0.4037 | 0.7551 | 0.6624 | 0.542 | 0.4118 | 0.0582 | 0.1913
Load_TR6_F5_37 | customer | 0.1241 | 0.14 | 0.1798 | 0.14 | 0.1798 | 0.112 | 0.084 | 0.1365 | 0.0993 | 0.2019 | 0.1179 | 0.14 | 0.056 | 0.2639 | 0.056 | 0.2142 | 0.1056 | 0.166 | 0.1538 | 0.1241 | 0.4294 | 1.8841 | 0.2568 | 1.1737 | 1.2377 | 0.2197 | 0.4275 | 0.1106 | 0.2639 | 0.056 | 0.2032 | 0.1167 | 0.1117 | 0.512 | 0.3887 | 0.3576 | 0.2834 | 0.2197 | 0.3326 | 0.6015 | 0.5656 | 0.5587 | 0.6804 | 0.4121 | 0.5129 | 0.4378 | 0.1756 | 0.07
Load_TR6_F5_37_dup | customer | 0.0954 | 0.0954 | 0.058 | 0.1328 | 0.058 | 0.1328 | 0.058 | 0.058 | 0.1203 | 0.0705 | 0.058 | 0.058 | 0.058 | 0.1328 | 0.058 | 0.1042 | 0.6585 | 1.1697 | 0.3353 | 0.2964 | 0.5069 | 0.3686 | 0.3392 | 0.6903 | 0.5001 | 0.6184 | 0.3052 | 1.5742 | 1.5163 | 1.8786 | 0.2659 | 0.2177 | 0.1077 | 0.2764 | 2.8897 | 0.1229 | 1.2695 | 0.2959 | 0.1783 | 0.4813 | 0.6189 | 0.5553 | 0.5305 | 0.5532 | 0.5008 | 0.8176 | 0.8934 | 1.4333
Load_TR6_F5_38 | prosumer | 0.056 | 0.2009 | 0.1521 | 0.101 | 0.111 | 0.056 | 0.156 | 0.197 | 0.091 | 0.1723 | 0.1457 | 0.156 | 0.1265 | 0.1265 | 0.071 | 0.282 | 0.056 | 0.2436 | 0.1095 | 0.1345 | 0.5046 | 0.056 | 0.056 | 0.056 | 0.2174 | 0.3315 | 0.3165 | 0.4919 | 0.2629 | 0.3095 | 0.442 | 0.4293 | 0.0816 | 0.156 | 0.056 | 0.2078 | 0.1452 | 0.086 | 0.1645 | 0.1585 | 0.156 | 0.0752 | 0.1778 | 0.056 | 0.5248 | 0.407 | 0.8477 | 0.3234
Load_TR6_F5_38_dup | customer | 0.0645 | 0.057 | 0.1318 | 0.0869 | 0.057 | 0.1617 | 0.057 | 0.057 | 0.057 | 0.1617 | 0.057 | 0.0645 | 0.1542 | 0.057 | 0.3239 | 0.308 | 0.057 | 0.2489 | 0.2802 | 0.4523 | 0.3208 | 0.4013 | 0.5672 | 0.3064 | 0.573 | 0.4211 | 0.228 | 0.1103 | 0.1019 | 0.1168 | 0.057 | 0.1617 | 0.057 | 0.1243 | 0.0944 | 0.057 | 0.057 | 0.2683 | 0.2205 | 0.2603 | 0.2411 | 0.1165 | 0.4836 | 0.4022 | 0.4627 | 0.7165 | 0.6169 | 0.5997
Load_TR6_F5_39 | prosumer | 0.5529 | 0.135 | 0.18 | 0.1812 | 0.057 | 0.2657 | 0.1084 | 0.122 | 0.1492 | 0.1339 | 0.057 | 0.1723 | 0.1498 | 0.096 | 0.2261 | 0.135 | 0.1108 | 0.1847 | 0.0647 | 0.7141 | 0.5025 | 0.4722 | 0.1188 | 0.0724 | 1.7641 | 0.9154 | 0.206 | 0.1552 | 0.1108 | 0.1723 | 0.1766 | 1.3491 | 0.3818 | 0.2374 | 0.152 | 0.7484 | 1.0239 | 0.962 | 0.383 | 0.5567 | 0.5009 | 0.5767 | 1.2947 | 1.2529 | 0.7982 | 0.2665 | 0.2031 | 0.1581
Load_TR6_F5_39_dup | customer | 0.2628 | 0.0545 | 0.2449 | 0.0653 | 0.1687 | 0.157 | 0.1818 | 0.0784 | 0.1177 | 0.1687 | 0.1439 | 0.0522 | 0.2014 | 0.1373 | 1.0754 | 0.3988 | 0.0791 | 0.0875 | 0.1308 | 0.0285 | 0.2259 | 2.0443 | 0.5129 | 0.6517 | 0.2164 | 0.4438 | 0.2123 | 0.2622 | 0.148 | 0.2538 | 1.2904 | 0.8121 | 0.0973 | 0.1813 | 0.1574 | 0.0718 | 0.2669 | 0.026 | 0.1647 | 0.1741 | 0.0849 | 0.4054 | 0.4818 | 0.4924 | 1.225 | 0.2884 | 0.4675 | 0.3096
Load_TR6_F5_3_dup | prosumer | 0.3915 | 0.047 | 0.047 | 0.047 | 0.1275 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.0783 | 0.0962 | 0.0873 | 0.0873 | 0.047 | 0.047 | 0.1007 | 0.0738 | 0.047 | 0.047 | 0.047 | 0.1275 | 0.047 | 0.1141 | 0.0604 | 0.5079 | 0.1059 | 0.1472 | 0.0627 | 0.1275 | 0.0525 | 0.1179 | 0.2262 | 0.1507 | 0.2066 | 0.1501 | 0.2176 | 0.1383 | 0.123 | 0.0515 | 0.1096 | 0.226 | 0.2922 | 0.5291 | 0.3477 | 0.3217 | 0.6137 | 0.442
Load_TR6_F5_4 | customer | 0.1792 | 0.0787 | 0.0572 | 0.2008 | 0.05 | 0.1362 | 0.1218 | 0.0787 | 0.1792 | 0.05 | 0.05 | 0.208 | 0.05 | 0.1649 | 0.2553 | 0.2019 | 0.5247 | 0.05 | 0.2661 | 0.245 | 0.2019 | 0.3168 | 0.2298 | 0.1235 | 0.3168 | 0.4174 | 0.208 | 0.05 | 0.1649 | 0.0931 | 0.05 | 0.05 | 0.3122 | 0.2019 | 0.2521 | 0.3096 | 0.2537 | 0.4001 | 0.2653 | 0.5032 | 0.2595 | 0.3376 | 0.7699 | 0.4169 | 0.3994 | 0.6697 | 0.05 | 0.05
Load_TR6_F5_40 | customer | 0.0886 | 0.0803 | 0.0803 | 0.101 | 0.0596 | 0.043 | 0.043 | 0.1176 | 0.043 | 0.043 | 0.1176 | 0.043 | 0.0927 | 0.0679 | 0.043 | 0.043 | 0.2416 | 0.2042 | 0.2269 | 0.3214 | 0.0637 | 0.0969 | 0.043 | 0.043 | 0.043 | 0.1176 | 0.0657 | 0.043 | 0.1176 | 0.043 | 0.0844 | 0.0761 | 0.043 | 0.043 | 0.0471 | 0.2973 | 0.2545 | 0.1606 | 0.2493 | 0.2469 | 0.4119 | 0.4043 | 0.4213 | 0.503 | 0.6577 | 0.5122 | 0.345 | 0.2887
Load_TR6_F5_40_dup | prosumer | 0.119 | 0.1351 | 0.039 | 0.1911 | 0.063 | 0.039 | 0.1271 | 0.1271 | 0.039 | 0.2151 | 0.039 | 0.063 | 0.1911 | 0.039 | 0.1671 | 0.087 | 0.039 | 0.039 | 0.1448 | 1.0933 | 0.1137 | 0.3879 | 0.4548 | 0.2218 | 0.5245 | 0.354 | 0.0455 | 0.0403 | 0.3384 | 0.1439 | 0.1271 | 0.1271 | 0.0435 | 0.0541 | 2.238 | 3.9898 | 0.7948 | 0.1431 | 0.039 | 0.2151 | 0.039 | 0.039 | 0.087 | 0.1671 | 0.039 | 0.039 | 0.079 | 0.1751
Load_TR6_F5_41 | prosumer | 0.047 | 0.2342 | 0.0559 | 0.1272 | 0.1629 | 0.047 | 0.2431 | 0.047 | 0.047 | 0.2431 | 0.1201 | 0.1094 | 0.1807 | 0.047 | 0.047 | 0.1985 | 0.0916 | 0.047 | 0.1896 | 0.1005 | 0.0846 | 0.047 | 0.1461 | 0.153 | 0.107 | 0.2346 | 0.2792 | 0.1272 | 0.3574 | 0.0697 | 1.5125 | 0.5336 | 0.3142 | 0.2941 | 0.3789 | 0.1309 | 0.5082 | 0.1433 | 0.3139 | 0.2629 | 0.999 | 0.7833 | 0.6331 | 0.7996 | 0.5206 | 0.853 | 0.5634 | 0.047
Load_TR6_F5_41_dup | prosumer | 0.4006 | 0.0911 | 0.2539 | 0.036 | 0.2466 | 0.0643 | 0.1479 | 0.163 | 0.064 | 0.2092 | 0.0738 | 0.036 | 0.1899 | 0.121 | 0.0619 | 0.3067 | 0.0767 | 0.1282 | 0.2043 | 0.2191 | 0.064 | 0.2499 | 0.036 | 0.0399 | 0.1626 | 0.1385 | 0.4859 | 0.3705 | 0.2568 | 0.3345 | 0.1912 | 0.2059 | 0.4445 | 0.2387 | 0.4964 | 0.3708 | 0.1561 | 0.3386 | 0.1303 | 0.3627 | 0.4343 | 0.7727 | 0.5724 | 0.4984 | 0.5095 | 0.2083 | 0.1444 | 0.2749
Load_TR6_F5_42 | prosumer | 0.1264 | 0.1264 | 0.044 | 0.0515 | 0.2013 | 0.044 | 0.089 | 0.1639 | 0.044 | 0.2088 | 0.044 | 0.0815 | 0.1714 | 0.044 | 0.2088 | 0.0921 | 0.9597 | 0.2062 | 0.2162 | 0.7856 | 0.2111 | 0.284 | 0.2887 | 0.2167 | 0.4752 | 0.3406 | 0.2644 | 0.2008 | 2.0375 | 2.4804 | 2.2993 | 0.4566 | 0.089 | 0.044 | 0.4718 | 0.2328 | 0.2604 | 0.3468 | 0.0962 | 0.4681 | 0.534 | 0.9451 | 0.6534 | 0.5449 | 0.7026 | 0.6137 | 0.2394 | 0.2088
Load_TR6_F5_42_dup | prosumer | 0.1694 | 0.073 | 0.2433 | 0.1461 | 0.0616 | 0.3277 | 0.053 | 0.2346 | 0.0616 | 0.0929 | 0.2705 | 0.0789 | 0.1461 | 0.2433 | 0.0929 | 0.2619 | 0.0876 | 0.0862 | 0.1129 | 0.053 | 0.3479 | 0.4525 | 0.085 | 0.1777 | 0.2564 | 0.1172 | 0.2516 | 0.2594 | 0.0635 | 0.3164 | 0.073 | 0.1135 | 0.2758 | 0.053 | 0.2346 | 0.1547 | 0.1308 | 0.1654 | 0.253 | 0.3673 | 0.2108 | 0.2902 | 0.2852 | 0.2442 | 0.3849 | 0.2337 | 0.5034 | 0.5649
Load_TR6_F5_43 | prosumer | 0.1233 | 0.2319 | 0.0561 | 0.1126 | 0.048 | 0.2588 | 0.1045 | 0.0694 | 0.2092 | 0.06 | 0.0939 | 0.2694 | 0.048 | 0.1741 | 0.1549 | 0.1236 | 0.3967 | 1.4683 | 1.0002 | 1.1177 | 0.1742 | 0.0534 | 0.06 | 0.498 | 0.048 | 0.1747 | 0.2193 | 0.0736 | 0.2403 | 0.123 | 0.1566 | 0.4004 | 0.1103 | 0.1678 | 0.073 | 0.3092 | 0.3678 | 0.3425 | 0.1403 | 0.3618 | 1.703 | 1.8987 | 0.888 | 0.2403 | 0.0642 | 0.5544 | 0.2299 | 0.2953
Load_TR6_F5_43_dup | prosumer | 0.0898 | 0.1984 | 0.04 | 0.113 | 0.1619 | 0.04 | 0.0887 | 0.1862 | 0.0765 | 0.0765 | 0.1619 | 0.113 | 0.1231 | 0.1518 | 0.2721 | 0.1784 | 0.0602 | 0.0954 | 0.1843 | 0.04 | 0.1619 | 0.4901 | 1.5345 | 0.1023 | 0.0765 | 0.2665 | 0.0927 | 0.1495 | 1.385 | 1.1643 | 1.206 | 0.228 | 0.0519 | 0.1747 | 1.028 | 0.8618 | 0.1532 | 0.5169 | 0.04 | 0.113 | 0.1397 | 0.0622 | 0.04 | 0.2349 | 0.04 | 0.1231 | 0.1396 | 0.0522
Load_TR6_F5_44 | customer | 0.0778 | 0.1228 | 0.051 | 0.2312 | 0.0887 | 0.051 | 0.1896 | 0.1302 | 0.0852 | 0.2347 | 0.051 | 0.1126 | 0.2073 | 0.1177 | 0.0767 | 0.1765 | 0.1433 | 0.1703 | 0.0573 | 0.2563 | 0.0636 | 0.0972 | 0.1537 | 0.1201 | 0.051 | 0.2746 | 0.1233 | 0.2512 | 0.1834 | 0.153 | 0.1117 | 0.175 | 0.051 | 0.2586 | 0.0613 | 0.1138 | 0.1696 | 0.193 | 0.4075 | 0.3068 | 0.281 | 0.0715 | 0.1703 | 0.3054 | 0.2044 | 0.1433 | 0.1765 | 0.051
Load_TR6_F5_44_dup | customer | 0.058 | 0.058 | 0.058 | 0.124 | 0.058 | 0.058 | 0.124 | 0.058 | 0.058 | 0.124 | 0.058 | 0.1093 | 0.0727 | 0.058 | 0.058 | 0.1057 | 0.0763 | 0.2889 | 0.2068 | 0.1429 | 0.2544 | 0.2464 | 0.2464 | 0.2464 | 0.2504 | 0.2922 | 0.4587 | 0.474 | 1.2443 | 0.0653 | 0.1988 | 0.058 | 0.124 | 0.058 | 0.058 | 0.124 | 0.058 | 0.058 | 0.058 | 0.058 | 0.124 | 0.058 | 0.058 | 0.0983 | 0.0837 | 0.058 | 0.058 | 0.124
Load_TR6_F5_45 | customer | 0.1531 | 0.1684 | 0.0848 | 0.2953 | 0.0646 | 0.1771 | 0.2117 | 0.08 | 0.1185 | 0.056 | 0.3328 | 0.056 | 0.2944 | 0.0945 | 0.056 | 0.1425 | 0.056 | 0.3328 | 0.0843 | 0.3932 | 0.5963 | 0.4003 | 0.8593 | 2.7715 | 2.6415 | 0.6541 | 0.0646 | 0.056 | 0.2203 | 0.2418 | 0.1396 | 0.2492 | 0.1726 | 0.8238 | 0.9153 | 1.1316 | 0.8455 | 0.2986 | 0.2433 | 0.4562 | 0.4094 | 0.7414 | 0.6522 | 0.6812 | 0.0752 | 0.5267 | 0.3558 | 0.0993
Load_TR6_F5_45_dup | customer | 0.187 | 0.1662 | 0.0881 | 0.2727 | 0.05 | 0.05 | 0.1527 | 0.1356 | 0.0976 | 0.2593 | 0.05 | 0.2984 | 0.0586 | 1.0681 | 1.4265 | 0.214 | 0.5406 | 0.8316 | 0.9966 | 0.6087 | 0.3843 | 0.1442 | 0.547 | 0.1613 | 0.1074 | 0.7758 | 1.09 | 0.6731 | 1.257 | 0.8486 | 1.0352 | 0.6751 | 0.2582 | 0.3401 | 1.3483 | 0.5826 | 0.987 | 0.56 | 1.0996 | 0.0795 | 0.2508 | 0.0805 | 0.2203 | 1.0015 | 0.05 | 0.2383 | 0.1186 | 0.0757
Load_TR6_F5_46 | prosumer | 0.1843 | 0.0682 | 0.2438 | 0.055 | 0.1711 | 0.141 | 0.1116 | 0.1542 | 0.1013 | 0.1145 | 0.1975 | 0.055 | 0.2438 | 0.0682 | 0.0814 | 0.174 | 0.0959 | 0.0707 | 0.1872 | 0.1248 | 0.1309 | 0.1812 | 0.2506 | 0.2246 | 0.0676 | 0.2005 | 0.1116 | 0.055 | 0.2339 | 0.1463 | 0.055 | 0.1909 | 0.1211 | 0.073 | 0.3785 | 0.1552 | 0.1956 | 0.3678 | 0.3704 | 0.7163 | 0.613 | 0.3896 | 0.4531 | 0.0833 | 0.1459 | 0.2476 | 0.055 | 0.1182
Load_TR6_F5_46_dup | customer | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.0868 | 0.193 | 0.4297 | 0.3687 | 0.1625 | 0.1246 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.1625 | 0.102 | 0.0983 | 0.2442 | 0.2032 | 0.3193 | 0.3671 | 0.4407 | 0.4692 | 0.4998 | 0.4705 | 0.3909 | 0.6031 | 0.049 | 0.049
Load_TR6_F5_47 | prosumer | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.2316 | 0.0633 | 0.0702 | 0.1614 | 0.053 | 0.053 | 0.0652 | 0.1365 | 0.2334 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.7607 | 0.7597 | 0.0992 | 0.4641 | 0.4855 | 0.2749 | 0.4052 | 0.3632 | 2.1216 | 0.8012 | 0.4918 | 0.1782 | 0.053 | 0.053
Load_TR6_F5_47_dup | customer | 0.3591 | 0.9482 | 0.044 | 0.1133 | 0.0527 | 0.044 | 0.0656 | 0.1003 | 0.044 | 0.0656 | 0.1003 | 0.0786 | 0.0873 | 0.083 | 0.083 | 0.044 | 0.1219 | 0.0997 | 0.3071 | 0.9246 | 0.0632 | 0.1508 | 0.1386 | 0.3964 | 1.0214 | 0.0486 | 0.0496 | 0.1915 | 0.1774 | 0.2525 | 0.2871 | 0.4574 | 1.935 | 0.2351 | 0.2299 | 1.3185 | 1.1608 | 0.4796 | 0.2843 | 0.5727 | 0.5323 | 0.5807 | 0.6233 | 0.3609 | 0.044 | 0.1219 | 0.044 | 0.044
Load_TR6_F5_48 | customer | 0.719 | 0.0936 | 0.0603 | 0.2786 | 0.053 | 0.1838 | 0.0821 | 0.126 | 0.1547 | 0.1111 | 0.126 | 0.2128 | 0.053 | 0.1613 | 0.1775 | 0.053 | 0.2858 | 0.053 | 0.2722 | 1.2856 | 3.5097 | 2.2409 | 0.5172 | 2.7508 | 2.9894 | 2.0162 | 0.2556 | 0.4033 | 0.1098 | 0.1935 | 0.2871 | 0.053 | 0.1057 | 0.2331 | 0.126 | 0.1256 | 0.1402 | 0.126 | 0.053 | 0.2858 | 0.053 | 0.1474 | 0.1184 | 0.126 | 0.2128 | 0.053 | 0.0895 | 0.2493
Load_TR6_F5_48_dup | prosumer | 0.1378 | 0.2048 | 0.0947 | 0.1595 | 0.1876 | 0.0813 | 0.2121 | 0.0902 | 0.0902 | 0.2479 | 0.0947 | 0.1961 | 0.1465 | 0.0942 | 0.2484 | 0.2445 | 0.2772 | 0.1463 | 0.2755 | 0.3422 | 0.4176 | 0.515 | 1.1808 | 0.5949 | 0.6971 | 0.2829 | 0.1452 | 0.2153 | 0.1126 | 0.2121 | 0.05 | 0.1821 | 0.174 | 0.167 | 0.3619 | 0.1725 | 0.1342 | 0.1458 | 0.1283 | 0.2686 | 0.3135 | 0.4806 | 0.6913 | 0.3774 | 0.5138 | 0.4818 | 0.5363 | 0.2223
Load_TR6_F5_49 | customer | 0.2188 | 0.1888 | 0.1012 | 0.174 | 0.16 | 0.1578 | 0.112 | 0.1338 | 0.1467 | 0.1547 | 0.1793 | 0.053 | 0.2314 | 0.1026 | 0.1012 | 0.1226 | 0.053 | 0.053 | 0.2148 | 0.3728 | 0.0861 | 0.1409 | 0.1671 | 0.7855 | 2.1227 | 0.856 | 0.1642 | 0.6884 | 0.4998 | 0.3126 | 2.2571 | 0.187 | 0.1361 | 0.1956 | 0.2352 | 0.1714 | 0.5405 | 0.299 | 0.1047 | 0.3494 | 0.8437 | 1.4294 | 0.4527 | 0.718 | 0.4858 | 0.6928 | 0.9891 | 0.2623
Load_TR6_F5_49_dup | customer | 0.219 | 0.055 | 0.055 | 0.219 | 0.055 | 0.2115 | 0.0625 | 0.1857 | 0.1519 | 0.055 | 0.055 | 0.1966 | 0.0774 | 0.1519 | 0.1221 | 0.1789 | 0.137 | 0.2196 | 0.1863 | 0.346 | 0.1921 | 0.1402 | 0.2758 | 0.1221 | 0.1789 | 0.9337 | 0.7622 | 0.0923 | 0.1817 | 0.055 | 0.0992 | 0.5318 | 0.4149 | 2.0476 | 2.9623 | 0.4472 | 1.6713 | 0.2061 | 1.5611 | 1.309 | 0.4895 | 0.8395 | 0.8439 | 0.8357 | 0.5523 | 0.4551 | 0.4537 | 0.6877
Load_TR6_F5_4_dup | prosumer | 0.2269 | 0.0699 | 0.1484 | 0.1484 | 0.062 | 0.117 | 0.1798 | 0.062 | 0.219 | 0.0777 | 0.1719 | 0.1248 | 0.062 | 0.2347 | 0.0639 | 0.2155 | 0.344 | 0.336 | 1.1251 | 0.3158 | 0.29 | 0.117 | 0.2185 | 0.5223 | 2.0403 | 0.5525 | 0.3934 | 0.7104 | 0.1013 | 0.3749 | 0.2419 | 0.2645 | 0.3922 | 0.2245 | 0.2491 | 0.2941 | 0.1496 | 0.0856 | 0.2112 | 0.062 | 0.1562 | 0.1405 | 0.062 | 0.2347 | 0.062 | 0.1641 | 0.1327 | 0.062
Load_TR6_F5_5 | customer | 0.11 | 0.1457 | 0.11 | 0.033 | 0.1815 | 0.0743 | 0.033 | 0.1457 | 0.033 | 0.1457 | 0.033 | 0.0929 | 0.1629 | 0.11 | 0.033 | 0.1573 | 0.0984 | 0.033 | 0.0509 | 0.5894 | 0.1192 | 0.0962 | 0.1912 | 0.1252 | 0.033 | 0.2228 | 0.033 | 0.1928 | 0.0815 | 0.312 | 0.3061 | 0.2888 | 0.2141 | 0.2715 | 0.2669 | 0.2891 | 0.2308 | 0.2263 | 0.2908 | 0.4163 | 0.5261 | 0.529 | 0.2993 | 0.2118 | 0.2228 | 0.033 | 0.033 | 0.1457
Load_TR6_F5_50 | prosumer | 1.7918 | 0.3697 | 0.1176 | 0.11 | 0.1706 | 0.057 | 0.2236 | 0.057 | 0.057 | 0.1024 | 0.1782 | 0.057 | 0.2236 | 0.057 | 0.057 | 0.1479 | 0.1327 | 0.057 | 0.2236 | 0.057 | 0.057 | 0.163 | 0.1176 | 0.057 | 0.057 | 0.2236 | 0.057 | 0.057 | 0.2236 | 0.057 | 0.1327 | 0.3376 | 0.2392 | 0.5259 | 0.3155 | 0.3468 | 0.5131 | 0.414 | 0.265 | 0.4545 | 0.7936 | 0.3432 | 0.3415 | 0.6068 | 0.3692 | 0.057 | 0.2236 | 0.057
Load_TR6_F5_50_dup | customer | 1.9461 | 0.534 | 0.0773 | 0.1474 | 0.1469 | 0.1415 | 0.1528 | 0.054 | 0.1469 | 0.1474 | 0.0617 | 0.2349 | 0.0651 | 0.1055 | 0.1564 | 0.387 | 0.2078 | 0.3349 | 0.2564 | 0.0878 | 0.1096 | 0.1306 | 0.1074 | 0.2727 | 0.164 | 0.2201 | 0.054 | 0.1707 | 0.104 | 0.2111 | 0.1286 | 0.1752 | 0.2884 | 0.2396 | 0.4113 | 0.2575 | 0.3184 | 0.175 | 0.9709 | 0.8176 | 0.6069 | 0.4869 | 0.5375 | 0.4955 | 0.6912 | 0.5086 | 0.1299 | 0.0948
Load_TR6_F5_51 | prosumer | 0.1684 | 0.0842 | 0.1569 | 0.0842 | 0.0496 | 0.1627 | 0.0784 | 0.064 | 0.1253 | 0.041 | 0.2001 | 0.041 | 0.0842 | 0.1569 | 0.0899 | 0.0581 | 0.2001 | 0.041 | 0.1235 | 0.9394 | 0.1202 | 0.2139 | 0.1023 | 0.0928 | 0.2438 | 0.041 | 0.0928 | 0.107 | 0.1906 | 1.1989 | 0.1593 | 0.2097 | 0.1832 | 0.1092 | 0.1483 | 0.0727 | 0.0918 | 0.1176 | 0.0554 | 0.0999 | 0.9906 | 0.8566 | 0.299 | 0.182 | 0.3879 | 0.3345 | 0.041 | 0.1512
Load_TR6_F5_51_dup | prosumer | 0.0616 | 0.3393 | 0.1044 | 0.1395 | 0.1598 | 0.206 | 0.1395 | 0.2275 | 0.1383 | 0.1366 | 0.3146 | 0.2966 | 0.2784 | 0.2014 | 0.1941 | 0.4658 | 0.1028 | 0.057 | 0.3872 | 0.1409 | 0.0773 | 0.3343 | 0.0937 | 0.0638 | 0.258 | 0.1561 | 0.0845 | 0.1919 | 0.2564 | 0.057 | 0.3778 | 0.0705 | 0.1395 | 0.206 | 0.1533 | 0.5712 | 0.3863 | 0.1304 | 0.2952 | 0.0797 | 0.1507 | 0.2885 | 0.1395 | 0.0864 | 0.2794 | 0.0983 | 0.201 | 0.1721
Load_TR6_F5_52 | customer | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2019 | 0.1946 | 0.1366 | 0.05 | 0.1838 | 1.3797 | 0.2213 | 2.5824 | 1.0973 | 1.7195 | 0.1692 | 0.0628 | 0.2958 | 0.2018 | 0.1493 | 0.1884 | 0.6112 | 1.5205 | 2.6068 | 0.3137 | 1.7604 | 4.0329 | 2.8137 | 0.6546 | 0.2729 | 0.2942 | 1.8944 | 2.5318 | 1.1477 | 0.337 | 0.5458 | 0.3406 | 0.3129
Load_TR6_F5_52_dup | prosumer | 0.363 | 0.037 | 0.037 | 0.2073 | 0.037 | 0.1299 | 0.1144 | 0.037 | 0.2073 | 0.037 | 0.0447 | 0.1995 | 0.037 | 0.2073 | 0.037 | 0.2492 | 0.2545 | 0.3983 | 0.2073 | 0.0398 | 0.2949 | 0.0944 | 0.1803 | 0.2803 | 0.112 | 0.2888 | 0.1306 | 0.292 | 0.2728 | 0.3161 | 0.1174 | 0.2762 | 0.2059 | 0.037 | 0.2325 | 0.2018 | 0.1148 | 0.1763 | 0.037 | 0.1144 | 0.1299 | 0.037 | 0.0445 | 0.1467 | 0.5123 | 0.3108 | 0.8834 | 0.7567
Load_TR6_F5_53 | customer | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.0755 | 0.048 | 0.048 | 0.048 | 0.0522 | 0.2875 | 0.058 | 0.0501 | 0.0649 | 0.5917 | 0.8031 | 0.0988 | 0.0779 | 0.1083 | 0.1485 | 0.1359 | 0.0832 | 0.1466 | 0.2333 | 0.1159 | 0.6739 | 0.3826 | 0.102 | 0.0812 | 0.1445 | 0.1493 | 0.113 | 0.0605 | 0.1499 | 0.1789 | 0.2456 | 0.2739 | 1.324 | 0.6998 | 0.4863 | 0.4052 | 0.5519 | 0.5492 | 0.4068 | 0.2061
Load_TR6_F5_53_dup | customer | 0.049 | 0.0997 | 0.0744 | 0.0955 | 0.0786 | 0.049 | 0.104 | 0.0701 | 0.1124 | 0.0617 | 0.1082 | 0.0659 | 0.049 | 0.1251 | 0.2793 | 0.2718 | 0.2824 | 0.2498 | 0.3271 | 0.1543 | 0.1632 | 0.1251 | 0.049 | 0.1251 | 0.049 | 0.1251 | 0.1088 | 0.2965 | 0.211 | 0.2478 | 0.172 | 0.0638 | 0.0963 | 0.2109 | 0.0934 | 0.3333 | 1.0791 | 0.1382 | 0.205 | 0.1292 | 0.3058 | 0.4248 | 0.3682 | 0.4856 | 0.1251 | 0.049 | 0.049 | 0.1251
Load_TR6_F5_54 | customer | 0.1592 | 0.057 | 0.1446 | 0.0716 | 0.0716 | 0.1446 | 0.057 | 0.1592 | 0.057 | 0.0862 | 0.13 | 0.057 | 0.1592 | 0.057 | 0.2728 | 0.2027 | 0.0764 | 0.057 | 0.1592 | 0.057 | 0.1592 | 0.057 | 0.057 | 0.1592 | 0.0896 | 2.524 | 2.5641 | 0.2103 | 0.8201 | 2.686 | 2.2205 | 0.1596 | 0.1565 | 0.2469 | 0.3985 | 1.3399 | 0.1766 | 0.1065 | 1.127 | 2.8346 | 2.0007 | 0.3595 | 0.4098 | 0.3344 | 0.057 | 0.1592 | 0.057 | 0.1227
Load_TR6_F5_54_dup | customer | 0.0675 | 0.2919 | 0.053 | 0.053 | 0.2458 | 0.1136 | 0.053 | 0.3063 | 0.053 | 0.1397 | 0.053 | 0.1852 | 0.1742 | 0.1156 | 0.2437 | 0.1397 | 0.159 | 0.1578 | 1.1347 | 0.458 | 0.2438 | 0.2543 | 0.0964 | 0.0964 | 0.1941 | 0.1652 | 0.1551 | 0.3748 | 0.5858 | 0.3413 | 0.2943 | 0.2267 | 0.258 | 0.2656 | 0.1514 | 0.1742 | 0.117 | 0.1893 | 0.053 | 0.1397 | 0.053 | 0.2196 | 0.053 | 0.053 | 0.1666 | 0.2584 | 0.1454 | 0.2643
Load_TR6_F5_55 | prosumer | 0.1015 | 0.1604 | 0.05 | 0.1236 | 0.1383 | 0.05 | 0.2119 | 0.05 | 0.153 | 0.1162 | 0.05 | 0.2119 | 0.05 | 0.05 | 0.0868 | 0.1751 | 0.2829 | 0.0944 | 0.05 | 0.2119 | 0.05 | 0.1131 | 0.3002 | 0.2788 | 0.1988 | 0.9677 | 0.2367 | 0.0807 | 0.05 | 0.1835 | 0.6644 | 0.9621 | 0.4112 | 0.5032 | 1.1996 | 0.6627 | 0.3797 | 0.2356 | 0.3001 | 0.7988 | 1.7475 | 0.5562 | 0.5453 | 0.4073 | 0.7049 | 0.4486 | 0.364 | 0.2045
Load_TR6_F5_55_dup | customer | 0.055 | 0.1914 | 0.1049 | 0.0838 | 0.1127 | 0.1644 | 0.1319 | 0.1548 | 0.1415 | 0.055 | 0.055 | 0.1548 | 0.055 | 0.1864 | 0.1099 | 1.4883 | 0.2453 | 0.1037 | 0.2926 | 0.1624 | 0.079 | 0.203 | 0.1221 | 0.0886 | 0.2125 | 0.0838 | 0.055 | 0.2365 | 0.0598 | 0.1771 | 0.4343 | 0.4027 | 0.4964 | 0.6243 | 0.7345 | 0.4422 | 0.4739 | 0.5416 | 0.4468 | 0.1415 | 0.1548 | 0.1415 | 0.1192 | 0.0906 | 0.1175 | 0.079 | 0.5105 | 0.4226
Load_TR6_F5_56 | customer | 0.2137 | 0.055 | 0.055 | 0.2137 | 0.055 | 0.0983 | 0.1704 | 0.055 | 0.2137 | 0.055 | 0.055 | 0.1921 | 0.0766 | 0.055 | 0.1849 | 0.0839 | 0.055 | 0.2137 | 0.055 | 0.1921 | 0.0766 | 0.055 | 0.1849 | 0.242 | 0.1948 | 0.272 | 0.284 | 0.1887 | 0.3312 | 0.0728 | 0.1989 | 0.2859 | 0.1166 | 0.2003 | 0.055 | 0.2165 | 1.8546 | 0.4684 | 2.2502 | 0.3829 | 0.6911 | 0.4591 | 1.3834 | 0.7137 | 0.91 | 0.818 | 0.3054 | 0.1921
Load_TR6_F5_56_dup | customer | 0.1596 | 0.058 | 0.058 | 0.3068 | 0.0812 | 0.134 | 0.254 | 0.058 | 0.2138 | 0.1741 | 0.058 | 0.2254 | 0.1625 | 0.1199 | 0.1664 | 0.2558 | 0.3967 | 0.4446 | 0.3787 | 0.37 | 0.3512 | 0.2714 | 0.4475 | 0.2022 | 0.2706 | 0.2293 | 0.1587 | 0.0943 | 0.3423 | 0.2277 | 0.544 | 0.3641 | 0.3131 | 0.5343 | 0.3813 | 0.5955 | 0.058 | 0.058 | 0.2283 | 0.1524 | 0.0653 | 0.1814 | 0.2066 | 0.058 | 0.1819 | 0.1045 | 0.1596 | 0.2283
Load_TR6_F5_57 | prosumer | 0.4256 | 0.059 | 0.2195 | 0.3158 | 0.059 | 0.059 | 0.2336 | 0.3016 | 0.059 | 0.2866 | 0.2486 | 0.059 | 0.4762 | 0.059 | 0.2993 | 0.2359 | 0.1726 | 0.8566 | 0.561 | 0.2021 | 0.4593 | 0.3356 | 0.1183 | 0.5712 | 0.3807 | 0.2092 | 1.1143 | 0.6441 | 0.2966 | 2.4825 | 2.733 | 1.1558 | 1.4092 | 1.1842 | 1.9046 | 0.5764 | 0.644 | 0.5299 | 0.5408 | 0.6459 | 0.6177 | 0.7055 | 0.7212 | 0.6713 | 0.7422 | 0.669 | 0.3482 | 0.2364
Load_TR6_F5_57_dup | customer | 0.1464 | 0.1814 | 0.1324 | 0.1804 | 0.215 | 0.051 | 0.3513 | 0.051 | 0.2991 | 0.1032 | 0.051 | 0.2683 | 0.134 | 0.1737 | 0.2693 | 0.1729 | 0.2444 | 0.2686 | 0.7101 | 0.7012 | 0.4257 | 0.2242 | 0.1405 | 0.1256 | 0.0883 | 0.314 | 0.051 | 0.0578 | 0.1804 | 0.051 | 1.2044 | 0.1972 | 0.3062 | 0.227 | 0.1421 | 1.4478 | 0.1988 | 0.2699 | 0.28 | 0.1136 | 0.3723 | 0.3352 | 0.346 | 0.2516 | 0.4304 | 0.3387 | 0.3996 | 0.4074
Load_TR6_F5_58 | prosumer | 0.2256 | 0.053 | 0.1229 | 0.1533 | 0.2138 | 0.0623 | 0.1861 | 0.1763 | 0.0937 | 0.2687 | 0.053 | 0.2256 | 0.1042 | 0.2268 | 0.0844 | 0.1314 | 0.1471 | 0.1229 | 0.2396 | 0.1368 | 0.207 | 0.1725 | 0.1368 | 0.2256 | 0.1368 | 0.0548 | 0.0577 | 0.2734 | 0.0844 | 0.2109 | 0.3884 | 0.2666 | 0.5399 | 0.5149 | 0.3838 | 0.5083 | 0.3842 | 0.4186 | 2.1153 | 2.5706 | 1.6833 | 0.0765 | 0.1829 | 0.1795 | 0.1001 | 0.1785 | 0.1368 | 0.1785
Load_TR6_F5_58_dup | prosumer | 0.1677 | 0.056 | 0.056 | 0.1677 | 0.056 | 0.1677 | 0.056 | 0.056 | 0.056 | 0.1677 | 0.056 | 0.056 | 0.1677 | 0.056 | 0.1278 | 0.0959 | 0.056 | 0.056 | 0.1677 | 0.056 | 0.1278 | 0.0959 | 0.056 | 0.1677 | 0.056 | 0.056 | 0.056 | 0.1677 | 0.056 | 0.1518 | 0.072 | 0.056 | 0.1677 | 0.056 | 0.056 | 0.1677 | 0.056 | 0.056 | 0.056 | 0.2031 | 0.201 | 0.2158 | 0.2897 | 0.2397 | 0.4504 | 0.3108 | 0.368 | 0.624
Load_TR6_F5_59 | prosumer | 0.7599 | 0.052 | 0.1568 | 0.1246 | 0.0681 | 0.2133 | 0.052 | 0.1568 | 0.1246 | 0.1004 | 0.181 | 0.052 | 0.2133 | 0.0681 | 0.554 | 0.454 | 0.2417 | 0.3635 | 0.1482 | 0.1327 | 0.3543 | 0.052 | 0.0831 | 0.3299 | 0.2479 | 0.2028 | 0.4459 | 0.2545 | 1.0239 | 0.4608 | 0.2786 | 0.285 | 0.3637 | 0.3157 | 0.1003 | 0.3005 | 0.1784 | 0.4586 | 0.4053 | 0.4241 | 0.5774 | 0.7511 | 0.6382 | 0.1165 | 0.1649 | 0.1161 | 0.2214 | 0.052
Load_TR6_F5_59_dup | customer | 0.1068 | 0.265 | 0.1256 | 0.4429 | 0.0893 | 0.366 | 0.2232 | 0.2348 | 0.3348 | 0.1897 | 0.1423 | 0.3065 | 0.1344 | 0.2507 | 0.2752 | 0.2215 | 0.3032 | 0.3596 | 0.2039 | 0.2956 | 0.1957 | 0.1612 | 0.2256 | 0.3191 | 0.1659 | 0.2518 | 0.4052 | 0.3933 | 0.5127 | 0.1799 | 0.1449 | 0.2677 | 0.3708 | 0.1769 | 0.4455 | 0.0954 | 0.4106 | 0.3872 | 0.3908 | 0.278 | 1.7122 | 0.3657 | 0.6276 | 0.8699 | 0.4802 | 0.4697 | 0.4523 | 0.6785
Load_TR6_F5_5_dup | prosumer | 0.2849 | 0.2368 | 0.1978 | 0.2302 | 0.1487 | 0.1549 | 0.1925 | 0.2357 | 0.2116 | 0.1294 | 0.1263 | 0.1579 | 0.179 | 0.3426 | 0.0618 | 0.1429 | 0.2493 | 0.082 | 0.5802 | 0.0928 | 0.1294 | 0.3851 | 0.0621 | 0.1782 | 0.3434 | 0.055 | 0.3985 | 0.1231 | 0.2301 | 0.5305 | 0.1643 | 1.2329 | 0.3789 | 0.3637 | 0.5412 | 0.4656 | 0.6471 | 0.2541 | 0.3603 | 0.7856 | 1.6686 | 0.617 | 0.8008 | 0.7364 | 0.7433 | 0.7931 | 0.9316 | 0.6674
Load_TR6_F5_6 | customer | 0.044 | 0.044 | 0.1053 | 0.1506 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.2681 | 0.2037 | 0.2537 | 0.357 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.2698 | 0.2698 | 0.1904 | 0.2077 | 0.1208 | 0.0878 | 0.386 | 0.0954 | 0.044 | 0.044 | 0.044 | 0.044 | 0.1259 | 0.2702 | 0.4128 | 0.2703 | 0.3539 | 0.3838 | 0.3857 | 0.3489 | 0.22 | 0.044
Load_TR6_F5_60 | prosumer | 0.048 | 0.1549 | 0.048 | 0.048 | 0.1549 | 0.048 | 0.048 | 0.1549 | 0.048 | 0.1549 | 0.048 | 0.048 | 0.1549 | 0.1086 | 0.229 | 0.2045 | 0.3574 | 0.2536 | 0.242 | 0.1343 | 0.1623 | 0.8564 | 0.1565 | 0.048 | 0.1549 | 0.0572 | 0.7935 | 0.5391 | 0.048 | 0.1549 | 0.048 | 0.048 | 0.327 | 0.048 | 0.0487 | 1.0719 | 0.283 | 0.0893 | 0.1549 | 0.048 | 0.1091 | 0.0938 | 0.048 | 0.0556 | 0.1473 | 0.048 | 0.048 | 0.0862
Load_TR6_F5_60_dup | customer | 0.1726 | 0.1003 | 0.057 | 0.2159 | 0.057 | 0.057 | 0.1653 | 0.1076 | 0.057 | 0.057 | 0.2087 | 0.0642 | 0.0787 | 1.2415 | 0.097 | 0.1993 | 1.3792 | 1.0353 | 1.3393 | 0.9763 | 2.497 | 0.3245 | 0.2334 | 1.6163 | 0.3725 | 1.4164 | 0.057 | 0.9998 | 0.8418 | 1.623 | 0.3558 | 0.2091 | 0.2035 | 0.2833 | 0.5547 | 1.5895 | 0.2121 | 0.5087 | 0.2669 | 0.7303 | 0.543 | 0.7202 | 2.1174 | 0.6897 | 0.3038 | 0.3734 | 0.3972 | 0.3092
Load_TR6_F5_61 | customer | 0.2667 | 0.053 | 0.0589 | 0.207 | 0.1069 | 0.1 | 0.2197 | 0.053 | 0.2667 | 0.053 | 0.094 | 0.2257 | 0.1116 | 1.9659 | 0.8412 | 1.3094 | 0.2877 | 0.1727 | 0.3508 | 0.4026 | 1.3043 | 0.193 | 0.1351 | 0.053 | 0.2331 | 0.1259 | 0.1205 | 0.3801 | 0.2548 | 0.2657 | 0.094 | 0.3154 | 0.1869 | 0.1706 | 0.2199 | 0.3245 | 0.3902 | 0.2385 | 0.9998 | 0.804 | 0.3483 | 0.278 | 0.2454 | 0.5865 | 0.4732 | 0.1273 | 0.1175 | 0.1424
Load_TR6_F5_61_dup | prosumer | 0.8069 | 0.4644 | 0.4347 | 0.3725 | 0.4447 | 0.0887 | 0.2177 | 0.1146 | 0.1786 | 0.1742 | 0.0739 | 0.2193 | 0.1411 | 0.7522 | 1.055 | 0.237 | 0.1874 | 0.055 | 0.1224 | 0.2436 | 0.1136 | 0.3147 | 1.2415 | 2.3482 | 0.3344 | 0.2378 | 0.3921 | 0.5304 | 0.6396 | 0.7573 | 0.1964 | 0.0822 | 0.232 | 1.2149 | 0.485 | 2.4083 | 1.3988 | 0.4145 | 0.7633 | 0.6336 | 0.5807 | 0.5176 | 0.4835 | 0.6368 | 0.7579 | 0.6555 | 0.5817 | 0.3233
Load_TR6_F5_62 | prosumer | 0.0734 | 0.1549 | 0.056 | 0.056 | 0.1374 | 0.0909 | 0.056 | 0.1607 | 0.0676 | 0.1642 | 0.1374 | 0.056 | 0.1723 | 0.056 | 0.1723 | 0.056 | 0.1549 | 0.0734 | 0.056 | 0.1723 | 0.056 | 0.056 | 0.1723 | 0.056 | 0.2327 | 0.2876 | 0.2331 | 0.5264 | 0.2321 | 0.5089 | 0.4379 | 0.5267 | 0.2319 | 0.0721 | 0.1142 | 0.1142 | 0.056 | 0.1723 | 0.1315 | 0.2103 | 0.6784 | 0.4258 | 0.5984 | 0.6139 | 0.1491 | 0.0793 | 0.0676 | 0.1607
Load_TR6_F5_62_dup | customer | 0.1154 | 0.05 | 0.3316 | 0.0745 | 0.209 | 0.1971 | 0.05 | 0.3561 | 0.05 | 0.2744 | 0.1317 | 0.05 | 0.1399 | 0.1715 | 0.1447 | 0.2551 | 0.1511 | 0.1733 | 0.5874 | 0.6525 | 0.3772 | 0.3213 | 0.2424 | 0.05 | 0.2499 | 0.1562 | 0.0891 | 0.6733 | 0.1535 | 0.2995 | 0.2165 | 0.355 | 0.258 | 0.2025 | 0.6346 | 0.6913 | 0.1674 | 0.3399 | 0.1808 | 0.1622 | 0.1132 | 0.05 | 0.2926 | 0.1135 | 0.1648 | 0.2413 | 0.05 | 0.1098
Load_TR6_F5_63 | customer | 0.4363 | 0.4532 | 0.0295 | 0.1874 | 0.0465 | 0.1453 | 0.0931 | 0.025 | 0.1469 | 0.0915 | 0.025 | 0.1109 | 0.0465 | 0.0465 | 0.1919 | 0.0304 | 0.1636 | 0.1335 | 0.0401 | 0.0565 | 0.1819 | 0.079 | 0.1594 | 0.025 | 0.1382 | 0.1002 | 0.052 | 0.079 | 0.025 | 0.165 | 0.0733 | 0.0519 | 0.1056 | 0.106 | 0.0895 | 0.2177 | 0.1102 | 0.2273 | 0.0884 | 0.2069 | 0.3915 | 0.4668 | 0.4359 | 0.446 | 0.7716 | 0.8114 | 0.4869 | 0.1324
Load_TR6_F5_63_dup | customer | 0.1684 | 0.2135 | 0.065 | 0.3097 | 0.0853 | 0.1009 | 0.3167 | 0.097 | 0.236 | 0.1474 | 0.1233 | 0.0853 | 0.3439 | 0.1009 | 0.058 | 0.3124 | 0.1324 | 0.7032 | 2.315 | 0.5179 | 0.2474 | 0.5992 | 0.3827 | 0.7663 | 2.1706 | 2.5795 | 2.2937 | 0.2468 | 0.3021 | 0.1566 | 0.1863 | 0.1404 | 0.1086 | 0.2048 | 0.2705 | 0.7733 | 0.1069 | 0.1629 | 0.2819 | 0.1554 | 0.2195 | 0.1279 | 0.1629 | 0.1768 | 0.1631 | 0.1838 | 0.2609 | 0.1479
Load_TR6_F5_64 | customer | 0.2762 | 0.1562 | 0.1224 | 0.1519 | 0.1961 | 0.142 | 0.4171 | 0.5411 | 0.1522 | 0.1415 | 0.2762 | 0.1656 | 0.128 | 0.2213 | 0.2112 | 0.0808 | 0.2673 | 0.0671 | 0.1858 | 0.2326 | 0.1374 | 0.1918 | 0.0992 | 0.2638 | 0.1459 | 0.114 | 0.0899 | 0.3426 | 0.0675 | 0.4327 | 0.1649 | 0.3367 | 0.188 | 0.2391 | 0.1656 | 0.1327 | 0.1293 | 0.2235 | 0.1374 | 0.295 | 0.053 | 0.0751 | 0.2776 | 0.1327 | 0.112 | 0.2454 | 0.3517 | 0.2673
Load_TR6_F5_64_dup | customer | 0.1474 | 0.046 | 0.1334 | 0.2709 | 0.0802 | 0.1237 | 0.3148 | 0.046 | 0.2215 | 0.217 | 0.1043 | 0.3342 | 0.0897 | 0.0994 | 0.2954 | 0.1043 | 0.0848 | 0.3099 | 0.1456 | 0.2234 | 0.2236 | 0.0973 | 0.2526 | 0.181 | 0.0744 | 0.3204 | 0.0946 | 0.2184 | 0.123 | 0.198 | 0.1892 | 0.1944 | 0.2526 | 0.1033 | 0.2696 | 0.1822 | 0.0998 | 0.548 | 0.1323 | 0.3742 | 0.7361 | 0.6087 | 0.731 | 1.0361 | 0.7173 | 0.5039 | 0.6304 | 0.311
Load_TR6_F5_65 | customer | 0.1256 | 0.051 | 0.0551 | 0.1215 | 0.051 | 0.051 | 0.0966 | 0.08 | 0.051 | 0.0759 | 0.1008 | 0.051 | 0.051 | 0.051 | 0.051 | 0.1256 | 0.2975 | 0.4056 | 0.2806 | 0.2372 | 0.0605 | 0.0634 | 0.1132 | 0.051 | 0.2041 | 0.2141 | 0.1276 | 0.051 | 0.0717 | 0.1049 | 0.051 | 0.051 | 0.1256 | 0.051 | 0.1091 | 0.0676 | 0.0966 | 0.08 | 0.051 | 0.051 | 0.0883 | 0.0883 | 0.051 | 0.1256 | 0.051 | 0.1256 | 0.051 | 0.051
Load_TR6_F5_65_dup | customer | 0.1823 | 0.048 | 0.1512 | 0.1567 | 0.1192 | 0.1887 | 0.048 | 0.1192 | 0.048 | 0.2441 | 0.0638 | 0.1113 | 0.1966 | 0.048 | 0.048 | 0.1247 | 0.1119 | 1.0913 | 0.3151 | 0.3174 | 0.3007 | 0.3775 | 0.207 | 0.3627 | 0.2224 | 0.2714 | 0.3776 | 0.2642 | 0.4403 | 0.5407 | 1.2901 | 0.4804 | 0.3614 | 0.2332 | 0.3552 | 0.3398 | 0.2082 | 0.0762 | 0.3634 | 0.4132 | 0.7189 | 0.7294 | 0.5619 | 0.7093 | 0.863 | 0.6242 | 0.224 | 0.0839
Load_TR6_F5_66 | customer | 0.2714 | 0.0836 | 0.1839 | 0.055 | 0.1409 | 0.1266 | 0.055 | 0.1337 | 0.1337 | 0.055 | 0.1767 | 0.0908 | 0.055 | 0.1624 | 0.1051 | 0.1009 | 1.178 | 0.2713 | 1.3651 | 2.9296 | 1.8908 | 1.6856 | 0.0847 | 0.2808 | 0.1467 | 0.306 | 0.2235 | 1.7286 | 2.4446 | 0.9494 | 1.8269 | 0.3568 | 0.3535 | 0.4475 | 0.614 | 1.198 | 1.0537 | 0.2382 | 0.2008 | 0.1695 | 0.055 | 0.2125 | 0.055 | 0.055 | 0.2456 | 0.412 | 0.2408 | 0.4474
Load_TR6_F5_66_dup | customer | 0.043 | 0.2115 | 0.043 | 0.1655 | 0.0889 | 0.0583 | 0.1961 | 0.043 | 0.2115 | 0.043 | 0.1349 | 0.1196 | 0.0507 | 0.2038 | 0.053 | 0.1526 | 0.1624 | 0.1651 | 0.2865 | 0.0515 | 0.043 | 0.0966 | 0.1579 | 0.043 | 0.2671 | 0.1225 | 1.1124 | 0.1043 | 0.043 | 0.043 | 0.1655 | 0.748 | 0.2751 | 0.3278 | 0.161 | 0.2341 | 0.1431 | 0.3818 | 0.5056 | 0.6541 | 1.0704 | 0.2013 | 0.3476 | 0.2203 | 0.4236 | 0.263 | 0.3166 | 0.043
Load_TR6_F5_67 | prosumer | 0.206 | 0.056 | 0.1958 | 0.206 | 0.056 | 0.3458 | 0.056 | 0.1981 | 0.2037 | 0.056 | 0.2628 | 0.139 | 0.1428 | 0.2471 | 0.2983 | 0.2656 | 0.1224 | 0.2479 | 1.499 | 0.6079 | 2.2168 | 0.4507 | 1.3429 | 0.1822 | 0.5988 | 0.3338 | 0.3518 | 0.5609 | 0.317 | 0.2607 | 0.2535 | 0.2695 | 0.2957 | 0.4184 | 0.2817 | 1.035 | 0.4022 | 1.0756 | 0.1554 | 0.4709 | 0.2233 | 0.4452 | 0.507 | 0.4055 | 0.5494 | 0.2707 | 0.1727 | 0.3458
Load_TR6_F5_67_dup | customer | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.0701 | 0.1634 | 0.1451 | 1.0588 | 0.2395 | 0.1965 | 0.1865 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.2109 | 0.2055 | 0.2082 | 0.1858 | 0.2418 | 0.2524 | 0.2201 | 0.1164 | 0.1463 | 0.333 | 0.4171 | 0.2517 | 0.1873 | 0.3023 | 0.3449 | 0.2994 | 0.3211 | 0.057 | 0.057
Load_TR6_F5_68 | prosumer | 0.1758 | 0.1277 | 0.2226 | 0.1277 | 0.051 | 0.2163 | 0.1341 | 0.051 | 0.2993 | 0.051 | 0.051 | 0.2695 | 0.0808 | 0.1446 | 0.1418 | 0.1617 | 0.1758 | 0.0893 | 0.3248 | 0.2004 | 0.0822 | 0.1914 | 0.051 | 0.2737 | 0.5205 | 0.051 | 0.2226 | 0.051 | 0.1901 | 0.1602 | 0.9086 | 0.2993 | 0.051 | 0.168 | 0.1525 | 0.0808 | 0.2865 | 0.426 | 0.7091 | 0.2033 | 0.1208 | 0.2567 | 0.0936 | 0.051 | 0.1702 | 0.1801 | 0.1852 | 0.6415
Load_TR6_F5_68_dup | customer | 0.054 | 0.1718 | 0.2131 | 0.054 | 0.1544 | 0.2306 | 0.1042 | 0.2487 | 0.0861 | 0.1544 | 0.2651 | 0.1329 | 0.1237 | 0.1892 | 0.054 | 0.1544 | 0.054 | 0.1744 | 0.2106 | 0.054 | 0.3597 | 0.2982 | 0.1988 | 0.4421 | 0.2538 | 0.3262 | 0.7406 | 0.2978 | 0.362 | 0.4484 | 0.4954 | 0.2856 | 0.3048 | 0.1503 | 0.1932 | 0.2975 | 0.3399 | 0.2899 | 0.7484 | 1.8906 | 0.1824 | 0.054 | 0.2254 | 0.1595 | 0.054 | 0.3023 | 0.0827 | 0.054
Load_TR6_F5_6_dup | prosumer | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.3374 | 0.3999 | 0.0501 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.0782 | 0.2179 | 0.5089 | 0.5147 | 0.0601 | 0.0644 | 0.0595 | 0.0733 | 0.1322 | 0.545 | 0.4611 | 0.5946 | 0.4912 | 0.5498 | 0.4401 | 0.6002 | 0.3867 | 0.5132 | 0.4941 | 0.6733 | 0.5128
Load_TR6_F5_7 | prosumer | 0.1615 | 0.1396 | 0.1932 | 0.1557 | 0.1249 | 0.1757 | 0.1049 | 0.1795 | 0.0671 | 0.2817 | 0.043 | 0.2444 | 0.1044 | 0.043 | 0.2122 | 0.1366 | 0.043 | 0.3059 | 0.2605 | 0.2383 | 0.1106 | 0.0635 | 0.3675 | 1.5558 | 0.2545 | 0.3059 | 0.1069 | 0.2222 | 0.304 | 0.0574 | 0.1476 | 0.051 | 0.1454 | 0.1471 | 0.0993 | 0.1236 | 0.2458 | 0.0572 | 0.6474 | 1.0319 | 0.3037 | 0.5238 | 1.4961 | 0.1975 | 0.1932 | 0.1557 | 0.0498 | 0.1944
Load_TR6_F5_7_dup | prosumer | 0.1589 | 0.2565 | 0.0867 | 0.2526 | 0.055 | 0.2145 | 0.2326 | 0.055 | 0.1685 | 0.1529 | 0.1749 | 0.2442 | 0.0956 | 0.1818 | 0.1807 | 0.1586 | 0.188 | 0.2427 | 0.2248 | 0.1891 | 0.2129 | 0.1927 | 0.2411 | 0.2595 | 0.3083 | 0.1378 | 0.4259 | 0.5473 | 0.4384 | 0.6389 | 0.4121 | 1.6748 | 2.6703 | 1.521 | 0.071 | 0.055 | 0.2406 | 0.2065 | 0.4073 | 0.4372 | 0.2902 | 0.2427 | 0.4791 | 0.7489 | 0.5158 | 0.8341 | 0.3558 | 0.136
Load_TR6_F5_8 | prosumer | 0.2053 | 0.052 | 0.1984 | 0.1212 | 0.133 | 0.1866 | 0.052 | 0.052 | 0.1605 | 0.1591 | 0.0968 | 0.2228 | 0.0764 | 0.1009 | 0.2162 | 0.0764 | 0.172 | 0.1231 | 0.0601 | 0.1171 | 0.052 | 0.1799 | 0.1397 | 0.1167 | 0.2281 | 0.0964 | 0.3313 | 0.1443 | 0.1541 | 0.9182 | 0.1795 | 0.6122 | 0.1258 | 0.0968 | 0.2065 | 0.1371 | 0.173 | 0.3214 | 0.1559 | 0.384 | 0.3604 | 0.3798 | 0.4732 | 0.2978 | 0.271 | 0.4514 | 0.1102 | 0.052
Load_TR6_F5_8_dup | prosumer | 0.1195 | 0.053 | 0.3061 | 0.053 | 0.053 | 0.3061 | 0.053 | 0.2098 | 0.1493 | 0.1372 | 0.2219 | 0.053 | 0.053 | 0.1611 | 0.1738 | 0.1252 | 0.1251 | 0.186 | 0.1371 | 0.222 | 0.1344 | 0.0776 | 0.3584 | 0.9441 | 0.3063 | 0.1879 | 0.1385 | 0.2941 | 0.053 | 0.1072 | 0.2519 | 0.053 | 0.2698 | 0.0893 | 0.0651 | 0.3642 | 1.1314 | 0.2974 | 0.3327 | 0.4819 | 0.5124 | 0.7975 | 0.7171 | 0.1195 | 0.1195 | 0.1671 | 0.335 | 0.128
Load_TR6_F5_9 | prosumer | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.1908 | 0.0494 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.1007 | 0.2342 | 0.3516 | 0.1312 | 0.0809
Load_TR6_F5_9_dup | customer | 0.1081 | 0.2098 | 0.1103 | 0.1925 | 0.1492 | 0.119 | 0.2444 | 0.054 | 0.0627 | 0.3007 | 0.054 | 0.1536 | 0.2098 | 0.054 | 0.2588 | 0.1045 | 0.2286 | 0.1348 | 0.2567 | 0.3834 | 0.2213 | 0.1495 | 0.2885 | 0.125 | 0.1716 | 0.4111 | 0.0865 | 0.2444 | 0.054 | 0.1882 | 0.1752 | 0.054 | 0.2357 | 0.0627 | 0.1232 | 0.2401 | 0.054 | 0.2271 | 0.0713 | 0.054 | 0.0857 | 0.2776 | 0.054 | 0.3007 | 0.0627 | 0.1969 | 0.1665 | 0.119
Load_TR6_F6_1 | prosumer | 0.0554 | 0.1155 | 0.1307 | 0.051 | 0.1174 | 0.0643 | 0.1086 | 0.0731 | 0.1263 | 0.0554 | 0.0643 | 0.1174 | 0.051 | 0.1307 | 0.051 | 0.051 | 0.317 | 0.1131 | 0.2397 | 0.1434 | 0.0599 | 0.1218 | 0.051 | 0.2621 | 0.1591 | 0.151 | 0.4616 | 0.2264 | 0.3551 | 0.1462 | 0.1857 | 0.1081 | 0.1174 | 0.0554 | 0.1317 | 0.8324 | 1.1293 | 1.701 | 0.3391 | 0.4142 | 0.3533 | 0.0997 | 0.0997 | 0.082 | 0.051 | 0.205 | 0.1032 | 0.0554
Load_TR6_F6_10 | customer | 0.1423 | 0.0871 | 0.0706 | 0.1588 | 0.054 | 0.1147 | 0.1147 | 0.0816 | 0.1478 | 0.054 | 0.1754 | 0.054 | 0.065 | 0.1643 | 0.054 | 0.0761 | 0.4422 | 0.3533 | 0.7104 | 0.6381 | 0.2371 | 0.1172 | 0.1699 | 0.0595 | 0.054 | 0.1147 | 0.1147 | 0.054 | 0.1312 | 0.0981 | 0.0595 | 0.1699 | 0.054 | 0.1008 | 0.1727 | 0.1328 | 0.2931 | 0.13 | 0.2469 | 0.3251 | 0.4142 | 0.6395 | 0.6821 | 0.3721 | 0.5876 | 0.5355 | 0.3411 | 0.1169
Load_TR6_F6_10_dup | prosumer | 0.1191 | 0.1001 | 0.1982 | 0.1121 | 0.2205 | 0.1064 | 0.2114 | 0.0926 | 0.2177 | 0.1402 | 0.0851 | 0.2703 | 0.055 | 0.1876 | 0.1678 | 0.055 | 0.2026 | 0.1528 | 0.135 | 0.2205 | 0.0778 | 0.1121 | 0.055 | 0.2026 | 0.1528 | 0.0893 | 0.2511 | 0.07 | 0.1368 | 0.2186 | 0.055 | 0.135 | 0.2205 | 0.1399 | 0.3691 | 0.1841 | 0.1625 | 0.3773 | 0.1803 | 0.3071 | 0.4958 | 0.4652 | 0.7612 | 0.6137 | 0.4098 | 0.6679 | 0.386 | 0.055
Load_TR6_F6_10_tri | prosumer | 0.1386 | 0.054 | 0.101 | 0.0916 | 0.1057 | 0.0869 | 0.0681 | 0.1245 | 0.054 | 0.1386 | 0.054 | 0.054 | 0.1151 | 0.0775 | 0.1198 | 0.0728 | 0.1386 | 0.1449 | 0.2587 | 0.9685 | 0.2824 | 0.2379 | 0.1757 | 0.1882 | 0.1485 | 0.3368 | 0.2457 | 0.1809 | 0.1031 | 0.2601 | 0.1386 | 0.054 | 0.054 | 0.1386 | 0.0616 | 0.1961 | 0.3623 | 0.3009 | 0.4291 | 0.4174 | 0.4297 | 0.2852 | 0.1151 | 0.0963 | 0.0963 | 0.2121 | 0.3658 | 0.4239
Load_TR6_F6_11 | prosumer | 0.1079 | 0.1972 | 0.121 | 0.1963 | 0.0561 | 0.042 | 0.1342 | 0.1972 | 0.042 | 0.1342 | 0.1619 | 0.1695 | 0.042 | 0.1897 | 0.1417 | 0.042 | 0.3202 | 0.0843 | 0.3738 | 1.0797 | 0.1301 | 0.338 | 0.0552 | 0.176 | 0.1554 | 0.042 | 0.2339 | 0.1195 | 0.1055 | 0.1798 | 0.0881 | 0.1619 | 0.097 | 0.1709 | 0.1509 | 0.1342 | 0.176 | 0.0632 | 0.0953 | 0.2959 | 0.3421 | 0.3778 | 0.5919 | 0.4103 | 0.2513 | 0.3658 | 0.1549 | 0.2984
Load_TR6_F6_11_dup | prosumer | 0.1903 | 0.047 | 0.1773 | 0.06 | 0.1382 | 0.0991 | 0.047 | 0.1903 | 0.047 | 0.0731 | 0.1642 | 0.047 | 0.1838 | 0.2845 | 0.047 | 0.0673 | 0.1773 | 0.273 | 0.2101 | 0.0843 | 0.1553 | 0.0991 | 0.047 | 0.3681 | 0.0964 | 0.2818 | 0.0699 | 0.0613 | 0.1439 | 0.3797 | 0.092 | 0.2357 | 0.0751 | 0.185 | 0.1024 | 0.1944 | 0.2918 | 0.0573 | 0.3278 | 0.3732 | 0.5399 | 0.4781 | 0.2611 | 0.047 | 0.0926 | 0.1447 | 0.047 | 0.047
Load_TR6_F6_11_tri | customer | 0.054 | 0.132 | 0.054 | 0.1233 | 0.0627 | 0.1103 | 0.0757 | 0.0843 | 0.1016 | 0.054 | 0.132 | 0.054 | 0.054 | 0.054 | 0.106 | 0.08 | 0.054 | 0.0886 | 0.0973 | 0.0908 | 0.054 | 0.054 | 0.1688 | 0.054 | 0.1357 | 0.4827 | 0.245 | 0.1841 | 0.4586 | 0.2866 | 0.2456 | 0.1896 | 0.1841 | 0.0835 | 0.2436 | 0.0564 | 0.054 | 0.1464 | 0.2648 | 0.2765 | 0.3085 | 0.392 | 0.435 | 0.362 | 0.2556 | 0.3573 | 0.2166 | 0.054
Load_TR6_F6_12 | customer | 0.1177 | 0.227 | 0.051 | 0.1177 | 0.075 | 0.2697 | 0.051 | 0.2432 | 0.1015 | 0.051 | 0.2937 | 0.051 | 0.171 | 0.107 | 0.099 | 0.179 | 0.051 | 0.465 | 0.3526 | 2.8683 | 0.403 | 0.3637 | 0.2552 | 0.3151 | 0.1177 | 0.1661 | 0.1786 | 0.1624 | 0.2329 | 1.4727 | 0.1438 | 0.1177 | 0.227 | 0.051 | 0.1737 | 0.171 | 0.1177 | 0.227 | 0.051 | 0.1177 | 0.227 | 0.051 | 0.1355 | 0.2955 | 0.195 | 0.0547 | 0.226 | 0.1372
Load_TR6_F6_12_dup | customer | 0.1362 | 0.047 | 0.047 | 0.047 | 0.1064 | 0.151 | 0.0619 | 0.1956 | 0.047 | 0.151 | 0.1064 | 0.0842 | 0.1733 | 0.047 | 0.1585 | 0.099 | 0.415 | 1.7066 | 0.047 | 0.4809 | 0.1956 | 0.0619 | 0.1139 | 0.1436 | 0.2033 | 0.9705 | 1.2923 | 1.6727 | 0.1362 | 0.136 | 0.3184 | 0.2048 | 0.2282 | 0.3873 | 0.1665 | 0.047 | 0.1139 | 0.1436 | 0.047 | 0.2105 | 0.047 | 0.047 | 0.047 | 0.1494 | 0.3245 | 0.047 | 0.2105 | 0.047
Load_TR6_F6_12_tri | customer | 0.3067 | 0.049 | 0.1817 | 0.049 | 0.1335 | 0.0973 | 0.0852 | 0.1455 | 0.049 | 0.049 | 0.1455 | 0.0852 | 0.049 | 0.1697 | 0.0611 | 0.0671 | 1.0818 | 0.1534 | 0.049 | 0.5914 | 0.0669 | 0.0694 | 1.0402 | 0.2587 | 0.049 | 0.049 | 0.0792 | 0.1516 | 0.049 | 0.1817 | 0.049 | 0.1576 | 0.1552 | 0.1263 | 0.1901 | 0.0548 | 0.1794 | 0.1497 | 0.2 | 0.4147 | 0.3842 | 0.6581 | 1.4278 | 1.2124 | 0.6323 | 0.4066 | 0.3932 | 0.055
Load_TR6_F6_13 | prosumer | 0.052 | 0.0876 | 0.1351 | 0.052 | 0.0757 | 0.1469 | 0.052 | 0.1351 | 0.0876 | 0.1291 | 0.0935 | 0.052 | 0.052 | 0.1232 | 0.0995 | 0.0698 | 0.1529 | 0.052 | 0.1707 | 0.052 | 0.052 | 0.4893 | 0.2159 | 0.1027 | 0.1441 | 0.0825 | 0.107 | 0.052 | 0.294 | 0.1555 | 0.1465 | 0.2442 | 0.2753 | 0.052 | 0.1291 | 0.0935 | 0.053 | 1.8396 | 0.3741 | 0.3299 | 0.133 | 0.2521 | 0.6982 | 0.2603 | 0.1605 | 0.2284 | 0.3306 | 0.2109
Load_TR6_F6_13_dup | prosumer | 0.0944 | 0.1496 | 0.1932 | 0.1823 | 0.1201 | 0.1347 | 0.1349 | 0.2552 | 0.0741 | 0.243 | 0.1201 | 0.047 | 0.2079 | 0.047 | 0.2609 | 0.1293 | 0.1816 | 0.2086 | 0.0638 | 0.6013 | 0.0858 | 1.0394 | 0.194 | 0.6151 | 2.744 | 2.68 | 0.8407 | 0.5005 | 1.2634 | 0.4981 | 0.3215 | 0.1956 | 0.3642 | 0.4163 | 0.7701 | 0.5509 | 0.2004 | 0.3936 | 0.4989 | 0.4599 | 0.3267 | 0.2641 | 0.047 | 0.2238 | 0.1664 | 0.047 | 0.047 | 0.3432
Load_TR6_F6_13_tri | customer | 0.2038 | 0.082 | 0.1526 | 0.057 | 0.1321 | 0.1777 | 0.0946 | 0.057 | 0.2175 | 0.1298 | 0.1321 | 0.2152 | 0.057 | 0.1634 | 0.1839 | 0.057 | 0.1048 | 0.1611 | 0.1865 | 0.1674 | 0.502 | 1.177 | 1.7948 | 0.2823 | 0.1336 | 0.2226 | 0.0928 | 0.2486 | 0.2216 | 0.062 | 0.159 | 0.0718 | 0.243 | 0.2043 | 0.2673 | 0.4729 | 0.5835 | 0.29 | 1.0764 | 1.627 | 0.5959 | 0.4816 | 0.6031 | 0.5233 | 0.6391 | 0.5402 | 0.7172 | 0.1526
Load_TR6_F6_14 | prosumer | 0.2174 | 0.1888 | 0.049 | 0.0879 | 0.1725 | 0.2649 | 0.1233 | 0.049 | 0.2631 | 0.049 | 0.1742 | 0.1379 | 0.1233 | 0.0871 | 0.225 | 0.049 | 0.5617 | 0.1192 | 0.1189 | 0.2203 | 0.2093 | 0.2811 | 0.1045 | 0.2678 | 0.0696 | 0.1281 | 0.184 | 0.0903 | 0.2218 | 0.091 | 0.2173 | 0.0701 | 0.1959 | 0.1556 | 0.1821 | 0.6159 | 0.0718 | 1.1305 | 0.0913 | 0.4863 | 0.154 | 0.1144 | 0.1977 | 0.0531 | 0.1192 | 0.049 | 0.049 | 0.1805
Load_TR6_F6_14_dup | prosumer | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.09 | 0.8521 | 0.3474 | 0.15 | 0.1798 | 0.0837 | 0.3225 | 0.1077 | 0.0617 | 1.3952 | 1.0523 | 0.7505 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0551 | 0.0602 | 0.1638 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Load_TR6_F6_14_tri | prosumer | 0.05 | 0.129 | 0.1951 | 0.1041 | 0.0981 | 0.2801 | 0.05 | 0.195 | 0.1832 | 0.1003 | 0.2779 | 0.0572 | 0.2008 | 0.05 | 0.3282 | 0.0992 | 0.4994 | 1.3634 | 0.2825 | 0.1159 | 0.2574 | 0.0921 | 0.0931 | 0.237 | 0.1101 | 1.4852 | 0.0875 | 0.4494 | 0.1341 | 0.244 | 0.1161 | 0.1903 | 0.1218 | 0.05 | 0.1702 | 0.05 | 0.3481 | 0.0673 | 0.1081 | 0.4333 | 0.5049 | 0.4805 | 0.6033 | 0.5761 | 0.4943 | 0.5864 | 0.4953 | 0.3282
Load_TR6_F6_15 | prosumer | 0.4098 | 0.4859 | 0.5834 | 0.6385 | 0.1726 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.0601 | 0.0779 | 0.1088 | 0.0913 | 0.146 | 0.2199 | 0.2545 | 0.2049 | 0.2295 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.176 | 0.2661 | 0.4436 | 0.2896 | 0.1503 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.4777 | 0.3902 | 2.0329 | 0.486
Load_TR6_F6_15_dup | customer | 0.1487 | 0.1431 | 0.041 | 0.0818 | 0.1499 | 0.041 | 0.1907 | 0.041 | 0.1703 | 0.0614 | 0.041 | 0.041 | 0.1499 | 0.0818 | 0.0511 | 1.2044 | 0.2037 | 0.0496 | 0.2596 | 0.1495 | 0.2201 | 0.3125 | 1.9132 | 1.1068 | 1.3465 | 0.1627 | 0.3299 | 0.3956 | 0.3945 | 0.1728 | 0.0771 | 0.5747 | 0.0748 | 0.239 | 0.3139 | 0.1398 | 0.1204 | 0.4716 | 0.1558 | 0.4471 | 0.646 | 0.744 | 0.5853 | 0.6742 | 0.503 | 1.8849 | 0.1839 | 0.041
Load_TR6_F6_15_tri | customer | 0.1953 | 0.1549 | 0.052 | 0.2982 | 0.052 | 0.244 | 0.1062 | 0.1073 | 0.1891 | 0.1058 | 0.204 | 0.1462 | 0.052 | 0.204 | 0.1675 | 0.2674 | 0.2037 | 0.2592 | 0.3863 | 0.2691 | 0.4468 | 0.1462 | 0.052 | 0.2781 | 0.0722 | 0.052 | 0.1462 | 0.1487 | 0.2015 | 0.052 | 0.2037 | 0.1466 | 0.1073 | 0.243 | 0.1582 | 0.451 | 0.2849 | 0.3213 | 0.3677 | 0.052 | 0.1669 | 0.1833 | 0.1058 | 0.4451 | 0.052 | 0.1462 | 0.0589 | 0.2442
Load_TR6_F6_16 | prosumer | 0.049 | 0.11 | 0.049 | 0.11 | 0.049 | 0.0863 | 0.0727 | 0.049 | 0.049 | 0.11 | 0.049 | 0.049 | 0.0592 | 0.049 | 0.11 | 0.0625 | 0.0964 | 0.049 | 0.093 | 0.0659 | 0.049 | 0.0541 | 0.0795 | 0.3813 | 0.0705 | 0.11 | 0.049 | 0.11 | 0.049 | 0.049 | 0.11 | 0.049 | 0.0508 | 0.1136 | 0.049 | 0.11 | 0.1541 | 0.2199 | 0.1536 | 0.4226 | 0.7588 | 2.7296 | 2.9558 | 0.5208 | 0.2587 | 0.2317 | 0.524 | 0.3624
Load_TR6_F6_16_dup | customer | 0.2086 | 0.1666 | 0.0888 | 0.1325 | 0.0724 | 0.2748 | 0.084 | 0.1658 | 0.2095 | 0.056 | 0.189 | 0.1862 | 0.056 | 0.1434 | 0.1618 | 0.1806 | 0.1456 | 0.175 | 0.1052 | 0.2701 | 0.1637 | 0.2729 | 0.302 | 0.2066 | 0.5992 | 0.2037 | 0.3296 | 0.3115 | 0.2634 | 0.21 | 0.1332 | 0.1161 | 0.2109 | 0.056 | 1.2823 | 0.5953 | 0.1616 | 0.3013 | 0.269 | 0.2399 | 0.5815 | 0.4152 | 0.2562 | 0.119 | 0.091 | 0.2842 | 0.056 | 0.21
Load_TR6_F6_16_tri | prosumer | 0.1849 | 0.128 | 0.2753 | 0.0835 | 0.2469 | 0.112 | 0.039 | 0.1503 | 0.2531 | 0.0835 | 0.1577 | 0.039 | 0.1503 | 0.245 | 0.0842 | 0.2867 | 0.142 | 0.125 | 0.8527 | 0.3009 | 0.151 | 0.2524 | 0.0538 | 0.3495 | 0.039 | 0.039 | 0.1038 | 0.2995 | 0.039 | 0.2011 | 0.0427 | 0.2011 | 0.1948 | 0.0464 | 0.2234 | 0.18 | 0.039 | 0.1092 | 0.2942 | 0.039 | 0.2482 | 0.5081 | 0.4723 | 0.2813 | 0.2461 | 0.1429 | 0.1525 | 0.0876
Load_TR6_F6_17 | customer | 0.048 | 0.0648 | 0.107 | 0.048 | 0.1238 | 0.048 | 0.048 | 0.2026 | 0.0709 | 0.048 | 0.1238 | 0.048 | 0.048 | 0.048 | 0.1238 | 0.0579 | 0.1238 | 0.048 | 0.048 | 0.1196 | 0.0522 | 0.0523 | 0.5601 | 0.2665 | 0.1049 | 0.1523 | 0.0747 | 0.0799 | 0.4127 | 0.2576 | 0.3766 | 0.0564 | 0.0564 | 0.1974 | 0.0803 | 0.1699 | 0.118 | 0.2443 | 0.2396 | 0.5066 | 0.4499 | 0.3441 | 0.0817 | 0.048 | 0.1238 | 0.048 | 0.0859 | 0.0859
Load_TR6_F6_17_dup | prosumer | 1.5652 | 0.058 | 0.1013 | 0.1734 | 0.058 | 0.2167 | 0.058 | 0.1806 | 0.0941 | 0.058 | 0.2167 | 0.058 | 0.1951 | 0.0796 | 0.058 | 0.058 | 0.1806 | 0.0941 | 0.1575 | 0.1734 | 0.058 | 0.2512 | 0.129 | 0.2488 | 0.1098 | 0.2167 | 0.058 | 0.0869 | 0.1878 | 0.058 | 0.058 | 0.2023 | 0.1242 | 0.3855 | 0.643 | 0.3245 | 0.2419 | 0.252 | 0.3929 | 0.6587 | 0.5563 | 0.7328 | 0.5313 | 0.6222 | 0.4331 | 0.144 | 0.2167 | 0.058
Load_TR6_F6_17_tri | customer | 0.041 | 0.2289 | 0.0729 | 0.1038 | 0.198 | 0.041 | 0.0537 | 0.1817 | 0.1074 | 0.1238 | 0.0983 | 0.0927 | 0.1672 | 0.041 | 0.1812 | 0.1206 | 0.1812 | 0.041 | 0.2068 | 0.095 | 0.085 | 0.1429 | 0.1206 | 0.1682 | 0.4906 | 0.286 | 0.5189 | 0.3554 | 0.3869 | 0.3945 | 0.3138 | 0.3703 | 0.377 | 0.3779 | 0.6748 | 1.162 | 0.2321 | 0.1682 | 0.2484 | 0.5214 | 0.5388 | 0.4236 | 0.8172 | 0.6395 | 0.7078 | 0.4083 | 0.3317 | 0.2921
Load_TR6_F6_18 | customer | 0.0587 | 0.139 | 0.052 | 0.1189 | 0.0788 | 0.052 | 0.1056 | 0.0922 | 0.052 | 0.052 | 0.1457 | 0.052 | 0.0922 | 0.1056 | 0.052 | 0.1457 | 0.052 | 0.052 | 0.1457 | 0.052 | 0.0855 | 0.1123 | 0.052 | 0.052 | 0.1457 | 0.052 | 0.052 | 0.0654 | 0.1323 | 0.167 | 0.1754 | 0.1092 | 0.1057 | 0.1841 | 0.1494 | 0.2263 | 0.3069 | 0.2691 | 0.4072 | 1.1602 | 1.1278 | 0.7377 | 0.7139 | 0.8032 | 0.0654 | 0.052 | 0.1457 | 0.052
Load_TR6_F6_18_dup | customer | 0.1819 | 0.1611 | 0.047 | 0.1287 | 0.1079 | 0.1535 | 0.1112 | 0.0797 | 0.1991 | 0.1287 | 0.047 | 0.2377 | 0.1053 | 0.1383 | 0.2138 | 0.047 | 0.1002 | 0.2428 | 0.0995 | 2.1966 | 0.3534 | 0.4137 | 0.2086 | 1.0992 | 1.0083 | 0.2235 | 0.1683 | 0.1026 | 0.3336 | 0.1241 | 0.2727 | 0.504 | 0.2136 | 0.1235 | 0.1222 | 0.3395 | 0.3474 | 0.4177 | 0.1575 | 0.0587 | 0.2843 | 0.047 | 0.1903 | 0.1528 | 0.1002 | 0.1961 | 0.3762 | 0.4781
Load_TR6_F6_18_tri | customer | 0.4513 | 0.3232 | 0.2727 | 0.1363 | 0.057 | 0.1363 | 0.057 | 0.057 | 0.0658 | 0.1275 | 0.057 | 0.057 | 0.1011 | 0.0922 | 0.057 | 0.1058 | 0.0682 | 0.8861 | 0.1363 | 0.057 | 0.057 | 0.057 | 0.1099 | 0.0834 | 0.057 | 0.1363 | 0.057 | 0.1363 | 0.057 | 0.1363 | 0.057 | 0.057 | 0.057 | 1.263 | 0.8385 | 0.1042 | 0.1852 | 0.2467 | 1.0522 | 1.3462 | 1.3784 | 0.3542 | 0.4631 | 0.838 | 0.6385 | 0.5651 | 0.4399 | 0.6156
Load_TR6_F6_19 | customer | 0.054 | 0.1864 | 0.0603 | 0.054 | 0.1864 | 0.0603 | 0.0666 | 0.1801 | 0.054 | 0.1801 | 0.0666 | 0.054 | 0.1927 | 0.054 | 0.054 | 0.1927 | 0.4951 | 0.2003 | 0.2167 | 0.5054 | 0.2429 | 0.2497 | 0.1044 | 0.0981 | 0.3204 | 0.1553 | 0.1977 | 0.2044 | 0.3098 | 0.1738 | 0.1261 | 0.2506 | 0.2159 | 0.8827 | 1.0173 | 0.054 | 0.0666 | 0.1801 | 0.054 | 0.1927 | 0.054 | 0.054 | 0.1234 | 0.1234 | 0.1357 | 0.5017 | 0.054 | 0.1738
Load_TR6_F6_19_dup | customer | 0.1547 | 0.047 | 0.047 | 0.1547 | 0.066 | 0.0787 | 0.142 | 0.047 | 0.085 | 0.1357 | 0.047 | 0.047 | 0.1737 | 0.047 | 0.047 | 0.047 | 0.2194 | 0.1593 | 1.4743 | 0.179 | 0.116 | 0.1625 | 0.1774 | 0.1862 | 1.6277 | 1.698 | 0.5062 | 0.369 | 0.3038 | 0.3038 | 0.2687 | 0.3347 | 0.3314 | 0.2383 | 0.1611 | 0.0597 | 0.8382 | 0.047 | 0.047 | 0.1737 | 0.047 | 0.1737 | 0.047 | 0.047 | 0.104 | 0.1167 | 0.5075 | 0.5374
Load_TR6_F6_19_tri | prosumer | 1.4919 | 0.198 | 0.054 | 0.2693 | 0.1869 | 0.054 | 0.1632 | 0.1789 | 0.1681 | 0.1632 | 0.2207 | 0.1887 | 0.116 | 0.2778 | 0.3294 | 1.2673 | 0.231 | 0.1888 | 0.2213 | 0.3032 | 0.4066 | 0.1222 | 0.2046 | 0.5446 | 1.7556 | 1.6946 | 0.3591 | 0.1985 | 0.3166 | 1.2721 | 0.3948 | 0.1747 | 0.131 | 0.371 | 0.1453 | 0.2199 | 0.2469 | 0.7333 | 1.7611 | 0.4414 | 0.4348 | 0.5174 | 0.7517 | 0.5188 | 0.888 | 0.4255 | 0.1615 | 0.2948
Load_TR6_F6_1_dup | prosumer | 0.6777 | 0.2975 | 0.1331 | 0.2034 | 0.039 | 0.1517 | 0.039 | 0.1782 | 0.1527 | 0.0645 | 0.1706 | 0.1461 | 0.1905 | 0.1461 | 0.2904 | 0.3235 | 0.1776 | 0.1252 | 0.039 | 0.1252 | 0.2114 | 0.0721 | 0.2644 | 0.039 | 0.2041 | 0.1325 | 0.039 | 0.2074 | 0.1292 | 0.0615 | 1.193 | 0.5837 | 0.0629 | 0.2745 | 0.2799 | 1.707 | 0.6123 | 1.0009 | 2.8028 | 2.0251 | 0.4756 | 1.4462 | 0.0954 | 0.2081 | 0.1172 | 0.1066 | 0.2243 | 0.1123
Load_TR6_F6_1_tri | customer | 0.2127 | 0.2841 | 0.1348 | 0.041 | 0.2593 | 0.041 | 0.041 | 0.041 | 0.1348 | 0.041 | 0.041 | 0.0544 | 0.1214 | 0.041 | 0.041 | 0.1348 | 0.041 | 0.8415 | 1.6426 | 1.3606 | 0.9599 | 0.9502 | 0.1229 | 0.1002 | 0.2006 | 0.0585 | 0.041 | 0.1348 | 0.041 | 0.1281 | 0.0477 | 0.041 | 0.1523 | 0.1778 | 0.0913 | 0.2382 | 0.1734 | 0.2543 | 0.4748 | 0.3187 | 0.1249 | 0.2941 | 0.1748 | 0.5545 | 0.2439 | 0.5292 | 0.3258 | 0.041
Load_TR6_F6_2 | prosumer | 0.054 | 0.1884 | 0.054 | 0.1884 | 0.054 | 0.1548 | 0.0876 | 0.1077 | 0.1346 | 0.054 | 0.054 | 0.054 | 0.1884 | 0.054 | 0.0876 | 0.2234 | 0.054 | 0.1749 | 0.0674 | 0.2243 | 0.3149 | 0.2995 | 0.25 | 0.5658 | 0.2361 | 0.162 | 0.054 | 0.054 | 0.3443 | 0.3674 | 1.3489 | 0.756 | 1.5054 | 1.6958 | 0.3187 | 0.3064 | 0.172 | 0.1639 | 0.0863 | 0.3626 | 0.2834 | 0.3523 | 0.5009 | 0.5856 | 0.6959 | 0.4609 | 0.3702 | 0.1919
Load_TR6_F6_20 | prosumer | 0.2571 | 0.056 | 0.056 | 0.056 | 0.0926 | 0.2205 | 0.056 | 0.2571 | 0.056 | 0.056 | 0.1657 | 0.1474 | 0.056 | 0.0948 | 0.2297 | 0.056 | 0.2205 | 0.0926 | 0.1383 | 0.1748 | 0.101 | 0.3092 | 1.5479 | 0.5339 | 0.429 | 0.3908 | 0.197 | 1.9931 | 0.0982 | 0.056 | 0.2993 | 0.1827 | 0.2649 | 0.423 | 0.2508 | 0.2938 | 0.2388 | 0.1074 | 0.1626 | 0.7577 | 1.1895 | 1.15 | 0.6617 | 0.6074 | 0.4599 | 0.056 | 0.056 | 0.1291
Load_TR6_F6_20_dup | customer | 0.0897 | 0.034 | 0.034 | 0.0982 | 0.0468 | 0.0821 | 0.0682 | 0.0768 | 0.034 | 0.0811 | 0.064 | 0.034 | 0.034 | 0.1111 | 0.2918 | 0.1798 | 0.1797 | 0.0725 | 0.0725 | 0.0854 | 0.0597 | 0.1197 | 0.4145 | 0.168 | 0.2493 | 0.1627 | 1.3402 | 0.7751 | 0.2609 | 0.1811 | 0.2246 | 0.2018 | 0.2577 | 0.2269 | 0.5269 | 1.7902 | 1.1048 | 0.1947 | 1.0221 | 0.3483 | 0.2383 | 0.4348 | 0.2858 | 0.2853 | 0.034 | 0.1357 | 0.216 | 0.3089
Load_TR6_F6_20_tri | prosumer | 0.0865 | 0.1556 | 0.045 | 0.197 | 0.045 | 0.045 | 0.197 | 0.045 | 0.1141 | 0.1279 | 0.045 | 0.197 | 0.045 | 0.0708 | 0.1001 | 0.1556 | 0.0812 | 0.2131 | 0.6091 | 2.179 | 0.045 | 0.045 | 0.197 | 0.045 | 0.1279 | 0.1141 | 0.0519 | 0.1901 | 0.045 | 0.197 | 0.045 | 0.0869 | 0.2341 | 2.1727 | 0.8067 | 0.2232 | 0.0656 | 0.2509 | 0.0758 | 0.3251 | 0.4125 | 0.3053 | 0.521 | 0.7396 | 0.8242 | 0.4991 | 0.4349 | 0.5479
Load_TR6_F6_21 | customer | 0.1254 | 0.052 | 0.1254 | 0.052 | 0.1254 | 0.052 | 0.0724 | 0.105 | 0.052 | 0.052 | 0.052 | 0.052 | 0.0642 | 0.1132 | 0.052 | 0.1254 | 0.052 | 0.2161 | 0.2836 | 0.2265 | 0.1174 | 0.1134 | 0.5578 | 0.2652 | 0.192 | 0.1772 | 0.1772 | 0.5284 | 0.052 | 0.1254 | 0.052 | 0.1254 | 0.2181 | 0.2022 | 0.2428 | 0.6408 | 1.6016 | 0.1057 | 0.1034 | 1.338 | 0.8674 | 0.5839 | 0.4352 | 0.3243 | 0.3163 | 0.4132 | 1.4392 | 0.6315
Load_TR6_F6_21_dup | prosumer | 0.1244 | 0.1021 | 0.052 | 0.091 | 0.1355 | 0.052 | 0.052 | 0.1188 | 0.1077 | 0.0854 | 0.1411 | 0.052 | 0.2061 | 0.052 | 0.1077 | 0.1313 | 0.0537 | 0.2135 | 0.0836 | 0.303 | 0.1262 | 0.062 | 0.1813 | 0.137 | 0.233 | 0.299 | 0.3454 | 0.3743 | 0.2857 | 0.2038 | 0.2179 | 0.5131 | 0.2342 | 0.347 | 1.9509 | 1.9731 | 0.4431 | 0.1481 | 0.1826 | 0.052 | 0.1577 | 0.0687 | 0.052 | 0.0716 | 0.3675 | 0.3739 | 0.4304 | 0.4093
Load_TR6_F6_21_tri | prosumer | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.0957 | 0.2023 | 1.586 | 0.2136 | 0.2404 | 0.3295 | 0.2387 | 0.2666 | 0.2173 | 0.2148 | 0.2039 | 0.0667 | 0.2789 | 0.057 | 0.0875 | 0.1359 | 0.1655 | 0.2202 | 0.4241 | 1.5294 | 0.1527 | 0.1178 | 0.394 | 0.4334 | 0.4249 | 0.4501 | 1.3017 | 0.3582 | 0.3034 | 0.3893 | 0.6133 | 0.6786 | 0.4811 | 0.3101 | 0.057
Load_TR6_F6_22 | customer | 0.1 | 0.039 | 0.161 | 0.039 | 0.039 | 0.039 | 0.161 | 0.039 | 0.039 | 0.161 | 0.039 | 0.1174 | 0.0826 | 0.039 | 0.1174 | 0.0826 | 0.039 | 0.1436 | 0.0564 | 0.0564 | 0.4432 | 0.3622 | 0.3965 | 0.1465 | 0.3079 | 0.383 | 0.1013 | 0.1696 | 0.3169 | 0.4179 | 0.2562 | 0.1323 | 1.1966 | 0.5117 | 0.3723 | 0.1535 | 0.2504 | 0.2941 | 0.4967 | 0.5827 | 0.8331 | 0.743 | 0.959 | 0.5067 | 0.6223 | 1.5459 | 0.4965 | 0.4752
Load_TR6_F6_22_dup | customer | 0.2227 | 0.1151 | 0.3522 | 0.0744 | 0.3055 | 0.1852 | 0.051 | 0.2285 | 0.2622 | 0.051 | 0.268 | 0.1212 | 0.2179 | 0.2025 | 0.051 | 0.3144 | 0.0613 | 0.2262 | 0.2861 | 0.051 | 0.3518 | 0.563 | 0.3647 | 0.3004 | 0.1628 | 0.6804 | 1.4358 | 1.6422 | 0.3159 | 0.1537 | 0.3341 | 0.1553 | 0.3568 | 0.4492 | 0.2858 | 0.4827 | 0.5195 | 0.5182 | 0.5961 | 0.6181 | 0.1527 | 0.1446 | 0.2771 | 0.1199 | 0.2677 | 0.223 | 0.051 | 0.3724
Load_TR6_F6_22_tri | prosumer | 0.2816 | 0.2033 | 0.1291 | 0.1033 | 0.2098 | 0.172 | 0.0764 | 0.2944 | 0.0649 | 0.2183 | 0.1635 | 0.0764 | 0.278 | 0.0814 | 0.054 | 0.2531 | 0.1287 | 0.0839 | 0.5026 | 0.2776 | 0.3392 | 0.1674 | 0.1525 | 0.0649 | 0.2183 | 0.1635 | 0.054 | 0.173 | 0.2088 | 0.054 | 0.1859 | 0.2239 | 0.1805 | 0.3794 | 0.5955 | 1.3508 | 3.7459 | 0.104 | 0.0689 | 0.3128 | 0.054 | 0.054 | 0.2183 | 0.1635 | 0.0689 | 0.3128 | 0.054 | 0.3203
Load_TR6_F6_23 | prosumer | 0.5882 | 0.7813 | 0.052 | 0.052 | 0.1484 | 0.052 | 0.1484 | 0.052 | 0.052 | 0.1484 | 0.052 | 0.052 | 0.1484 | 0.052 | 0.052 | 0.052 | 0.1484 | 0.052 | 0.3881 | 1.4103 | 0.2312 | 0.2278 | 0.3323 | 0.2387 | 0.3262 | 0.1504 | 0.056 | 0.602 | 0.5703 | 0.3626 | 0.3215 | 2.5018 | 2.7719 | 1.2218 | 0.3058 | 0.1931 | 0.2258 | 0.2999 | 0.2574 | 0.5837 | 0.4726 | 0.6074 | 1.6151 | 0.5905 | 0.4387 | 0.6311 | 0.0589 | 0.1415
Load_TR6_F6_23_dup | customer | 0.3155 | 0.0932 | 0.0932 | 0.2431 | 0.144 | 0.2776 | 0.1191 | 0.1483 | 0.1435 | 0.2018 | 0.2328 | 0.1236 | 0.1527 | 0.1553 | 0.1858 | 0.1306 | 0.2011 | 0.401 | 0.3297 | 2.2031 | 0.3703 | 0.2867 | 0.3323 | 0.2205 | 0.2218 | 0.2238 | 0.3617 | 0.3564 | 0.2557 | 0.0894 | 0.1826 | 0.063 | 0.2733 | 0.2908 | 0.2762 | 1.4792 | 0.6578 | 0.3024 | 0.4321 | 0.5315 | 0.126 | 0.2291 | 0.5173 | 0.3206 | 0.574 | 0.4136 | 0.4121 | 0.6332
Load_TR6_F6_23_tri | prosumer | 0.036 | 0.1527 | 0.036 | 0.036 | 0.1118 | 0.0768 | 0.0477 | 0.141 | 0.036 | 0.1527 | 0.036 | 0.106 | 0.0827 | 0.0768 | 0.1118 | 0.1956 | 0.2473 | 0.3015 | 0.0948 | 0.1527 | 0.036 | 1.7484 | 0.2156 | 0.2823 | 0.259 | 0.2583 | 0.3585 | 0.1774 | 0.2837 | 0.036 | 0.036 | 0.036 | 0.1527 | 0.036 | 0.1875 | 0.0682 | 0.2063 | 0.3577 | 0.2615 | 0.2531 | 0.2855 | 0.3699 | 0.5027 | 0.6114 | 0.2163 | 0.1527 | 0.036 | 0.0477
Load_TR6_F6_24 | prosumer | 0.2092 | 0.1034 | 0.2223 | 0.1031 | 0.1539 | 0.2165 | 0.0874 | 0.1827 | 0.053 | 0.2115 | 0.1644 | 0.1323 | 0.2436 | 0.053 | 0.2021 | 0.1738 | 0.053 | 0.4486 | 0.1644 | 0.125 | 0.2508 | 0.053 | 0.1254 | 0.2505 | 0.0586 | 0.1588 | 0.1178 | 0.1467 | 0.053 | 0.295 | 0.0808 | 0.053 | 0.1258 | 0.092 | 0.2584 | 0.1175 | 0.1503 | 0.2256 | 0.1177 | 0.2043 | 0.1716 | 0.0962 | 0.1683 | 0.053 | 0.2338 | 0.1421 | 0.1971 | 0.1788
Load_TR6_F6_24_dup | customer | 0.1334 | 0.0549 | 0.05 | 0.05 | 0.1384 | 0.05 | 0.1236 | 0.0647 | 0.0598 | 0.1285 | 0.05 | 0.05 | 0.1138 | 0.0745 | 0.0795 | 0.1089 | 0.0795 | 0.1714 | 0.1401 | 1.1418 | 0.1138 | 0.05 | 0.1384 | 0.4884 | 0.1384 | 0.1273 | 0.1236 | 0.0708 | 0.0788 | 0.1257 | 0.1389 | 0.0837 | 0.1208 | 0.0741 | 0.0984 | 0.1006 | 0.2349 | 0.1106 | 0.1448 | 0.3548 | 0.4186 | 0.3839 | 0.4922 | 0.5629 | 1.1592 | 0.7488 | 0.3171 | 0.05
Load_TR6_F6_24_tri | customer | 0.2719 | 0.052 | 0.1792 | 0.1198 | 0.1015 | 0.2075 | 0.0965 | 0.1036 | 0.2004 | 0.052 | 0.1842 | 0.1644 | 0.1227 | 0.1368 | 0.052 | 0.0803 | 0.1792 | 0.052 | 0.052 | 0.141 | 0.3321 | 1.3662 | 0.3339 | 0.1048 | 0.6736 | 1.2293 | 0.3364 | 0.3851 | 0.227 | 0.4204 | 2.5258 | 1.3899 | 2.0774 | 1.0047 | 0.7934 | 0.2075 | 0.052 | 0.141 | 0.151 | 0.1184 | 0.1311 | 0.1792 | 0.0803 | 0.7724 | 0.2966 | 0.0569 | 0.1926 | 0.151
Load_TR6_F6_25 | customer | 0.1575 | 0.049 | 0.2248 | 0.0809 | 0.1737 | 0.132 | 0.1162 | 0.1894 | 0.049 | 0.049 | 0.2567 | 0.049 | 0.1575 | 0.2609 | 0.229 | 0.1563 | 0.0741 | 0.224 | 0.171 | 0.1371 | 1.2344 | 0.5633 | 0.154 | 0.317 | 0.3329 | 0.1463 | 0.2492 | 0.0714 | 0.0938 | 0.1894 | 0.1162 | 0.23 | 0.1279 | 0.051 | 0.309 | 0.3711 | 0.3072 | 0.0969 | 0.1783 | 1.8633 | 0.5422 | 0.2309 | 0.3295 | 0.2807 | 0.3066 | 0.4227 | 0.8571 | 0.7434
Load_TR6_F6_25_dup | prosumer | 0.7085 | 0.8561 | 0.6791 | 0.4445 | 0.5047 | 0.5046 | 0.4546 | 0.053 | 0.103 | 0.3702 | 0.0706 | 0.1462 | 0.2206 | 0.1419 | 0.2425 | 0.0772 | 0.2986 | 0.3324 | 0.219 | 0.2361 | 1.31 | 0.1763 | 1.1442 | 1.6591 | 2.9719 | 2.5166 | 0.3887 | 0.4531 | 1.1197 | 1.8656 | 0.7043 | 0.8619 | 0.4219 | 0.121 | 0.3344 | 0.535 | 0.2886 | 0.4054 | 1.8025 | 1.4287 | 0.6183 | 0.9348 | 0.7434 | 1.0702 | 1.0687 | 1.0089 | 0.9259 | 0.9322
Load_TR6_F6_25_tri | prosumer | 0.2114 | 0.056 | 0.056 | 0.056 | 0.2114 | 0.056 | 0.1831 | 0.0842 | 0.1196 | 0.1478 | 0.056 | 0.1902 | 0.0772 | 0.0631 | 0.2043 | 0.056 | 0.056 | 0.2483 | 0.09 | 0.1205 | 0.1715 | 0.913 | 2.4546 | 1.5886 | 0.4008 | 0.6994 | 2.5671 | 2.261 | 0.1196 | 0.1837 | 0.2352 | 0.7049 | 0.3116 | 0.3374 | 0.3927 | 0.264 | 0.2114 | 0.3739 | 0.4871 | 0.3444 | 0.056 | 0.2114 | 0.2614 | 0.2122 | 0.1972 | 0.0701 | 0.056 | 0.0772
Load_TR6_F6_26 | customer | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.222 | 0.4265 | 0.5606 | 0.516 | 0.1593
Load_TR6_F6_26_dup | prosumer | 0.042 | 0.115 | 0.042 | 0.042 | 0.042 | 0.1109 | 0.0461 | 0.042 | 0.042 | 0.042 | 0.1109 | 0.0461 | 0.042 | 0.042 | 0.0947 | 0.102 | 0.042 | 0.042 | 0.042 | 0.2446 | 0.042 | 0.0947 | 0.0623 | 0.042 | 0.042 | 0.115 | 0.042 | 0.042 | 0.115 | 0.042 | 0.1353 | 0.0825 | 0.1446 | 0.1864 | 0.042 | 0.0753 | 0.1367 | 1.3271 | 0.042 | 0.042 | 0.115 | 0.042 | 0.115 | 0.042 | 0.0461 | 0.1109 | 0.0704 | 0.0866
Load_TR6_F6_26_tri | prosumer | 0.054 | 0.1175 | 0.054 | 0.0681 | 0.2404 | 0.1336 | 0.115 | 0.2167 | 0.054 | 0.3059 | 0.054 | 0.1034 | 0.1281 | 0.1825 | 0.054 | 0.054 | 0.2082 | 0.1482 | 0.0575 | 0.2424 | 0.1175 | 0.054 | 0.2424 | 0.0752 | 0.0963 | 0.0716 | 1.1937 | 0.0649 | 0.2298 | 0.212 | 0.3681 | 0.9931 | 0.487 | 0.4045 | 0.3254 | 0.4305 | 0.1996 | 0.3827 | 0.2238 | 0.3279 | 2.0188 | 1.5906 | 0.9017 | 0.582 | 0.054 | 0.2031 | 0.1568 | 0.0611
Load_TR6_F6_27 | customer | 0.048 | 0.2272 | 0.048 | 0.048 | 0.2272 | 0.048 | 0.1539 | 0.1213 | 0.048 | 0.2272 | 0.048 | 0.2272 | 0.048 | 0.0969 | 0.1783 | 0.048 | 0.048 | 0.048 | 0.2272 | 0.048 | 1.0212 | 0.0969 | 0.0643 | 0.2109 | 0.048 | 0.2272 | 0.048 | 0.048 | 0.3277 | 0.1973 | 0.1509 | 0.2424 | 0.0642 | 0.0851 | 0.2787 | 0.3038 | 0.0584 | 0.1454 | 0.0643 | 0.2716 | 0.0802 | 0.2885 | 0.249 | 0.4339 | 1.4475 | 0.5929 | 0.2233 | 0.162
Load_TR6_F6_27_dup | customer | 0.1547 | 0.1833 | 0.056 | 0.056 | 0.259 | 0.079 | 0.0703 | 0.2677 | 0.056 | 0.056 | 0.056 | 0.2677 | 0.0703 | 0.1608 | 0.1772 | 0.1192 | 0.4061 | 1.6454 | 2.7619 | 1.0943 | 0.056 | 0.2205 | 0.1174 | 0.1969 | 1.6703 | 1.1759 | 0.2595 | 0.387 | 0.1407 | 0.1158 | 0.226 | 0.6708 | 1.8759 | 0.6628 | 0.4027 | 0.3906 | 0.2193 | 0.3344 | 0.3735 | 0.6267 | 0.724 | 0.6359 | 0.5024 | 0.4874 | 0.363 | 0.9421 | 0.4182 | 0.2079
Load_TR6_F6_27_tri | prosumer | 0.2138 | 0.046 | 0.1833 | 0.0765 | 0.1146 | 0.1451 | 0.046 | 0.2138 | 0.046 | 0.1604 | 0.0994 | 0.046 | 0.046 | 0.1375 | 0.2607 | 0.0707 | 0.2168 | 0.3815 | 0.1146 | 2.0723 | 0.6099 | 0.203 | 0.0861 | 0.1375 | 0.1223 | 0.046 | 0.1909 | 1.1296 | 0.2067 | 0.3279 | 0.1079 | 0.1487 | 0.376 | 0.2966 | 0.306 | 0.1231 | 0.1236 | 0.046 | 0.046 | 0.046 | 0.2138 | 0.046 | 0.1451 | 0.1146 | 0.046 | 0.046 | 0.1924 | 0.7252
Load_TR6_F6_28 | customer | 0.7194 | 0.5078 | 0.5059 | 0.4831 | 0.1434 | 0.1554 | 0.1978 | 0.1587 | 0.1557 | 0.159 | 0.1485 | 0.2358 | 0.058 | 0.0719 | 0.361 | 0.058 | 0.1951 | 0.1892 | 0.2181 | 0.6069 | 0.6304 | 0.1464 | 0.288 | 0.2943 | 0.3549 | 0.1837 | 0.1911 | 0.1579 | 0.2991 | 3.0261 | 2.9471 | 0.5879 | 0.2437 | 0.3486 | 0.106 | 0.2441 | 0.1431 | 2.0566 | 1.7342 | 0.6827 | 0.5982 | 0.9191 | 0.7375 | 0.6437 | 0.735 | 0.7823 | 0.3306 | 0.2056
Load_TR6_F6_28_dup | customer | 0.86 | 0.6393 | 0.3871 | 0.1919 | 0.1795 | 0.0638 | 0.1887 | 0.0983 | 0.2796 | 0.047 | 0.1336 | 0.2443 | 0.0791 | 0.1923 | 0.1662 | 0.1433 | 0.2218 | 0.1935 | 0.2036 | 0.2104 | 0.1279 | 0.2186 | 0.1705 | 0.0507 | 0.3087 | 0.2554 | 0.2389 | 0.5085 | 0.1383 | 0.0631 | 0.1876 | 0.1389 | 0.0984 | 0.0584 | 0.2978 | 0.1556 | 0.4161 | 0.2502 | 0.296 | 0.4988 | 0.4578 | 0.5372 | 0.6022 | 0.4648 | 0.0599 | 0.1108 | 0.267 | 0.0631
Load_TR6_F6_28_tri | prosumer | 0.053 | 0.1209 | 0.053 | 0.0832 | 0.0907 | 0.053 | 0.1209 | 0.053 | 0.053 | 0.0907 | 0.0832 | 0.1697 | 0.334 | 0.1209 | 0.053 | 0.0869 | 0.2702 | 0.2605 | 0.4216 | 0.2504 | 0.3293 | 0.0643 | 0.0681 | 0.1058 | 0.3334 | 0.0832 | 0.053 | 0.1209 | 0.0643 | 0.1096 | 0.0756 | 0.0983 | 0.053 | 0.053 | 0.0945 | 0.0794 | 0.155 | 0.3522 | 0.0833 | 0.4538 | 0.7806 | 0.7169 | 0.5174 | 0.6187 | 0.8185 | 0.7373 | 0.7022 | 0.3214
Load_TR6_F6_29 | customer | 0.5521 | 0.2815 | 0.1591 | 0.0647 | 0.2063 | 0.049 | 0.049 | 0.222 | 0.049 | 0.1512 | 0.1198 | 0.049 | 0.2142 | 0.0569 | 0.1038 | 0.3551 | 0.1418 | 0.187 | 0.1041 | 0.1041 | 0.167 | 0.0548 | 0.2509 | 0.1215 | 0.1753 | 0.3081 | 0.1949 | 0.5239 | 0.3965 | 0.1955 | 0.3742 | 0.4365 | 0.4061 | 0.3488 | 0.3947 | 0.2598 | 0.3129 | 0.3716 | 1.528 | 1.2817 | 0.7127 | 0.5118 | 0.7592 | 0.4575 | 0.5331 | 0.6434 | 0.6777 | 0.7769
Load_TR6_F6_29_dup | prosumer | 0.058 | 0.058 | 0.1607 | 0.1059 | 0.0922 | 0.1744 | 0.058 | 0.2018 | 0.0648 | 0.147 | 0.1196 | 0.058 | 0.1333 | 0.1333 | 0.058 | 0.1744 | 0.0922 | 0.058 | 0.2087 | 0.2113 | 0.3668 | 0.4278 | 0.4249 | 4.231 | 3.2232 | 0.6594 | 0.3335 | 0.8885 | 0.9344 | 0.3753 | 0.3559 | 0.8294 | 0.2697 | 0.2867 | 0.3644 | 0.2343 | 0.386 | 0.4537 | 0.1402 | 0.058 | 0.1607 | 0.1059 | 1.0091 | 1.0617 | 0.058 | 0.1881 | 0.0785 | 0.058
Load_TR6_F6_29_tri | prosumer | 0.049 | 0.049 | 0.1479 | 0.0737 | 0.049 | 0.049 | 0.1726 | 0.049 | 0.049 | 0.1541 | 0.0675 | 0.049 | 0.1726 | 0.049 | 0.049 | 0.0595 | 1.3601 | 0.916 | 1.1712 | 0.049 | 0.1726 | 0.049 | 0.1479 | 0.0737 | 0.049 | 0.0923 | 0.1293 | 0.0923 | 0.1293 | 0.057 | 0.312 | 1.8827 | 2.6091 | 2.8747 | 0.3944 | 0.1003 | 0.3606 | 0.049 | 0.049 | 0.1602 | 0.0614 | 0.0552 | 0.1664 | 0.0552 | 0.1664 | 0.049 | 0.049 | 0.0675
Load_TR6_F6_2_dup | prosumer | 0.04 | 0.0957 | 0.1593 | 0.04 | 0.1753 | 0.0798 | 0.04 | 0.1036 | 0.1514 | 0.04 | 0.04 | 0.04 | 0.1673 | 0.0877 | 0.0877 | 0.1673 | 0.04 | 0.215 | 0.04 | 0.04 | 0.3344 | 0.0867 | 0.2175 | 0.1793 | 0.2959 | 0.2534 | 0.2786 | 0.28 | 0.048 | 0.2071 | 0.04 | 0.1912 | 0.2183 | 0.5053 | 0.4533 | 0.4186 | 0.2866 | 0.2874 | 0.1134 | 0.1362 | 0.3364 | 0.3469 | 0.4869 | 0.286 | 0.4342 | 0.7652 | 0.0559 | 0.1991
Load_TR6_F6_2_tri | prosumer | 0.058 | 0.3031 | 0.0998 | 0.2188 | 0.1995 | 0.1409 | 0.2442 | 0.2085 | 0.1319 | 0.3067 | 0.058 | 0.2771 | 0.0653 | 0.3023 | 0.058 | 0.2516 | 0.2069 | 0.2791 | 0.1681 | 0.3311 | 0.1981 | 0.2903 | 0.4739 | 0.599 | 1.1839 | 0.3418 | 0.4499 | 0.4598 | 0.714 | 0.2566 | 0.2213 | 0.1816 | 0.109 | 0.4626 | 0.2942 | 0.538 | 1.2064 | 0.7283 | 3.1452 | 2.9911 | 1.4404 | 0.5711 | 0.6326 | 0.6666 | 0.2959 | 0.5548 | 0.1971 | 0.4961
Load_TR6_F6_3 | customer | 0.05 | 0.1212 | 0.1035 | 0.0856 | 0.0856 | 0.05 | 0.1212 | 0.0579 | 0.1133 | 0.0658 | 0.1054 | 0.05 | 0.1212 | 0.05 | 0.1212 | 0.05 | 1.39 | 1.9818 | 0.0929 | 0.0774 | 0.1707 | 0.2122 | 0.0968 | 0.05 | 0.0896 | 0.0817 | 0.2458 | 0.1391 | 0.1542 | 0.1648 | 0.1973 | 0.1982 | 0.0716 | 0.076 | 0.0551 | 0.1707 | 0.1268 | 0.157 | 0.3465 | 0.1677 | 0.1565 | 0.31 | 0.383 | 0.4626 | 0.3291 | 0.1124 | 0.1212 | 0.0579
Load_TR6_F6_30 | prosumer | 0.2153 | 0.2253 | 0.05 | 0.2907 | 0.1499 | 0.1213 | 0.3096 | 0.0596 | 0.2815 | 0.1591 | 0.1501 | 0.204 | 0.0932 | 0.3003 | 0.1692 | 0.0644 | 0.1597 | 0.2425 | 0.0884 | 0.2612 | 0.1054 | 0.082 | 0.245 | 0.1805 | 1.3452 | 0.2911 | 0.5263 | 0.5608 | 1.2779 | 0.303 | 0.371 | 0.3514 | 0.339 | 0.1475 | 0.1724 | 0.3125 | 0.2812 | 0.5006 | 0.7825 | 0.5096 | 0.6379 | 0.6434 | 0.6601 | 0.4017 | 0.5506 | 0.2345 | 0.1145 | 0.2785
Load_TR6_F6_30_dup | customer | 0.2731 | 0.2496 | 0.1669 | 0.0764 | 0.3924 | 0.1304 | 0.1228 | 0.2707 | 0.1863 | 0.2731 | 0.1203 | 0.057 | 0.2137 | 0.2268 | 0.1885 | 0.1127 | 0.1798 | 0.3365 | 0.057 | 0.1692 | 0.3535 | 0.057 | 0.1639 | 0.2554 | 0.2272 | 0.3779 | 0.5374 | 0.3346 | 1.7766 | 0.1971 | 0.4553 | 0.1867 | 0.057 | 0.3224 | 0.0711 | 0.1281 | 0.296 | 0.1815 | 0.259 | 0.2379 | 0.1104 | 0.4041 | 0.0911 | 0.259 | 0.2379 | 0.2086 | 0.2649 | 0.2128
Load_TR6_F6_30_tri | prosumer | 0.1562 | 0.054 | 0.054 | 0.164 | 0.054 | 0.164 | 0.054 | 0.054 | 0.109 | 0.109 | 0.054 | 0.164 | 0.054 | 0.054 | 0.4 | 0.2661 | 0.1978 | 0.1937 | 0.233 | 0.2682 | 0.1969 | 0.3088 | 0.2381 | 0.054 | 0.2572 | 0.3115 | 0.054 | 0.164 | 0.054 | 0.054 | 0.054 | 0.164 | 0.054 | 0.0933 | 0.1247 | 0.054 | 0.2963 | 1.7298 | 2.311 | 1.0317 | 0.4094 | 1.2764 | 0.6643 | 0.6859 | 0.6326 | 0.6116 | 0.3303 | 0.7015
Load_TR6_F6_31 | customer | 0.5301 | 0.3633 | 0.8709 | 0.3093 | 0.044 | 0.1915 | 0.0673 | 0.044 | 0.1915 | 0.0673 | 0.044 | 0.2071 | 0.0518 | 0.0536 | 0.1437 | 0.1572 | 0.044 | 0.0906 | 0.1742 | 1.714 | 0.2661 | 0.0889 | 0.1585 | 0.244 | 0.3715 | 0.2586 | 0.2038 | 0.2873 | 0.3967 | 0.4102 | 0.402 | 0.3089 | 0.2364 | 0.3193 | 0.2056 | 0.2989 | 0.3296 | 0.3206 | 0.346 | 0.5188 | 0.738 | 0.7827 | 0.5801 | 1.0081 | 0.7294 | 0.8534 | 0.6764 | 0.6089
Load_TR6_F6_31_dup | prosumer | 0.1921 | 0.1742 | 0.0792 | 0.2294 | 0.1037 | 0.1976 | 0.1687 | 0.046 | 0.3139 | 0.101 | 0.0798 | 0.2942 | 0.0588 | 0.1953 | 0.171 | 0.046 | 0.3203 | 0.046 | 1.1401 | 1.5248 | 1.8867 | 0.2924 | 0.176 | 0.0657 | 0.3109 | 0.0614 | 0.186 | 0.0511 | 0.3203 | 0.046 | 0.1644 | 0.2019 | 0.0526 | 0.3137 | 0.046 | 0.3203 | 0.0563 | 0.0563 | 0.2504 | 0.4571 | 0.391 | 0.7537 | 0.4145 | 0.5241 | 0.6955 | 0.3302 | 0.2608 | 0.1642
Load_TR6_F6_31_tri | customer | 0.1668 | 0.262 | 0.1882 | 0.2369 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.0897 | 0.0987 | 0.06 | 0.1017 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.1569 | 0.113 | 0.085 | 0.089 | 0.2425 | 0.3796 | 0.5042 | 0.5386 | 0.7329 | 0.3687 | 0.4883 | 0.598 | 0.5548 | 0.623
Load_TR6_F6_32 | prosumer | 0.1439 | 0.049 | 0.1439 | 0.049 | 0.1107 | 0.0822 | 0.049 | 0.1439 | 0.049 | 0.1439 | 0.049 | 0.2936 | 0.1192 | 0.049 | 0.1439 | 0.049 | 0.1268 | 0.5405 | 0.2913 | 0.2557 | 0.049 | 0.1107 | 0.3912 | 0.049 | 0.0822 | 0.1107 | 0.049 | 0.3526 | 0.2566 | 0.2207 | 0.2898 | 0.0875 | 0.0926 | 0.2346 | 1.1075 | 0.3947 | 0.284 | 0.254 | 0.759 | 1.4363 | 2.0407 | 0.527 | 0.4456 | 0.3504 | 0.1202 | 0.049 | 0.1439 | 0.049
Load_TR6_F6_32_dup | customer | 0.1666 | 0.1288 | 0.0505 | 0.1088 | 0.1878 | 0.0648 | 0.1193 | 0.1127 | 0.042 | 0.2107 | 0.1127 | 0.1334 | 0.1547 | 0.1368 | 0.1513 | 0.2694 | 0.3602 | 0.3708 | 0.2654 | 0.2707 | 0.3304 | 0.2588 | 0.2831 | 0.1508 | 1.0043 | 0.1261 | 0.1083 | 0.1334 | 0.1176 | 0.1144 | 0.1334 | 0.1468 | 0.0989 | 0.197 | 0.1514 | 0.1822 | 0.1869 | 0.2954 | 0.4107 | 0.3056 | 0.5218 | 0.7091 | 0.6132 | 0.1366 | 0.1061 | 0.19 | 0.1334 | 0.1127
Load_TR6_F6_32_tri | customer | 0.034 | 0.034 | 0.1509 | 0.0886 | 0.034 | 0.034 | 0.034 | 0.1821 | 0.0574 | 0.0808 | 0.1587 | 0.034 | 0.034 | 0.2055 | 0.034 | 0.1587 | 0.0808 | 0.034 | 0.3454 | 0.034 | 0.1899 | 0.1491 | 0.034 | 0.2559 | 0.3355 | 1.3299 | 0.1867 | 0.2496 | 0.4045 | 0.5296 | 0.3673 | 1.6724 | 1.1713 | 1.7739 | 0.2428 | 1.2952 | 0.9746 | 1.667 | 0.4614 | 0.2603 | 0.434 | 0.3551 | 0.5557 | 0.759 | 0.5009 | 0.3714 | 0.3893 | 0.3371
Load_TR6_F6_33 | customer | 0.038 | 0.1383 | 0.0841 | 0.2611 | 0.038 | 0.207 | 0.1383 | 0.1762 | 0.1475 | 0.0595 | 0.1604 | 0.1849 | 0.038 | 0.1383 | 0.207 | 0.038 | 0.1588 | 0.1864 | 0.038 | 0.0918 | 0.232 | 0.0595 | 0.207 | 0.1869 | 0.2965 | 0.1245 | 0.0672 | 0.1993 | 0.1383 | 0.1609 | 0.0841 | 0.1383 | 0.1916 | 0.1035 | 0.1189 | 0.1762 | 0.2769 | 0.3564 | 0.4375 | 0.5646 | 0.3755 | 0.2458 | 0.038 | 0.0666 | 0.2402 | 0.0764 | 0.1383 | 0.207
Load_TR6_F6_33_dup | customer | 0.4013 | 0.5618 | 0.048 | 0.0819 | 0.1633 | 0.048 | 0.1837 | 0.0616 | 0.143 | 0.1023 | 0.048 | 0.0955 | 0.1498 | 0.048 | 0.2143 | 0.1034 | 0.048 | 0.1997 | 0.0603 | 0.157 | 1.6781 | 0.6352 | 0.6732 | 0.3739 | 0.2995 | 0.2514 | 0.3985 | 0.5018 | 0.281 | 0.3891 | 0.1643 | 0.2894 | 0.2653 | 0.1202 | 0.2274 | 0.0957 | 0.3041 | 0.1746 | 0.1411 | 0.4301 | 0.4215 | 0.7709 | 0.4905 | 0.6684 | 0.3641 | 0.0548 | 0.3028 | 0.3937
Load_TR6_F6_33_tri | prosumer | 0.1783 | 0.1013 | 0.1279 | 0.2246 | 0.0631 | 0.1198 | 0.2448 | 0.1076 | 0.2383 | 0.1142 | 0.0752 | 0.2464 | 0.0858 | 0.0858 | 0.2666 | 0.055 | 0.2269 | 0.4334 | 0.2644 | 0.3032 | 0.3293 | 1.0755 | 0.1671 | 1.1582 | 2.1677 | 1.6464 | 0.2117 | 0.2473 | 0.1005 | 0.3155 | 0.0935 | 0.1013 | 0.239 | 0.0671 | 0.2496 | 0.1028 | 0.055 | 0.1068 | 0.2456 | 0.055 | 0.282 | 0.0704 | 0.141 | 0.2115 | 0.055 | 0.261 | 0.0914 | 0.2201
Load_TR6_F6_34 | customer | 0.1307 | 0.1171 | 0.0762 | 0.1715 | 0.049 | 0.1919 | 0.0558 | 0.0898 | 0.19 | 0.4351 | 0.2298 | 0.049 | 0.049 | 0.1987 | 0.049 | 0.049 | 0.1636 | 0.1706 | 0.2026 | 0.2676 | 0.2345 | 0.049 | 0.1579 | 0.0898 | 0.1171 | 0.1307 | 0.1524 | 0.5447 | 0.2799 | 0.2263 | 0.1511 | 0.1732 | 0.2501 | 0.2631 | 0.1123 | 0.4238 | 0.0982 | 0.2525 | 0.1645 | 0.1585 | 0.1239 | 0.049 | 0.1579 | 0.0898 | 0.9964 | 0.248 | 0.2244 | 0.1179
Load_TR6_F6_34_dup | prosumer | 0.6102 | 0.2305 | 0.1043 | 0.1644 | 0.1703 | 0.091 | 0.2173 | 0.0734 | 0.2701 | 0.0646 | 0.047 | 0.2085 | 0.047 | 0.163 | 0.1718 | 1.0381 | 0.3538 | 1.4624 | 1.3136 | 0.6903 | 0.1363 | 0.3913 | 0.3841 | 2.0925 | 1.0911 | 0.3598 | 0.4115 | 0.4885 | 0.3532 | 0.9276 | 1.2306 | 2.0705 | 0.3475 | 0.5002 | 1.027 | 0.79 | 0.4466 | 0.1864 | 0.4508 | 0.4318 | 2.1679 | 2.4652 | 1.9231 | 1.6923 | 1.179 | 0.3954 | 0.1263 | 0.1791
Load_TR6_F6_34_tri | prosumer | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.0545 | 0.1456 | 0.048 | 0.048 | 0.048 | 0.048 | 0.3358 | 3.0302 | 2.3349 | 0.6703 | 0.0811 | 0.0831 | 0.2456 | 0.048 | 0.048 | 0.1416 | 0.0617 | 0.1522 | 0.1324 | 2.2084 | 0.1524 | 0.1033 | 0.0957 | 0.2856 | 0.096 | 0.2101 | 0.3089 | 0.189 | 0.2424 | 0.2414 | 0.321 | 0.8466 | 0.2895 | 0.048
Load_TR6_F6_35 | customer | 0.1453 | 0.047 | 0.1143 | 0.1831 | 0.0832 | 0.2142 | 0.047 | 0.1025 | 0.1949 | 0.047 | 0.047 | 0.1365 | 0.1609 | 0.047 | 0.1195 | 0.168 | 0.0777 | 0.1402 | 0.1365 | 0.5834 | 0.971 | 0.047 | 0.1557 | 0.1417 | 0.047 | 0.1822 | 0.1765 | 0.1171 | 0.1937 | 0.0905 | 0.206 | 0.1751 | 0.1306 | 0.1275 | 0.1982 | 0.1183 | 0.2697 | 0.3651 | 0.2557 | 0.4082 | 0.5886 | 0.6253 | 0.047 | 0.1195 | 0.0884 | 0.0619 | 0.2355 | 0.047
Load_TR6_F6_35_dup | prosumer | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.6788 | 0.7915 | 0.0591 | 0.049 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.029 | 0.068 | 0.1721 | 1.344 | 0.5086 | 0.5667 | 0.5954 | 0.4701 | 0.3829 | 0.4618 | 0.1848 | 0.029
Load_TR6_F6_35_tri | prosumer | 0.3672 | 0.4471 | 0.1723 | 0.5444 | 0.2312 | 0.3334 | 0.5202 | 0.0756 | 0.048 | 0.048 | 0.1999 | 0.048 | 0.1654 | 0.0825 | 0.124 | 0.124 | 0.048 | 0.0825 | 0.1654 | 0.048 | 0.048 | 0.048 | 0.1999 | 0.048 | 0.1447 | 0.1032 | 0.048 | 0.0894 | 0.1585 | 0.048 | 0.048 | 0.1999 | 0.048 | 0.1861 | 0.0618 | 0.0588 | 0.048 | 0.4602 | 0.2001 | 0.2054 | 0.2773 | 0.1962 | 0.3691 | 0.3675 | 0.4489 | 0.4394 | 0.44 | 0.2532
Load_TR6_F6_36 | customer | 0.4308 | 0.4371 | 0.039 | 0.1419 | 0.1943 | 0.039 | 0.1046 | 0.2317 | 0.039 | 0.1943 | 0.1419 | 0.039 | 0.2458 | 0.0905 | 0.159 | 0.1772 | 0.0703 | 0.1872 | 0.1434 | 0.329 | 0.2249 | 0.249 | 0.1875 | 0.5527 | 0.1875 | 0.5383 | 0.2537 | 0.0602 | 0.2761 | 0.039 | 0.2037 | 0.1325 | 0.039 | 0.269 | 0.0672 | 0.2844 | 0.4433 | 1.1485 | 0.3935 | 0.2695 | 0.039 | 0.1419 | 0.1943 | 0.0831 | 0.119 | 0.1731 | 0.1419 | 0.1449
Load_TR6_F6_36_dup | prosumer | 0.0624 | 0.1919 | 0.038 | 0.1535 | 0.1008 | 0.038 | 0.1605 | 0.0938 | 0.137 | 0.0545 | 0.1008 | 0.1535 | 0.038 | 0.038 | 0.1535 | 0.1008 | 0.038 | 0.2163 | 0.038 | 0.0875 | 0.1354 | 0.0694 | 0.1535 | 0.038 | 0.0957 | 0.1586 | 0.038 | 0.1627 | 0.0916 | 0.0624 | 0.1506 | 0.0792 | 0.0694 | 0.0942 | 0.1706 | 0.3917 | 0.305 | 0.2763 | 0.2692 | 0.5359 | 0.522 | 0.3078 | 0.5569 | 0.6149 | 0.5928 | 0.5449 | 0.038 | 0.1535
Load_TR6_F6_36_tri | customer | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.0603 | 0.0537 | 0.047 | 0.047 | 0.047 | 0.047 | 0.055 | 0.082 | 0.0597 | 0.0645 | 0.047 | 0.0613 | 0.0677 | 0.047 | 0.047 | 0.0985 | 0.2154 | 0.2514 | 0.2527 | 0.2114 | 0.286 | 0.2886 | 0.2926 | 0.2628 | 0.4008 | 0.3885 | 0.2086 | 0.2614 | 0.4006 | 0.3035 | 0.1654 | 0.1822 | 0.3468
Load_TR6_F6_37 | customer | 0.048 | 0.048 | 0.2118 | 0.4566 | 0.9364 | 1.0645 | 1.7299 | 0.1862 | 0.048 | 0.1548 | 0.0794 | 0.048 | 0.136 | 0.0983 | 0.2416 | 0.084 | 0.0731 | 0.1611 | 0.048 | 0.2162 | 0.1139 | 1.0339 | 0.8547 | 1.4406 | 0.048 | 0.201 | 0.135 | 0.1619 | 0.4682 | 0.048 | 0.1485 | 0.0857 | 0.048 | 0.0794 | 0.1548 | 0.048 | 0.048 | 0.1862 | 0.048 | 1.1748 | 0.6749 | 0.7596 | 0.7576 | 0.4672 | 0.6206 | 1.66 | 0.6798 | 0.7638
Load_TR6_F6_37_dup | prosumer | 0.1595 | 0.2497 | 0.2079 | 0.057 | 0.2901 | 0.1595 | 0.2097 | 0.2163 | 0.1085 | 0.246 | 0.1996 | 0.1048 | 0.3569 | 0.1006 | 0.1216 | 1.0345 | 0.1286 | 0.217 | 0.2686 | 0.1488 | 0.4382 | 0.2634 | 2.2583 | 2.7794 | 1.2672 | 0.386 | 0.0501 | 0.1581 | 0.9243 | 2.6117 | 2.6988 | 0.4519 | 0.1048 | 0.2321 | 0.2255 | 0.1123 | 0.3453 | 0.049 | 0.2473 | 0.2103 | 0.049 | 0.2737 | 0.1838 | 0.0893 | 0.3683 | 0.049 | 0.1167 | 0.2304
Load_TR6_F6_37_tri | customer | 0.1197 | 0.032 | 0.0633 | 0.1385 | 0.032 | 0.032 | 0.0445 | 0.1573 | 0.032 | 0.032 | 0.1699 | 0.032 | 0.032 | 0.032 | 0.0445 | 0.1573 | 0.032 | 0.1009 | 0.1009 | 0.0508 | 0.2299 | 0.2704 | 0.2898 | 0.032 | 0.1936 | 0.526 | 0.3722 | 0.6069 | 0.4623 | 0.032 | 0.4372 | 0.4295 | 0.1033 | 0.2081 | 0.116 | 0.0997 | 0.4905 | 0.6653 | 0.4558 | 0.5949 | 0.5236 | 0.4225 | 0.5126 | 0.6503 | 0.2417 | 0.0869 | 0.371 | 0.1893
Load_TR6_F6_38 | customer | 0.4553 | 0.4774 | 0.2234 | 0.047 | 0.1091 | 0.1557 | 0.047 | 0.2178 | 0.047 | 0.047 | 0.1402 | 0.1246 | 0.047 | 0.2178 | 2.693 | 1.2884 | 0.394 | 0.0578 | 0.3344 | 0.1189 | 0.047 | 0.2448 | 0.2334 | 0.2023 | 0.2515 | 0.0664 | 1.0696 | 0.152 | 0.3592 | 0.1783 | 0.2771 | 0.0482 | 0.1517 | 0.1169 | 0.047 | 0.4042 | 0.0554 | 0.1904 | 0.1678 | 0.407 | 0.583 | 0.4514 | 0.2676 | 0.6207 | 0.3741 | 0.3131 | 0.1324 | 0.047
Load_TR6_F6_38_dup | prosumer | 0.9014 | 0.7945 | 0.9296 | 0.1301 | 0.055 | 0.055 | 0.055 | 0.1218 | 0.0633 | 0.1301 | 0.055 | 0.1301 | 0.055 | 0.055 | 0.4493 | 0.4483 | 0.3111 | 0.055 | 0.2905 | 0.2018 | 0.2015 | 0.2622 | 0.1612 | 0.5386 | 0.0631 | 0.3346 | 0.3323 | 0.1672 | 0.3614 | 0.0882 | 0.354 | 0.5765 | 0.4733 | 0.1605 | 0.1663 | 0.2837 | 0.055 | 0.1231 | 0.5016 | 0.8204 | 0.5678 | 0.4829 | 0.5369 | 0.8599 | 1.1469 | 0.674 | 1.0018 | 0.0633
Load_TR6_F6_38_tri | prosumer | 0.3134 | 0.05 | 0.2725 | 0.1309 | 0.1894 | 0.1359 | 0.22 | 0.1794 | 0.2268 | 0.05 | 0.3706 | 0.0644 | 0.0553 | 0.15 | 0.1219 | 0.2415 | 0.2676 | 0.2622 | 0.2 | 0.3055 | 0.4298 | 0.369 | 0.4626 | 0.2765 | 0.2927 | 0.301 | 0.1788 | 0.1003 | 0.2294 | 0.1151 | 0.2563 | 0.4148 | 0.2093 | 0.4234 | 0.2627 | 0.2981 | 0.5093 | 0.1801 | 0.2768 | 0.252 | 0.2227 | 0.5597 | 0.5161 | 0.3508 | 0.9864 | 0.4205 | 0.3797 | 0.0553
Load_TR6_F6_39 | customer | 0.7568 | 1.748 | 0.258 | 0.5238 | 0.3018 | 0.1552 | 0.057 | 0.029 | 0.1762 | 0.036 | 0.0851 | 0.1271 | 0.029 | 0.1832 | 0.029 | 0.057 | 0.1552 | 0.029 | 0.029 | 0.0781 | 0.1341 | 0.029 | 0.3409 | 0.3054 | 0.036 | 0.1762 | 0.029 | 0.1622 | 0.3019 | 0.2559 | 0.1876 | 0.3119 | 0.3953 | 0.243 | 0.1834 | 0.1135 | 0.7542 | 0.59 | 0.438 | 1.3968 | 0.6303 | 0.2946 | 0.2843 | 0.3594 | 0.3061 | 0.386 | 0.2768 | 0.0903
Load_TR6_F6_39_dup | customer | 0.1778 | 0.052 | 0.2058 | 0.052 | 0.1079 | 0.1498 | 0.052 | 0.052 | 0.1219 | 0.1359 | 0.052 | 0.052 | 0.2058 | 1.4303 | 0.7616 | 0.6417 | 0.436 | 0.3975 | 0.2519 | 0.3696 | 1.4947 | 0.2189 | 0.7004 | 1.881 | 0.08 | 0.3658 | 0.0587 | 0.5445 | 0.1108 | 0.3904 | 1.3999 | 0.7871 | 0.5632 | 0.443 | 0.6877 | 0.4301 | 0.6399 | 3.0957 | 3.697 | 1.0454 | 0.4731 | 0.5048 | 1.6946 | 0.8826 | 0.8744 | 0.1702 | 0.052 | 0.2058
Load_TR6_F6_39_tri | customer | 0.1674 | 0.0675 | 0.055 | 0.055 | 0.1799 | 0.055 | 0.1736 | 0.0612 | 0.055 | 0.055 | 0.1174 | 0.1174 | 0.055 | 0.055 | 0.1487 | 0.0862 | 0.2335 | 0.2545 | 0.6628 | 0.0561 | 0.3683 | 0.0869 | 0.1078 | 0.1424 | 0.0675 | 0.1674 | 0.1703 | 0.8358 | 1.3942 | 0.6943 | 1.0668 | 2.7365 | 2.6477 | 0.1695 | 0.055 | 0.055 | 0.1362 | 0.0987 | 0.055 | 0.1799 | 0.5365 | 0.4596 | 0.4438 | 0.5542 | 1.4945 | 1.2286 | 0.5084 | 0.1529
Load_TR6_F6_3_dup | customer | 0.2349 | 0.2027 | 0.0997 | 0.2026 | 0.2707 | 0.2481 | 0.0621 | 0.3275 | 0.1652 | 0.2447 | 0.1549 | 0.2182 | 0.1106 | 0.1517 | 0.286 | 0.1171 | 0.9321 | 0.6561 | 0.3224 | 0.1856 | 0.2775 | 0.2257 | 0.1262 | 0.371 | 0.0675 | 0.1504 | 0.336 | 0.1594 | 0.1549 | 0.1536 | 0.1106 | 0.2385 | 0.25 | 0.4256 | 0.1118 | 0.3442 | 0.1539 | 0.2388 | 0.3488 | 0.7848 | 0.9173 | 0.635 | 0.8784 | 0.6322 | 0.693 | 0.8428 | 0.7015 | 0.6851
Load_TR6_F6_3_tri | prosumer | 0.05 | 0.1306 | 0.05 | 0.05 | 0.05 | 0.1306 | 0.05 | 0.0679 | 0.1127 | 0.05 | 0.1306 | 0.05 | 0.1306 | 0.05 | 0.1261 | 0.0545 | 0.1037 | 0.0769 | 0.2938 | 0.1427 | 0.05 | 0.1306 | 0.05 | 0.1306 | 0.05 | 0.05 | 0.1261 | 0.2777 | 0.1306 | 0.05 | 0.1192 | 0.1124 | 0.3021 | 0.2299 | 0.4779 | 0.8079 | 0.1913 | 0.8334 | 0.3842 | 1.5918 | 0.2414 | 2.0483 | 1.4865 | 0.6139 | 0.3339 | 0.6353 | 0.9645 | 0.059
Load_TR6_F6_4 | prosumer | 0.038 | 0.038 | 0.1386 | 0.038 | 0.038 | 0.1386 | 0.038 | 0.038 | 0.1386 | 0.038 | 0.038 | 0.1386 | 0.038 | 0.038 | 0.1386 | 0.038 | 0.6554 | 1.4762 | 0.1072 | 0.4771 | 2.537 | 2.6376 | 0.4545 | 0.038 | 0.038 | 0.1386 | 0.038 | 0.1027 | 0.0739 | 0.038 | 0.1386 | 0.038 | 0.0667 | 0.1099 | 0.038 | 0.1386 | 0.038 | 0.0935 | 0.2545 | 0.4516 | 0.4324 | 0.5383 | 0.3471 | 0.7073 | 0.1314 | 0.038 | 0.1386 | 0.038
Load_TR6_F6_40 | customer | 0.116 | 0.1435 | 0.054 | 0.1573 | 0.1022 | 0.054 | 0.054 | 0.116 | 0.1435 | 0.054 | 0.0747 | 0.1848 | 0.054 | 0.1917 | 0.0678 | 0.054 | 0.054 | 0.1435 | 2.0585 | 0.6477 | 0.101 | 0.2546 | 0.188 | 0.3354 | 0.413 | 0.054 | 0.1642 | 0.0953 | 0.054 | 0.2055 | 0.054 | 0.054 | 0.216 | 0.1039 | 0.3041 | 0.054 | 0.1229 | 0.4397 | 0.3222 | 0.5606 | 0.4578 | 1.3998 | 0.4976 | 0.3628 | 0.5337 | 0.284 | 0.4844 | 0.1515
Load_TR6_F6_40_dup | prosumer | 0.1295 | 0.0823 | 0.1106 | 0.1012 | 0.0917 | 0.054 | 0.087 | 0.1059 | 0.054 | 0.054 | 0.054 | 0.0634 | 0.1295 | 0.054 | 0.1698 | 2.0509 | 1.8305 | 1.1694 | 0.4114 | 1.3354 | 0.054 | 0.054 | 0.054 | 0.1579 | 0.054 | 0.1389 | 0.054 | 0.1389 | 0.054 | 0.1648 | 0.376 | 0.1453 | 0.0864 | 0.4269 | 0.4964 | 0.0666 | 0.2591 | 0.2307 | 0.2955 | 0.054 | 0.054 | 0.054 | 0.3601 | 0.4062 | 0.4366 | 0.445 | 0.2895 | 0.1248
Load_TR6_F6_40_tri | customer | 0.048 | 0.1005 | 0.3037 | 0.0769 | 0.1203 | 0.269 | 0.1062 | 0.2394 | 0.1792 | 0.048 | 0.2621 | 0.3604 | 0.2161 | 1.5606 | 0.2934 | 1.4221 | 0.5454 | 0.3273 | 0.5762 | 0.5385 | 0.2503 | 0.3974 | 0.0572 | 0.048 | 0.3147 | 0.5124 | 0.048 | 0.2838 | 0.1493 | 0.048 | 0.3634 | 0.0697 | 0.048 | 0.1615 | 0.3194 | 0.0943 | 1.3534 | 0.2009 | 0.3023 | 0.5735 | 0.2367 | 0.4093 | 0.5228 | 1.2307 | 0.6806 | 0.7499 | 0.5675 | 0.5005
Load_TR6_F6_41 | customer | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.1063 | 0.1116 | 0.1449 | 1.0046 | 0.1016 | 0.0924 | 0.0736 | 0.049 | 0.0716 | 0.1202 | 0.1803 | 0.1701 | 0.9349 | 0.2773 | 0.4947 | 0.133 | 0.049 | 0.5026 | 1.3947 | 0.4174 | 0.1025 | 0.4385 | 0.2115 | 0.3798 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.3964 | 0.1651
Load_TR6_F6_41_dup | customer | 0.384 | 0.054 | 0.3461 | 0.0739 | 0.3415 | 0.1144 | 0.3091 | 0.1827 | 0.1592 | 0.1598 | 0.2388 | 0.1618 | 0.2782 | 0.1879 | 0.26 | 0.1622 | 0.1635 | 0.2891 | 0.3101 | 0.3613 | 0.447 | 2.2095 | 2.5968 | 1.951 | 0.209 | 0.2639 | 0.2398 | 1.1335 | 0.6056 | 0.3996 | 0.246 | 0.1427 | 0.1418 | 0.7082 | 0.706 | 0.7192 | 0.8493 | 0.4953 | 0.7129 | 0.3661 | 0.2241 | 0.1353 | 0.2887 | 0.0849 | 0.2096 | 0.054 | 0.4059 | 0.066
Load_TR6_F6_41_tri | customer | 0.054 | 0.2155 | 0.0583 | 0.054 | 0.1315 | 0.1423 | 0.054 | 0.054 | 0.1423 | 0.1185 | 0.0985 | 0.1323 | 0.1099 | 0.054 | 0.1423 | 0.054 | 0.1315 | 0.1942 | 1.6659 | 1.4541 | 1.1433 | 0.1974 | 0.2347 | 0.6195 | 0.5548 | 0.7274 | 0.4009 | 0.1089 | 0.1653 | 0.1021 | 0.302 | 0.7193 | 0.1569 | 0.144 | 0.2498 | 0.054 | 0.2855 | 0.054 | 0.1423 | 0.1315 | 0.0729 | 0.2008 | 0.0583 | 0.3604 | 0.4995 | 0.436 | 0.5956 | 0.7427
Load_TR6_F6_42 | prosumer | 0.1166 | 0.0852 | 0.0544 | 0.2229 | 0.067 | 0.1005 | 0.046 | 0.1558 | 0.1214 | 0.046 | 0.1558 | 0.046 | 0.2312 | 0.046 | 0.1763 | 0.1009 | 0.046 | 0.1214 | 0.046 | 0.2312 | 0.0604 | 0.1989 | 0.0623 | 0.124 | 0.1558 | 0.046 | 0.046 | 0.2312 | 1.849 | 0.191 | 0.4265 | 0.1383 | 0.2033 | 0.1474 | 0.4352 | 0.1387 | 0.1366 | 0.0931 | 0.0921 | 0.1851 | 0.1005 | 0.1781 | 0.1206 | 0.2679 | 0.4704 | 0.107 | 0.1692 | 0.601
Load_TR6_F6_42_dup | customer | 0.5774 | 0.4897 | 0.2732 | 0.0848 | 0.2881 | 0.1433 | 0.1995 | 0.2392 | 0.042 | 0.2687 | 0.17 | 0.042 | 0.1823 | 0.2564 | 0.2729 | 0.2576 | 0.3535 | 0.489 | 0.0572 | 0.2406 | 0.3179 | 0.4507 | 0.4016 | 1.0075 | 3.0598 | 1.9052 | 0.4365 | 0.335 | 0.1935 | 0.3789 | 0.1551 | 0.302 | 0.3234 | 1.2339 | 1.1878 | 1.8042 | 0.3548 | 0.5796 | 0.5944 | 0.7312 | 0.9048 | 1.0234 | 0.6867 | 0.6497 | 0.1805 | 0.1955 | 0.2362 | 0.413
Load_TR6_F6_42_tri | prosumer | 0.5937 | 0.5725 | 0.5629 | 0.058 | 0.2905 | 0.13 | 0.1013 | 0.3193 | 0.058 | 0.21 | 0.2105 | 0.146 | 0.1781 | 0.1544 | 0.058 | 0.3626 | 1.9124 | 0.3362 | 0.2499 | 0.295 | 0.066 | 0.3546 | 0.058 | 0.135 | 0.2856 | 0.058 | 0.3417 | 0.1236 | 0.2912 | 0.3686 | 0.1963 | 0.4052 | 0.2604 | 0.3942 | 0.2771 | 0.2002 | 0.138 | 0.6411 | 1.6412 | 0.4917 | 0.5626 | 0.6514 | 0.4957 | 0.17 | 0.058 | 0.2726 | 0.148 | 0.058
Load_TR6_F6_43 | customer | 0.045 | 0.1388 | 0.045 | 0.1388 | 0.045 | 0.1388 | 0.045 | 0.045 | 0.1388 | 0.045 | 0.1388 | 0.045 | 0.1013 | 0.0825 | 0.045 | 0.0563 | 0.1013 | 0.2916 | 2.0625 | 0.8015 | 1.0392 | 0.5931 | 0.1832 | 1.1805 | 0.4183 | 0.1354 | 0.202 | 0.0892 | 0.0988 | 0.1668 | 0.0591 | 0.1247 | 0.045 | 0.0825 | 0.1013 | 0.1005 | 0.1478 | 0.0753 | 0.2416 | 0.2031 | 0.3022 | 0.3942 | 0.5067 | 0.4655 | 0.4839 | 0.5486 | 0.4088 | 1.1005
Load_TR6_F6_43_dup | prosumer | 0.211 | 0.046 | 0.3164 | 0.0894 | 0.0894 | 0.3041 | 0.0583 | 0.1415 | 0.1415 | 0.046 | 0.1564 | 0.2493 | 0.046 | 0.2493 | 0.1564 | 0.1502 | 0.2003 | 0.1167 | 0.2446 | 0.2148 | 1.1337 | 0.9164 | 0.2137 | 1.0145 | 1.3613 | 0.4072 | 0.3297 | 0.5557 | 0.1819 | 0.1962 | 0.3147 | 1.2989 | 0.4413 | 0.24 | 0.4094 | 0.2716 | 1.4863 | 0.4278 | 0.0828 | 0.046 | 0.2371 | 0.0644 | 0.2024 | 0.2034 | 0.1503 | 0.0721 | 0.3337 | 0.046
Load_TR6_F6_43_tri | customer | 0.1157 | 0.053 | 0.053 | 0.1336 | 0.053 | 0.1023 | 0.0843 | 0.053 | 0.053 | 0.1202 | 0.0664 | 0.1291 | 0.0575 | 0.1247 | 0.062 | 0.1336 | 0.1672 | 0.1479 | 0.0936 | 0.1381 | 0.0897 | 0.907 | 0.1905 | 0.1347 | 0.0575 | 0.2927 | 0.053 | 0.3139 | 0.053 | 0.1336 | 0.053 | 0.1336 | 0.053 | 0.0754 | 0.1112 | 0.053 | 0.1336 | 0.053 | 0.0799 | 0.1771 | 0.437 | 0.4265 | 0.8826 | 1.131 | 0.298 | 0.2241 | 0.053 | 0.0799
Load_TR6_F6_44 | prosumer | 0.145 | 0.1983 | 0.171 | 0.3482 | 0.1543 | 0.1841 | 0.2348 | 0.171 | 0.212 | 0.1902 | 0.283 | 0.0599 | 0.3518 | 0.1674 | 0.269 | 2.7175 | 0.4602 | 0.3566 | 0.1354 | 0.307 | 0.244 | 0.1013 | 0.3665 | 0.1818 | 0.3585 | 1.3912 | 0.086 | 1.1253 | 1.1774 | 1.6846 | 0.473 | 0.3574 | 2.3893 | 0.1671 | 0.6025 | 1.4326 | 1.136 | 1.2193 | 2.2385 | 0.5609 | 0.4093 | 0.7159 | 0.8341 | 0.8049 | 1.0649 | 0.9336 | 0.224 | 0.2953
Load_TR6_F6_44_dup | prosumer | 0.156 | 0.2934 | 0.1212 | 0.2222 | 0.0828 | 0.2867 | 0.1672 | 0.2298 | 0.2206 | 0.1212 | 0.2622 | 0.1452 | 0.0582 | 0.1329 | 0.2817 | 0.2319 | 0.0727 | 0.3443 | 0.097 | 0.1524 | 0.3199 | 0.1493 | 0.0945 | 0.0672 | 0.3549 | 0.0919 | 0.2217 | 0.1906 | 0.1017 | 1.5333 | 0.9708 | 1.6557 | 0.326 | 0.1343 | 0.4083 | 0.3734 | 0.3257 | 0.2777 | 0.6969 | 0.3692 | 0.3002 | 0.5996 | 0.2333 | 0.0919 | 0.1379 | 0.1705 | 0.2056 | 0.1928
Load_TR6_F6_44_tri | customer | 0.053 | 0.0612 | 0.1186 | 0.0612 | 0.1186 | 0.053 | 0.0858 | 0.094 | 0.053 | 0.1268 | 0.053 | 0.1268 | 0.053 | 0.1268 | 0.053 | 0.1104 | 0.6195 | 0.7395 | 0.3155 | 0.2845 | 0.0858 | 0.0694 | 0.1104 | 0.053 | 0.053 | 0.1268 | 0.1023 | 0.2133 | 1.4197 | 2.4125 | 0.2908 | 1.316 | 0.053 | 0.1442 | 0.3457 | 0.6691 | 0.1072 | 0.0806 | 0.1199 | 0.4366 | 0.5327 | 0.8407 | 0.4541 | 0.3889 | 0.3958 | 0.4617 | 0.053 | 0.053
Load_TR6_F6_45 | customer | 0.056 | 0.2407 | 0.056 | 0.1315 | 0.1651 | 0.056 | 0.1567 | 0.1399 | 0.056 | 0.2155 | 0.0812 | 0.056 | 0.2854 | 0.1837 | 0.2922 | 0.056 | 0.4031 | 0.4872 | 0.2993 | 0.191 | 0.6644 | 0.523 | 0.4831 | 0.8183 | 0.4127 | 0.4051 | 0.1674 | 0.5903 | 1.1843 | 0.6869 | 0.3927 | 0.2435 | 0.2455 | 0.662 | 0.5541 | 0.3378 | 0.3336 | 0.2648 | 2.6447 | 1.4062 | 0.4996 | 0.6059 | 2.2033 | 0.6148 | 0.7053 | 0.8135 | 0.5569 | 0.056
Load_TR6_F6_45_dup | customer | 0.052 | 0.1135 | 0.1182 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.1086 | 0.1873 | 0.1898 | 1.5669 | 2.6428 | 1.2797 | 0.2398 | 1.8927 | 3.3393 | 1.3787 | 0.2202 | 0.085 | 0.0674 | 0.0599 | 0.1266 | 0.142 | 0.0931 | 0.1347 | 0.1783 | 0.2047 | 0.2487 | 0.3186 | 0.1056 | 0.1147 | 0.3431 | 0.4766 | 0.3741 | 0.5872 | 0.8089 | 0.5527 | 0.4066 | 0.411 | 0.3946
Load_TR6_F6_45_tri | prosumer | 0.3544 | 0.295 | 0.2138 | 0.047 | 0.1241 | 0.1855 | 0.0787 | 0.0969 | 0.1018 | 0.2077 | 0.047 | 0.2016 | 0.1079 | 0.047 | 0.2534 | 0.0561 | 0.0602 | 0.3511 | 0.1479 | 0.2361 | 0.122 | 0.3176 | 0.3743 | 0.1761 | 0.1949 | 0.1341 | 0.2958 | 0.047 | 0.1555 | 0.3173 | 0.1118 | 0.0882 | 0.2499 | 0.2107 | 0.2014 | 0.4992 | 0.2862 | 0.3392 | 0.6267 | 0.3878 | 0.4121 | 0.5355 | 0.5621 | 0.4247 | 0.6046 | 0.5129 | 0.1286 | 0.047
Load_TR6_F6_46 | prosumer | 0.7056 | 0.1358 | 0.1486 | 0.1865 | 0.174 | 0.047 | 0.1801 | 0.1232 | 0.1929 | 0.1295 | 0.1422 | 0.1928 | 0.1676 | 0.047 | 0.085 | 0.288 | 0.2227 | 0.2119 | 0.1612 | 0.1422 | 0.2182 | 0.047 | 0.1041 | 0.2909 | 0.2622 | 0.5041 | 0.047 | 0.0641 | 0.4977 | 0.7051 | 0.2709 | 0.0955 | 0.3135 | 0.047 | 0.0724 | 0.2183 | 0.1167 | 0.0914 | 0.2437 | 0.0724 | 0.174 | 0.1865 | 0.174 | 0.1294 | 0.1358 | 0.1422 | 0.1421 | 0.2184
Load_TR6_F6_46_dup | customer | 0.0629 | 0.1583 | 0.1881 | 0.0824 | 0.264 | 0.0629 | 0.1588 | 0.136 | 0.2456 | 0.3331 | 0.2634 | 0.2617 | 0.1876 | 0.2025 | 0.0708 | 0.096 | 0.1988 | 0.1145 | 0.1241 | 0.1707 | 0.1145 | 1.2369 | 0.5034 | 0.1153 | 0.2113 | 0.2006 | 0.9709 | 0.8789 | 0.3988 | 0.2497 | 0.2121 | 0.3354 | 0.1515 | 0.2108 | 0.0576 | 0.1351 | 0.153 | 0.136 | 0.1868 | 0.1881 | 0.5016 | 0.4003 | 0.7206 | 0.8284 | 0.1577 | 0.158 | 0.1588 | 0.1373
Load_TR6_F6_46_tri | customer | 0.1351 | 0.1324 | 0.0536 | 0.088 | 0.0721 | 0.1869 | 0.0406 | 0.1709 | 0.0967 | 0.032 | 0.0893 | 0.1395 | 0.0708 | 0.032 | 0.184 | 0.0949 | 0.2233 | 0.3517 | 0.2105 | 0.2081 | 0.0701 | 0.2112 | 2.8267 | 0.241 | 1.5182 | 0.6308 | 0.1719 | 0.118 | 0.1387 | 0.2428 | 0.4549 | 0.1255 | 0.1109 | 0.5096 | 0.2711 | 0.2615 | 0.1635 | 0.2052 | 0.1303 | 0.2463 | 0.403 | 0.7206 | 1.4928 | 0.4927 | 0.3013 | 0.0851 | 0.0794 | 0.1365
Load_TR6_F6_47 | prosumer | 0.05 | 0.2224 | 0.05 | 0.1597 | 0.1127 | 0.0735 | 0.1989 | 0.05 | 0.05 | 0.191 | 0.0813 | 0.0578 | 0.2145 | 0.05 | 0.1205 | 0.1518 | 0.05 | 0.2224 | 0.05 | 0.1518 | 0.1205 | 0.3633 | 1.8014 | 0.0657 | 0.1283 | 0.144 | 0.05 | 0.0549 | 0.4977 | 1.0113 | 0.2696 | 0.1124 | 0.1046 | 0.2491 | 0.4523 | 0.7791 | 0.2391 | 0.2838 | 0.2563 | 0.4673 | 0.6659 | 0.8524 | 0.5596 | 0.4882 | 0.473 | 0.0735 | 0.1989 | 0.05
Load_TR6_F6_47_dup | customer | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.0651 | 0.067 | 0.067 | 0.2747 | 0.067 | 0.1645 | 0.067 | 0.067 | 1.0833 | 0.7592 | 1.3499 | 0.0532 | 0.049 | 0.0643 | 0.0836 | 0.3725 | 0.254 | 0.3183 | 0.049 | 0.049 | 0.049 | 0.202 | 0.2448 | 0.5062 | 1.9547 | 0.2224 | 0.326 | 1.5915 | 1.3369 | 0.9718 | 0.3877 | 0.4636 | 0.576 | 0.4538 | 0.1738 | 0.3233 | 0.049
Load_TR6_F6_47_tri | customer | 1.0471 | 0.5736 | 0.9302 | 0.0783 | 0.1046 | 0.1889 | 0.052 | 0.2243 | 0.0955 | 0.052 | 0.1683 | 0.1515 | 0.052 | 0.1453 | 0.1701 | 0.0564 | 0.1889 | 0.157 | 0.1092 | 0.2151 | 0.7098 | 0.6339 | 0.2616 | 0.0564 | 0.1702 | 0.0707 | 0.1932 | 0.1267 | 0.1284 | 0.2074 | 0.1408 | 0.2785 | 0.2671 | 0.1981 | 0.2468 | 0.1377 | 1.0737 | 1.4547 | 0.086 | 0.4534 | 0.5414 | 0.5363 | 0.7395 | 1.513 | 2.0652 | 0.9141 | 1.2317 | 0.7
Load_TR6_F6_48 | prosumer | 1.0705 | 1.043 | 0.0584 | 0.2291 | 0.1171 | 0.1414 | 0.2112 | 0.052 | 0.2716 | 0.0809 | 0.052 | 0.3006 | 0.052 | 0.2027 | 0.386 | 0.052 | 0.2044 | 1.1387 | 0.088 | 1.2314 | 1.2423 | 0.3924 | 0.3257 | 1.3252 | 0.5289 | 0.3799 | 0.1959 | 0.1853 | 0.3583 | 0.0839 | 0.2832 | 0.261 | 0.2211 | 0.3305 | 0.668 | 1.3922 | 0.6655 | 1.4904 | 0.5037 | 0.0584 | 1.4034 | 0.617 | 1.2445 | 0.6336 | 1.0957 | 0.7882 | 0.811 | 0.2282
Load_TR6_F6_48_dup | prosumer | 0.1516 | 0.4037 | 0.647 | 0.6764 | 0.5587 | 0.055 | 0.0614 | 0.1902 | 0.055 | 0.1967 | 0.055 | 0.1001 | 0.1516 | 0.055 | 0.1967 | 0.055 | 0.1967 | 0.2325 | 0.2009 | 0.31 | 0.4421 | 0.4893 | 0.2761 | 0.6445 | 3.9178 | 2.9216 | 0.6122 | 0.1461 | 2.024 | 0.2306 | 0.2635 | 0.2568 | 0.2774 | 0.1136 | 1.5768 | 0.9287 | 0.1847 | 0.3144 | 0.1821 | 0.3357 | 0.6648 | 0.6004 | 0.5574 | 0.7187 | 0.8912 | 0.8731 | 0.8478 | 0.055
Load_TR6_F6_48_tri | customer | 0.5703 | 0.7125 | 0.0927 | 0.171 | 0.1423 | 0.048 | 0.2653 | 0.048 | 0.2076 | 0.1057 | 0.048 | 0.1368 | 0.1095 | 0.0753 | 0.2231 | 0.0629 | 0.2225 | 0.0908 | 0.048 | 0.2653 | 0.048 | 0.1648 | 0.1486 | 0.0902 | 0.2729 | 0.2268 | 0.1461 | 0.1523 | 0.0927 | 0.2743 | 0.2639 | 0.3577 | 2.5429 | 0.2717 | 0.4078 | 0.1904 | 0.3325 | 0.2265 | 0.1902 | 0.1232 | 0.115 | 0.1983 | 0.1515 | 0.3036 | 0.6972 | 0.5686 | 0.5099 | 0.0753
Load_TR6_F6_49 | customer | 0.1002 | 0.1218 | 0.1161 | 0.1604 | 0.057 | 0.0786 | 0.2763 | 0.0865 | 0.0939 | 0.1825 | 0.057 | 0.165 | 0.1308 | 0.2104 | 0.1002 | 0.2194 | 0.1056 | 0.1164 | 0.2302 | 0.1542 | 0.1308 | 0.1456 | 0.165 | 0.2194 | 0.057 | 0.165 | 0.1235 | 0.153 | 0.165 | 0.1308 | 0.1456 | 0.165 | 0.2121 | 0.0644 | 0.1678 | 0.1951 | 0.0786 | 0.2194 | 0.057 | 0.1678 | 0.2177 | 0.3824 | 0.6582 | 0.4316 | 0.4859 | 0.2616 | 0.0624 | 0.322
Load_TR6_F6_49_dup | prosumer | 1.0279 | 1.1744 | 0.057 | 0.2101 | 0.0812 | 0.057 | 0.2343 | 0.057 | 0.1376 | 0.1537 | 0.057 | 0.2343 | 0.057 | 0.0628 | 0.3006 | 0.1264 | 0.7451 | 0.5513 | 0.2545 | 0.2612 | 0.5135 | 0.4785 | 0.2163 | 0.1779 | 0.1134 | 0.0731 | 0.2181 | 0.057 | 0.2343 | 0.3831 | 1.5327 | 0.3639 | 0.4432 | 0.4964 | 0.3003 | 0.1113 | 0.1315 | 0.6857 | 0.3886 | 0.4098 | 2.0248 | 0.9014 | 0.9683 | 0.8729 | 0.6088 | 0.886 | 0.6484 | 0.7532
Load_TR6_F6_49_tri | prosumer | 0.2728 | 0.049 | 0.2973 | 0.0988 | 0.049 | 0.2226 | 0.0573 | 0.1901 | 0.2061 | 0.1653 | 0.2309 | 0.049 | 0.2397 | 0.1565 | 0.1818 | 0.2143 | 0.2696 | 0.4273 | 0.2109 | 0.1071 | 0.3369 | 0.049 | 0.1813 | 0.2149 | 0.049 | 0.0821 | 0.3058 | 0.1052 | 0.1151 | 0.281 | 0.049 | 0.2309 | 0.1653 | 0.049 | 0.289 | 0.1071 | 0.0986 | 0.2976 | 0.049 | 0.1071 | 0.3892 | 0.5159 | 0.4539 | 0.4355 | 0.9275 | 0.8141 | 0.6107 | 0.8299
Load_TR6_F6_4_dup | prosumer | 0.0904 | 0.049 | 0.2208 | 0.1543 | 0.0941 | 0.2811 | 0.049 | 0.2916 | 0.0835 | 0.2295 | 0.1457 | 0.1742 | 0.1112 | 0.239 | 0.074 | 0.2842 | 0.2489 | 0.5082 | 0.7708 | 0.3435 | 0.4274 | 0.5377 | 0.4763 | 0.6389 | 2.1476 | 0.4241 | 0.1112 | 0.5263 | 0.1082 | 0.357 | 0.3483 | 0.5786 | 0.4813 | 1.4766 | 0.9882 | 0.429 | 0.074 | 0.364 | 0.404 | 0.1304 | 0.1964 | 0.0974 | 0.5677 | 0.7376 | 0.9333 | 0.3525 | 0.4857 | 0.5694
Load_TR6_F6_4_tri | customer | 0.4092 | 0.3567 | 0.0664 | 0.1901 | 0.1344 | 0.1301 | 0.1944 | 0.04 | 0.2845 | 0.04 | 0.04 | 0.055 | 0.1901 | 0.0929 | 0.0815 | 0.1901 | 0.0474 | 0.2066 | 0.0885 | 0.1609 | 0.1297 | 0.7581 | 2.5229 | 1.7852 | 0.162 | 0.2914 | 0.0515 | 0.1751 | 0.07 | 0.1226 | 0.1358 | 0.1061 | 0.1901 | 0.0884 | 0.1874 | 0.3237 | 1.1118 | 0.2097 | 0.1879 | 0.2355 | 0.3561 | 0.1861 | 0.2826 | 0.3114 | 0.3199 | 0.3961 | 0.3583 | 0.1706
Load_TR6_F6_5 | customer | 0.2803 | 0.048 | 0.2473 | 0.1221 | 0.048 | 0.2023 | 0.1592 | 0.0633 | 0.2023 | 0.1598 | 0.048 | 0.2687 | 0.4324 | 0.0545 | 1.0979 | 2.67 | 4.2192 | 1.1146 | 0.3164 | 0.9567 | 0.1892 | 0.1172 | 1.52 | 0.6907 | 0.1834 | 0.3567 | 0.1892 | 0.1803 | 0.1537 | 0.3532 | 0.3435 | 0.158 | 0.627 | 0.1458 | 1.3716 | 3.4335 | 2.2435 | 1.288 | 0.9384 | 1.5028 | 0.8328 | 0.74 | 0.472 | 0.8222 | 1.2449 | 0.7025 | 0.5239 | 0.7033
Load_TR6_F6_50 | customer | 0.044 | 0.2644 | 0.0762 | 0.1218 | 0.2189 | 0.044 | 0.044 | 0.1549 | 0.1663 | 0.1663 | 0.0519 | 0.1728 | 0.1678 | 0.0569 | 0.1886 | 0.1391 | 0.044 | 0.2491 | 0.0915 | 0.147 | 0.1936 | 0.1021 | 0.1731 | 0.0765 | 0.4802 | 0.0569 | 0.3152 | 0.1223 | 0.1608 | 0.1463 | 0.1359 | 0.1864 | 0.2042 | 0.1182 | 0.274 | 0.0689 | 0.148 | 0.2122 | 0.0483 | 0.4943 | 0.2042 | 0.216 | 0.3618 | 0.196 | 1.285 | 0.7678 | 0.1845 | 0.1263
Load_TR6_F6_50_dup | prosumer | 0.061 | 0.061 | 0.1339 | 0.061 | 0.3561 | 0.6324 | 0.0813 | 0.1299 | 0.0651 | 0.061 | 0.061 | 0.1096 | 0.0853 | 0.061 | 0.061 | 0.1339 | 0.061 | 0.1188 | 0.2201 | 0.3247 | 0.1871 | 1.3831 | 0.1079 | 0.0896 | 0.1693 | 0.3867 | 0.264 | 0.3867 | 0.3459 | 1.4724 | 0.208 | 0.208 | 0.2699 | 0.293 | 0.1422 | 0.1538 | 1.4642 | 0.2892 | 0.1584 | 0.309 | 0.4316 | 0.3347 | 0.1339 | 0.061 | 0.0934 | 0.1015 | 0.1177 | 0.0772
Load_TR6_F6_50_tri | prosumer | 0.086 | 0.1561 | 0.044 | 0.1981 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.1561 | 0.086 | 0.044 | 0.1911 | 0.051 | 0.4402 | 0.0927 | 0.1981 | 0.044 | 0.1055 | 0.2984 | 0.1339 | 0.2027 | 0.058 | 0.044 | 0.2212 | 0.2921 | 0.044 | 0.0668 | 0.0836 | 0.1204 | 0.5243 | 0.2721 | 0.3065 | 0.3684 | 0.1177 | 1.269 | 0.132 | 0.1694 | 0.3566 | 0.2272 | 0.6312 | 0.5479 | 0.3848 | 0.8235 | 0.4159 | 0.7879 | 0.2735 | 0.072
Load_TR6_F6_51 | customer | 0.0822 | 0.1252 | 0.0554 | 0.1521 | 0.05 | 0.1467 | 0.0607 | 0.05 | 0.1574 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1037 | 0.1037 | 0.05 | 0.2171 | 0.2611 | 0.3553 | 0.2986 | 0.2788 | 0.4645 | 0.3231 | 0.4142 | 0.3662 | 0.1143 | 0.2461 | 0.0708 | 0.4268 | 0.4816 | 0.3386 | 0.264 | 0.6762 | 0.2947 | 0.2469 | 0.5616 | 0.5158 | 0.2936 | 0.7212 | 0.6563 | 0.3926 | 0.5737 | 0.5577 | 0.6015 | 0.5304 | 0.05 | 0.0876
Load_TR6_F6_51_dup | customer | 0.7776 | 0.6679 | 0.1696 | 0.037 | 0.2765 | 0.037 | 0.037 | 0.2383 | 0.0752 | 0.1358 | 0.1777 | 0.037 | 0.1994 | 0.1141 | 0.037 | 0.5972 | 0.095 | 0.1376 | 0.1636 | 1.2082 | 0.1811 | 0.4677 | 0.302 | 1.1612 | 1.8629 | 2.1233 | 0.3141 | 0.2165 | 0.0896 | 0.0705 | 0.2001 | 0.1135 | 0.2964 | 0.331 | 0.1934 | 0.0647 | 1.3583 | 0.1295 | 0.2194 | 0.4224 | 0.4244 | 0.631 | 0.6798 | 0.4959 | 0.4968 | 0.6069 | 0.2655 | 0.142
Load_TR6_F6_51_tri | prosumer | 0.2015 | 0.051 | 0.2076 | 0.0757 | 0.051 | 0.1169 | 0.1664 | 0.051 | 0.051 | 0.051 | 0.2324 | 0.051 | 0.051 | 0.1747 | 0.1087 | 0.051 | 0.1334 | 0.1499 | 0.1606 | 0.2282 | 1.1752 | 0.8687 | 1.2004 | 1.0711 | 0.9242 | 3.7226 | 2.6225 | 0.4692 | 0.2324 | 0.051 | 0.0675 | 0.2159 | 0.051 | 0.1582 | 0.1252 | 0.0922 | 0.1911 | 0.051 | 0.2324 | 0.051 | 0.1417 | 0.1417 | 0.051 | 0.1911 | 0.0922 | 0.051 | 0.1664 | 0.1169
Load_TR6_F6_52 | prosumer | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.0929 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.0665 | 0.2355 | 0.0599 | 0.0552 | 0.049 | 0.2089 | 0.0539 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.1253 | 0.1814 | 0.0652 | 0.0757 | 0.1003 | 0.1805 | 0.1099 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049
Load_TR6_F6_52_dup | customer | 0.053 | 0.053 | 0.2313 | 0.053 | 0.1016 | 0.1827 | 0.053 | 0.0935 | 0.1908 | 0.053 | 0.2313 | 0.053 | 0.1908 | 0.0935 | 0.2883 | 0.3007 | 0.2267 | 0.3962 | 0.1194 | 0.0856 | 0.408 | 0.2027 | 0.053 | 0.2313 | 0.053 | 0.0854 | 0.1989 | 0.1445 | 0.3828 | 0.4351 | 0.4133 | 0.3 | 0.3538 | 0.4953 | 0.3045 | 1.1066 | 0.1624 | 0.059 | 0.2493 | 0.234 | 0.3789 | 0.2963 | 0.4147 | 0.2993 | 0.5999 | 0.6317 | 0.053 | 0.053
Load_TR6_F6_52_tri | prosumer | 0.2877 | 0.375 | 0.2157 | 0.056 | 0.056 | 0.142 | 0.1977 | 0.056 | 0.2692 | 0.0705 | 0.056 | 0.2271 | 0.1127 | 0.056 | 0.2128 | 0.1269 | 0.1359 | 0.2039 | 0.0778 | 0.194 | 0.056 | 0.2157 | 0.124 | 0.056 | 0.3002 | 0.1749 | 0.1127 | 0.3442 | 0.6062 | 0.5005 | 0.4543 | 0.0923 | 0.0975 | 0.2277 | 0.1045 | 0.2761 | 0.5675 | 0.495 | 0.3904 | 0.4816 | 0.5535 | 0.758 | 0.6344 | 0.2815 | 0.0787 | 0.1617 | 0.178 | 0.056
Load_TR6_F6_53 | prosumer | 0.045 | 0.3047 | 0.0879 | 0.051 | 0.3416 | 0.051 | 0.1595 | 0.045 | 0.2392 | 0.1535 | 0.1085 | 1.6839 | 1.3392 | 0.6422 | 0.1026 | 0.0857 | 0.3527 | 0.045 | 0.4795 | 1.0517 | 0.664 | 0.3311 | 0.0616 | 0.1609 | 0.1112 | 0.1655 | 0.2744 | 0.3035 | 0.2677 | 0.5255 | 0.3854 | 0.562 | 0.4345 | 0.1896 | 0.5622 | 0.1939 | 0.2977 | 0.3885 | 0.2918 | 0.1873 | 0.1692 | 0.2306 | 0.5601 | 0.376 | 0.5474 | 0.5203 | 0.3439 | 0.2445
Load_TR6_F6_53_dup | prosumer | 0.055 | 0.1269 | 0.2176 | 0.055 | 0.1774 | 0.1672 | 0.1054 | 0.2392 | 0.055 | 0.1312 | 0.2134 | 0.1185 | 0.1397 | 0.1668 | 0.1058 | 0.2134 | 0.055 | 0.055 | 0.2134 | 0.055 | 0.127 | 0.1414 | 0.0592 | 0.2277 | 0.1168 | 0.1773 | 0.163 | 0.1312 | 0.1429 | 0.6906 | 0.337 | 0.5922 | 0.4957 | 0.055 | 0.2557 | 0.0888 | 0.055 | 0.2895 | 0.2293 | 1.4752 | 0.4166 | 0.3136 | 0.3486 | 0.7944 | 0.0931 | 0.2036 | 0.141 | 0.0694
Load_TR6_F6_53_tri | prosumer | 0.1642 | 0.048 | 0.3088 | 0.0685 | 0.048 | 0.2473 | 0.13 | 0.048 | 0.3157 | 0.0617 | 0.0742 | 0.2895 | 0.0617 | 0.1369 | 0.1292 | 0.1593 | 0.1984 | 0.048 | 0.1642 | 0.2131 | 0.048 | 0.1801 | 0.1972 | 0.0545 | 0.3091 | 0.0617 | 0.2747 | 0.1168 | 0.3311 | 0.27 | 0.0851 | 0.1553 | 0.2561 | 0.4423 | 0.4568 | 0.0901 | 0.2999 | 0.3266 | 0.156 | 0.2982 | 0.1154 | 0.1946 | 0.3657 | 0.9993 | 0.3915 | 0.3086 | 0.1681 | 0.2246
Load_TR6_F6_54 | customer | 0.2049 | 0.0673 | 0.1072 | 0.1372 | 0.1937 | 0.0936 | 0.053 | 0.2102 | 0.053 | 0.2057 | 0.1387 | 0.1343 | 0.053 | 0.0673 | 0.2771 | 0.053 | 0.2565 | 0.088 | 0.1162 | 0.4177 | 0.3135 | 0.2419 | 0.5377 | 0.2338 | 0.1749 | 0.9945 | 1.7531 | 0.7077 | 0.053 | 0.2102 | 0.053 | 0.1102 | 0.153 | 0.053 | 0.103 | 0.1602 | 0.1343 | 0.0959 | 0.1673 | 0.053 | 0.2102 | 0.1343 | 0.053 | 0.053 | 0.1974 | 0.147 | 0.0887 | 0.2557
Load_TR6_F6_54_dup | customer | 0.7503 | 0.2568 | 0.054 | 0.2598 | 0.054 | 0.0801 | 0.2061 | 0.0816 | 0.054 | 0.2657 | 0.251 | 0.208 | 0.1565 | 0.054 | 0.2995 | 0.1329 | 0.0781 | 0.3967 | 0.2225 | 0.2209 | 1.5191 | 0.1092 | 0.1389 | 0.1128 | 0.1092 | 0.2046 | 0.1092 | 0.1197 | 0.1389 | 0.8332 | 0.2715 | 0.2846 | 0.3657 | 0.2556 | 0.3344 | 0.3876 | 0.4378 | 0.3632 | 0.5226 | 0.323 | 0.5758 | 0.5674 | 0.684 | 1.0293 | 0.4407 | 0.1683 | 0.1455 | 0.054
Load_TR6_F6_54_tri | customer | 0.475 | 0.3973 | 0.1698 | 0.0497 | 0.3182 | 0.063 | 0.0904 | 0.2908 | 0.043 | 0.1974 | 0.1371 | 0.1485 | 0.1459 | 0.043 | 0.1498 | 0.2314 | 0.1031 | 0.2194 | 0.1018 | 0.1228 | 1.0358 | 0.0829 | 0.1526 | 0.1813 | 1.56 | 0.883 | 1.923 | 0.3972 | 2.5188 | 2.5954 | 0.9561 | 0.2047 | 0.4224 | 0.043 | 0.1765 | 0.2708 | 0.075 | 0.2058 | 0.1845 | 0.7112 | 0.3785 | 0.3525 | 0.366 | 0.5935 | 0.3908 | 0.168 | 0.1632 | 0.2181
Load_TR6_F6_55 | prosumer | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.0921 | 0.4468 | 0.056 | 0.0778 | 0.882 | 0.7728 | 0.938 | 1.6545 | 0.071 | 1.0215 | 0.779 | 1.2854 | 1.1663 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.4931 | 1.3482 | 1.1422 | 0.1874 | 0.339 | 1.5287 | 0.1346 | 0.2976 | 0.3638 | 0.3457 | 0.2681 | 0.2726 | 0.3406
Load_TR6_F6_55_dup | customer | 0.1645 | 0.0923 | 0.114 | 0.1429 | 0.0707 | 0.1862 | 0.049 | 0.2538 | 0.049 | 0.049 | 0.1934 | 0.0634 | 0.049 | 0.1645 | 0.0923 | 0.049 | 0.1862 | 0.0707 | 0.0634 | 0.2019 | 0.0808 | 0.2396 | 0.0543 | 0.1429 | 0.1229 | 0.1827 | 0.224 | 0.2073 | 0.1702 | 0.2155 | 0.0863 | 0.2078 | 0.0584 | 0.0721 | 0.1827 | 0.0923 | 0.114 | 0.1429 | 0.049 | 0.2078 | 0.049 | 0.1637 | 0.3009 | 0.254 | 0.2513 | 0.3431 | 0.3098 | 0.2219
Load_TR6_F6_55_tri | customer | 0.049 | 0.2777 | 0.0925 | 0.0997 | 0.2084 | 0.1111 | 0.2083 | 0.1619 | 0.049 | 0.1078 | 0.2624 | 0.049 | 0.2535 | 0.1167 | 0.0997 | 0.1576 | 0.1054 | 0.1706 | 0.1488 | 0.1562 | 0.1576 | 0.2126 | 0.049 | 0.1975 | 0.223 | 0.2025 | 0.1794 | 0.078 | 0.049 | 0.0772 | 0.293 | 0.049 | 0.3212 | 0.049 | 0.1651 | 0.3932 | 0.0772 | 0.1337 | 0.2586 | 0.6139 | 0.5827 | 0.7466 | 0.6861 | 0.8749 | 1.2018 | 0.3003 | 0.1167 | 0.2535
Load_TR6_F6_56 | prosumer | 0.9617 | 0.5561 | 0.8354 | 0.7362 | 0.1576 | 0.137 | 0.2422 | 0.2307 | 0.0639 | 0.2913 | 0.1906 | 0.4184 | 0.6373 | 0.3183 | 0.4199 | 0.1819 | 0.2082 | 0.4571 | 1.5202 | 0.2489 | 0.1637 | 0.2213 | 0.3085 | 0.3175 | 0.1993 | 0.4181 | 0.1968 | 0.5473 | 0.7599 | 0.4932 | 0.2217 | 0.7588 | 0.1884 | 0.2482 | 0.3904 | 0.5471 | 1.3444 | 0.7669 | 1.3423 | 0.2905 | 0.3876 | 0.766 | 0.264 | 0.8794 | 1.2691 | 0.4119 | 0.6214 | 0.1681
Load_TR6_F6_56_dup | prosumer | 0.1897 | 0.2611 | 0.0791 | 0.2595 | 0.1702 | 0.1543 | 0.2043 | 0.1818 | 0.1425 | 0.1147 | 0.2849 | 0.1092 | 0.2156 | 0.1754 | 0.1177 | 0.2523 | 3.5086 | 1.2015 | 0.9525 | 0.316 | 1.4874 | 1.4209 | 1.0839 | 0.4138 | 0.2612 | 0.0993 | 0.4685 | 0.1098 | 0.2649 | 0.1957 | 0.4001 | 0.2838 | 0.1625 | 0.2981 | 0.2266 | 0.3572 | 0.2695 | 0.4171 | 0.3557 | 0.6853 | 0.7839 | 0.6368 | 0.969 | 0.695 | 1.1144 | 0.9802 | 0.1801 | 0.9379
Load_TR6_F6_56_tri | customer | 0.1034 | 0.089 | 0.2085 | 0.2412 | 0.2768 | 0.046 | 0.1751 | 0.0747 | 0.1177 | 0.1321 | 0.046 | 0.2038 | 0.046 | 0.1894 | 0.0603 | 0.046 | 0.0494 | 0.0692 | 0.1751 | 0.0747 | 0.046 | 0.0747 | 0.1751 | 0.046 | 0.3215 | 0.1177 | 0.046 | 0.2106 | 0.0601 | 0.1308 | 0.4847 | 0.245 | 0.1679 | 0.0921 | 2.1325 | 2.5812 | 1.7829 | 0.052 | 0.1044 | 0.6324 | 0.0603 | 0.0532 | 0.6161 | 0.4601 | 0.6164 | 0.7547 | 0.5523 | 1.4402
Load_TR6_F6_57 | prosumer | 0.046 | 0.1072 | 0.1908 | 0.0725 | 0.1989 | 0.046 | 0.2431 | 0.0814 | 0.0858 | 0.2387 | 0.0681 | 0.2563 | 0.046 | 0.1123 | 0.2121 | 0.046 | 0.196 | 0.1534 | 0.0898 | 0.991 | 0.5618 | 0.3996 | 0.1351 | 0.258 | 0.1792 | 0.103 | 0.5726 | 0.0536 | 0.1454 | 0.0995 | 0.046 | 0.1256 | 0.0813 | 1.1341 | 3.1862 | 2.1118 | 0.1759 | 0.1365 | 0.1237 | 0.2102 | 0.2442 | 0.4009 | 0.5292 | 0.3365 | 0.3203 | 0.6663 | 0.046 | 0.1759
Load_TR6_F6_57_dup | prosumer | 0.046 | 0.3098 | 0.0573 | 0.1178 | 0.1614 | 0.0629 | 0.236 | 0.1311 | 0.48 | 0.2878 | 0.2131 | 0.2759 | 0.1452 | 0.046 | 0.2084 | 0.046 | 0.1808 | 0.1863 | 0.8571 | 0.7638 | 0.2577 | 0.2316 | 0.1854 | 0.0869 | 0.1549 | 0.1914 | 0.2097 | 0.1813 | 0.1463 | 0.1136 | 0.046 | 0.2935 | 0.1551 | 0.0742 | 0.2312 | 0.1077 | 0.1587 | 0.1454 | 0.32 | 0.3603 | 0.442 | 0.5171 | 0.5757 | 0.3551 | 0.276 | 0.0742 | 0.1632 | 0.1757
Load_TR6_F6_57_tri | prosumer | 0.3805 | 0.1247 | 0.048 | 0.166 | 0.048 | 0.166 | 0.048 | 0.0716 | 0.1424 | 0.048 | 0.166 | 0.048 | 0.166 | 0.048 | 1.5799 | 0.0716 | 0.1365 | 0.6076 | 0.644 | 1.8739 | 0.056 | 0.0765 | 0.2355 | 0.1938 | 0.1938 | 0.1423 | 1.3364 | 0.8488 | 0.2237 | 0.1355 | 0.1634 | 0.3957 | 0.0821 | 0.1011 | 0.1129 | 0.2935 | 2.6605 | 2.272 | 0.1542 | 0.0598 | 0.048 | 0.2334 | 0.1269 | 0.4062 | 0.3871 | 0.4897 | 0.2498 | 0.048
Load_TR6_F6_58 | prosumer | 0.048 | 0.2095 | 0.048 | 0.048 | 0.0718 | 0.1434 | 0.048 | 0.048 | 0.048 | 0.1672 | 0.048 | 0.1136 | 0.1016 | 0.048 | 0.0957 | 0.1195 | 0.048 | 0.1672 | 0.096 | 0.1672 | 0.0929 | 0.0581 | 0.171 | 0.9263 | 0.048 | 0.3516 | 0.148 | 0.2672 | 0.0612 | 0.1023 | 0.3294 | 0.2348 | 0.3727 | 0.2383 | 0.0931 | 0.3196 | 0.3716 | 0.4502 | 0.5657 | 0.2976 | 0.1987 | 0.942 | 1.1321 | 0.4801 | 0.4652 | 0.3495 | 0.048 | 0.1672
Load_TR6_F6_58_dup | prosumer | 0.052 | 0.052 | 0.052 | 0.052 | 0.0717 | 0.1769 | 0.052 | 0.1769 | 0.0717 | 0.052 | 0.1901 | 0.0586 | 0.0849 | 0.1638 | 0.052 | 0.052 | 0.0798 | 0.1887 | 0.0876 | 0.2011 | 0.9673 | 0.2479 | 0.1966 | 0.052 | 0.1835 | 0.0651 | 0.0651 | 0.1835 | 0.052 | 0.1966 | 0.052 | 0.1572 | 0.0914 | 0.1177 | 0.1309 | 0.0564 | 0.3696 | 1.1587 | 0.2483 | 0.3633 | 0.7898 | 0.4565 | 0.5198 | 0.5305 | 0.4802 | 0.4264 | 0.1608 | 0.1875
Load_TR6_F6_58_tri | customer | 0.6712 | 0.4177 | 0.05 | 0.05 | 0.1163 | 0.0583 | 0.108 | 0.0666 | 0.0997 | 0.0749 | 0.05 | 0.05 | 0.05 | 0.0956 | 0.079 | 0.05 | 2.8977 | 0.121 | 0.3161 | 0.2878 | 0.3551 | 0.2553 | 0.0989 | 0.1729 | 0.6402 | 2.6501 | 3.4538 | 0.1012 | 0.0523 | 0.1741 | 0.1074 | 0.05 | 0.29 | 0.1555 | 0.3803 | 0.6844 | 0.836 | 0.7187 | 2.0877 | 0.7713 | 1.3992 | 0.593 | 0.6949 | 0.7518 | 0.5373 | 0.3644 | 0.5584 | 0.2376
Load_TR6_F6_59 | customer | 0.1036 | 0.1706 | 0.0976 | 0.0586 | 0.2602 | 0.053 | 0.1323 | 0.1865 | 0.053 | 0.174 | 0.1448 | 0.053 | 0.1223 | 0.587 | 1.4668 | 0.2019 | 1.5513 | 0.6897 | 0.3013 | 0.3667 | 0.2005 | 0.1182 | 0.3666 | 0.3576 | 0.1422 | 0.1766 | 0.053 | 0.1422 | 0.1766 | 0.1422 | 0.053 | 0.2658 | 0.053 | 0.1373 | 0.1716 | 0.2485 | 0.4158 | 0.3752 | 0.3559 | 0.4472 | 0.4233 | 0.5942 | 0.442 | 1.4198 | 1.6793 | 0.4103 | 0.2411 | 0.171
Load_TR6_F6_59_dup | prosumer | 0.3398 | 0.053 | 0.1617 | 0.2429 | 0.0866 | 0.0866 | 0.1951 | 0.1562 | 0.177 | 0.0908 | 0.2076 | 0.1643 | 0.1646 | 0.2153 | 0.5527 | 0.6306 | 0.4116 | 0.232 | 0.1718 | 0.1016 | 0.202 | 0.2074 | 0.1173 | 0.2429 | 0.1727 | 0.1962 | 0.3358 | 0.1472 | 0.458 | 1.2857 | 0.2749 | 0.4339 | 1.0597 | 0.8525 | 0.4597 | 0.5032 | 0.3017 | 0.1286 | 0.2313 | 0.5028 | 0.5858 | 0.7609 | 0.6387 | 0.7756 | 0.6367 | 0.6774 | 0.6668 | 0.1338
Load_TR6_F6_59_tri | prosumer | 0.033 | 0.033 | 0.033 | 0.0689 | 0.0689 | 0.033 | 0.033 | 0.033 | 0.0969 | 0.041 | 0.061 | 0.0769 | 0.0809 | 0.057 | 0.033 | 0.057 | 0.2721 | 0.1381 | 0.21 | 0.0728 | 0.1324 | 0.089 | 3.11 | 2.2321 | 0.6365 | 0.1025 | 0.1166 | 0.0567 | 0.1186 | 0.058 | 0.053 | 0.135 | 0.2414 | 0.069 | 0.0889 | 0.033 | 0.033 | 0.1097 | 0.0815 | 0.042 | 0.0621 | 0.1009 | 0.033 | 0.041 | 0.0969 | 0.033 | 0.1049 | 0.033
Load_TR6_F6_5_dup | prosumer | 0.046 | 0.1588 | 0.1193 | 0.2879 | 0.0573 | 0.046 | 0.2306 | 0.1879 | 0.1575 | 0.0901 | 0.2092 | 0.2327 | 0.1458 | 0.2465 | 0.1174 | 0.1137 | 0.046 | 0.1971 | 0.2214 | 0.0801 | 0.3318 | 0.0526 | 0.2675 | 0.151 | 0.2282 | 0.1903 | 0.0799 | 0.2538 | 0.1409 | 0.385 | 0.2854 | 0.1115 | 0.0499 | 0.0976 | 0.2802 | 0.2434 | 0.3925 | 0.2389 | 0.1841 | 0.4586 | 0.7928 | 0.4193 | 0.2906 | 0.4634 | 0.533 | 0.5935 | 0.5455 | 0.2354
Load_TR6_F6_5_tri | customer | 0.061 | 0.0523 | 0.1214 | 0.048 | 0.1258 | 0.0523 | 0.1214 | 0.0523 | 0.1214 | 0.048 | 0.1258 | 0.048 | 0.061 | 0.1128 | 0.0869 | 0.0869 | 0.0566 | 0.1171 | 0.048 | 0.048 | 0.048 | 0.1085 | 0.0653 | 0.061 | 0.1128 | 0.048 | 0.061 | 0.1128 | 0.0782 | 0.1408 | 0.048 | 0.149 | 0.0974 | 0.1723 | 0.0623 | 0.048 | 0.1008 | 0.1258 | 0.0572 | 0.1745 | 0.3424 | 0.3084 | 0.3381 | 0.1042 | 0.048 | 0.0653 | 0.1085 | 0.0782
Load_TR6_F6_6 | prosumer | 0.046 | 0.1994 | 0.046 | 0.1576 | 0.0878 | 0.046 | 0.1994 | 0.046 | 0.1366 | 0.1088 | 0.046 | 0.046 | 0.1994 | 0.046 | 0.1392 | 0.3114 | 0.1786 | 1.5454 | 1.2938 | 0.6964 | 0.1645 | 0.0809 | 0.046 | 0.1994 | 0.1681 | 0.8241 | 0.4977 | 0.3759 | 0.0502 | 0.106 | 0.1571 | 0.0544 | 0.2113 | 0.165 | 0.1274 | 0.2055 | 0.0753 | 0.1924 | 0.0746 | 0.2884 | 0.1402 | 0.2244 | 0.3742 | 0.2583 | 0.3784 | 0.2107 | 1.2444 | 0.2241
Load_TR6_F6_60 | customer | 0.5914 | 0.5487 | 0.047 | 0.1283 | 0.047 | 0.0644 | 0.1109 | 0.047 | 0.1051 | 0.0702 | 0.047 | 0.144 | 0.047 | 0.0644 | 0.1109 | 0.047 | 0.1283 | 0.047 | 0.0612 | 0.3289 | 0.2523 | 0.0988 | 0.9447 | 0.115 | 1.4616 | 0.1225 | 0.047 | 0.076 | 0.2276 | 0.1126 | 0.1425 | 0.123 | 0.1414 | 0.1353 | 0.0919 | 0.3063 | 0.7747 | 0.461 | 0.2416 | 0.1753 | 0.047 | 0.1283 | 0.2942 | 0.8006 | 0.4576 | 0.4026 | 0.278 | 0.1283
Load_TR6_F6_60_dup | customer | 0.0976 | 0.0782 | 0.0937 | 0.051 | 0.051 | 0.051 | 0.1209 | 0.051 | 0.051 | 0.051 | 0.0937 | 0.0782 | 0.051 | 0.1209 | 0.051 | 0.0774 | 0.0994 | 0.0939 | 0.9849 | 0.0552 | 0.0667 | 0.3635 | 1.4397 | 0.2315 | 0.4509 | 1.862 | 0.961 | 0.4497 | 0.4021 | 0.5185 | 0.6261 | 0.3146 | 0.2796 | 0.3427 | 0.439 | 0.9075 | 0.5325 | 0.5705 | 0.1838 | 0.5676 | 0.4355 | 0.6852 | 0.702 | 0.6203 | 0.7449 | 0.4691 | 0.5668 | 0.1821
Load_TR6_F6_60_tri | prosumer | 0.054 | 0.1719 | 0.0786 | 0.0822 | 0.0892 | 0.054 | 0.054 | 0.1173 | 0.054 | 0.054 | 0.1173 | 0.054 | 0.0857 | 0.0857 | 0.054 | 0.1173 | 0.3058 | 0.3028 | 0.0669 | 0.3347 | 0.204 | 0.054 | 0.054 | 0.1138 | 0.0575 | 0.054 | 0.0997 | 0.0716 | 0.1033 | 0.0681 | 0.1173 | 0.1193 | 0.2397 | 2.8577 | 0.434 | 0.2038 | 0.2724 | 0.2786 | 0.4477 | 0.4133 | 0.4717 | 0.9095 | 1.2033 | 0.4327 | 0.4417 | 0.3476 | 0.0822 | 0.0892
Load_TR6_F6_61 | prosumer | 0.5994 | 0.5442 | 0.5475 | 0.6563 | 0.3339 | 0.096 | 0.045 | 0.1867 | 0.1313 | 0.1673 | 0.0643 | 0.0579 | 0.1738 | 0.0977 | 0.2202 | 0.0929 | 0.1606 | 0.1094 | 0.0828 | 0.3248 | 0.1287 | 0.045 | 0.0617 | 1.0719 | 0.2045 | 0.1611 | 0.1518 | 0.2799 | 0.0555 | 0.287 | 0.1089 | 0.1786 | 0.524 | 0.1265 | 0.1867 | 0.1393 | 0.1055 | 0.1713 | 0.1949 | 1.2712 | 0.3241 | 0.4527 | 0.5515 | 0.5493 | 0.3648 | 0.3606 | 0.1025 | 0.0738
Load_TR6_F6_61_dup | prosumer | 0.0719 | 0.042 | 0.042 | 0.2062 | 0.042 | 0.0868 | 0.1614 | 0.042 | 0.042 | 0.2062 | 0.042 | 0.0793 | 0.1689 | 0.042 | 0.042 | 0.1212 | 0.2172 | 0.0441 | 0.9284 | 0.2993 | 1.5256 | 2.1318 | 2.6132 | 0.7326 | 0.2395 | 0.5331 | 4.1265 | 2.5312 | 0.3727 | 0.3885 | 3.9087 | 2.8208 | 0.555 | 0.5504 | 1.3131 | 0.6176 | 0.101 | 0.2062 | 0.1007 | 0.3896 | 0.3672 | 0.3629 | 0.1615 | 0.4036 | 0.3691 | 0.3012 | 0.4581 | 0.1092
Load_TR6_F6_61_tri | prosumer | 0.1444 | 0.2298 | 0.1611 | 0.153 | 0.0963 | 0.3036 | 0.094 | 0.183 | 0.1906 | 0.2472 | 0.1842 | 0.1934 | 0.1515 | 0.2126 | 0.3054 | 0.2342 | 0.3648 | 0.0842 | 0.0958 | 0.2224 | 0.2155 | 0.1476 | 0.2902 | 0.0704 | 0.1315 | 0.253 | 0.1565 | 0.9093 | 0.4148 | 0.7124 | 0.1774 | 0.1669 | 0.63 | 0.1632 | 0.3355 | 0.5556 | 0.124 | 0.2595 | 0.2849 | 0.4331 | 0.5291 | 0.421 | 0.4536 | 0.419 | 0.4381 | 0.2754 | 0.2013 | 0.1494
Load_TR6_F6_62 | prosumer | 0.1651 | 0.047 | 0.2207 | 0.1215 | 0.0825 | 0.0913 | 0.1924 | 0.0833 | 0.2053 | 0.1235 | 0.1268 | 0.2198 | 0.1223 | 0.1006 | 0.2983 | 0.1835 | 0.8476 | 0.138 | 0.1268 | 0.047 | 0.5935 | 0.2266 | 0.2853 | 0.1769 | 0.1268 | 0.2154 | 0.0825 | 0.0913 | 0.2154 | 0.1268 | 0.047 | 0.047 | 0.273 | 0.0692 | 0.1896 | 0.1526 | 0.047 | 0.1268 | 0.1695 | 0.138 | 0.1096 | 0.3694 | 0.2127 | 0.3691 | 0.0592 | 0.1817 | 1.5382 | 1.4055
Load_TR6_F6_62_dup | customer | 0.1604 | 0.055 | 0.055 | 0.1118 | 0.1766 | 0.055 | 0.2334 | 0.055 | 0.6563 | 0.9147 | 0.4722 | 0.055 | 0.1847 | 0.2353 | 0.055 | 0.2334 | 0.055 | 0.1036 | 0.5109 | 1.4866 | 1.7703 | 2.1891 | 2.5585 | 1.9797 | 0.1361 | 0.055 | 0.055 | 0.168 | 0.8155 | 0.055 | 0.1199 | 1.6688 | 0.4948 | 0.7275 | 0.2765 | 0.2253 | 0.0717 | 0.4107 | 0.6492 | 0.8626 | 0.9268 | 2.4162 | 2.2719 | 1.1693 | 0.9561 | 1.0328 | 0.1604 | 0.128
Load_TR6_F6_62_tri | customer | 0.5998 | 0.2279 | 0.056 | 0.056 | 0.0794 | 0.2044 | 0.056 | 0.2201 | 0.0638 | 0.0794 | 0.2044 | 0.056 | 0.1263 | 0.1576 | 0.056 | 0.1956 | 0.2547 | 0.181 | 0.2263 | 0.2576 | 0.2134 | 0.4063 | 0.3751 | 0.3846 | 0.6016 | 0.5128 | 0.5043 | 0.2677 | 1.107 | 1.817 | 2.348 | 0.1705 | 0.1825 | 0.4845 | 0.056 | 0.1282 | 0.3764 | 0.1224 | 1.6757 | 1.4086 | 1.375 | 0.4526 | 0.2551 | 0.4675 | 0.2619 | 0.2431 | 0.0873 | 0.1966
Load_TR6_F6_63 | prosumer | 0.1314 | 0.055 | 0.0868 | 0.1633 | 0.055 | 0.055 | 0.1951 | 0.055 | 0.1187 | 0.1314 | 0.0677 | 0.1824 | 0.055 | 0.2395 | 1.9225 | 0.9754 | 1.3233 | 1.8482 | 1.2958 | 0.2631 | 0.2753 | 0.4026 | 0.1484 | 0.2069 | 0.5373 | 0.5677 | 0.5401 | 0.2986 | 0.4586 | 0.2953 | 0.3023 | 0.4501 | 0.2202 | 0.3556 | 1.3429 | 0.1535 | 0.2067 | 0.0968 | 0.2085 | 0.2217 | 0.3476 | 0.528 | 0.3666 | 0.3974 | 1.0337 | 0.3053 | 0.5058 | 0.171
Load_TR6_F6_63_dup | prosumer | 0.1485 | 0.1704 | 0.2205 | 0.1769 | 0.048 | 0.2205 | 0.1769 | 0.1342 | 0.2502 | 0.0609 | 0.2205 | 0.106 | 0.2443 | 0.095 | 0.1769 | 0.2205 | 0.4403 | 0.2516 | 0.2474 | 0.048 | 0.1769 | 0.2205 | 0.1769 | 0.095 | 0.1734 | 0.0544 | 0.241 | 0.1499 | 0.1382 | 0.2199 | 0.1709 | 0.1793 | 0.3705 | 0.141 | 0.4137 | 0.4205 | 0.4351 | 0.3988 | 0.5446 | 0.599 | 0.5831 | 0.8045 | 0.6223 | 0.8015 | 0.9001 | 0.7618 | 0.58 | 0.9914
Load_TR6_F6_63_tri | prosumer | 0.048 | 0.091 | 0.1628 | 0.1259 | 0.2058 | 0.1259 | 0.048 | 0.2664 | 0.0653 | 0.1546 | 0.1771 | 0.1259 | 0.2058 | 0.1259 | 0.1197 | 0.1684 | 0.1076 | 0.1098 | 0.2147 | 0.1671 | 0.2203 | 0.1114 | 0.0913 | 0.0826 | 0.2707 | 0.061 | 0.1259 | 0.2058 | 0.2365 | 0.3792 | 0.3302 | 0.0567 | 0.3386 | 0.2015 | 0.2571 | 0.1848 | 0.3652 | 0.2416 | 0.1521 | 0.546 | 0.3229 | 0.048 | 0.2837 | 0.048 | 0.0956 | 0.2361 | 0.048 | 0.2334
Load_TR6_F6_64 | prosumer | 0.1491 | 0.1391 | 0.083 | 0.034 | 0.1911 | 0.1461 | 0.034 | 0.1881 | 0.103 | 0.08 | 0.1881 | 0.1491 | 0.097 | 0.1251 | 0.2994 | 0.4737 | 0.2383 | 0.5974 | 0.041 | 0.0743 | 0.2068 | 0.09 | 0.0608 | 0.2764 | 0.034 | 0.1491 | 0.1706 | 0.5376 | 0.4566 | 0.3491 | 0.3623 | 0.359 | 0.4337 | 0.1878 | 0.882 | 1.9299 | 0.4614 | 0.2341 | 1.177 | 0.7608 | 0.6809 | 0.7768 | 0.9805 | 0.7012 | 0.7603 | 0.8927 | 0.9862 | 0.6767
Load_TR6_F6_64_dup | customer | 0.1499 | 0.05 | 0.05 | 0.1049 | 0.095 | 0.05 | 0.1349 | 0.065 | 0.05 | 0.05 | 0.055 | 0.1449 | 0.05 | 0.05 | 0.05 | 0.0616 | 0.0868 | 0.1096 | 0.1595 | 0.0636 | 0.1499 | 0.05 | 0.1499 | 0.05 | 0.095 | 0.1049 | 0.05 | 0.1991 | 0.125 | 0.2259 | 0.328 | 0.1593 | 0.2107 | 0.2746 | 0.1589 | 0.1365 | 0.1903 | 0.2749 | 0.2307 | 1.6831 | 0.2909 | 0.3066 | 0.2822 | 0.3704 | 0.3082 | 0.9488 | 0.8168 | 0.2389
Load_TR6_F6_64_tri | customer | 0.053 | 0.053 | 0.1606 | 0.053 | 0.1452 | 0.0684 | 0.053 | 0.1529 | 0.0607 | 0.053 | 0.1606 | 0.053 | 0.0991 | 0.1145 | 0.053 | 0.1606 | 0.053 | 0.0537 | 0.1634 | 0.2302 | 0.3063 | 0.1736 | 0.5629 | 0.9979 | 0.0675 | 0.1057 | 0.1407 | 0.0878 | 0.972 | 0.1265 | 0.1479 | 0.0761 | 0.1375 | 0.053 | 0.053 | 0.1879 | 0.3499 | 1.1288 | 0.5981 | 0.2402 | 0.053 | 0.053 | 0.1606 | 0.053 | 0.1606 | 0.053 | 0.0607 | 0.1529
Load_TR6_F6_65 | prosumer | 0.1478 | 0.1059 | 0.05 | 0.05 | 0.2037 | 0.05 | 0.1269 | 0.1269 | 0.05 | 0.2037 | 0.05 | 0.2037 | 0.05 | 0.1199 | 0.1338 | 0.0543 | 0.2443 | 0.1614 | 0.223 | 0.3209 | 0.1951 | 0.3382 | 0.229 | 1.3619 | 0.265 | 0.1515 | 0.2037 | 0.05 | 0.1467 | 0.3094 | 1.259 | 0.2287 | 0.0984 | 0.1677 | 0.2486 | 0.1656 | 0.2381 | 0.1488 | 0.162 | 0.3544 | 1.2102 | 0.2354 | 0.7016 | 0.4429 | 0.3211 | 0.1987 | 0.2223 | 0.5724
Load_TR6_F6_65_dup | prosumer | 0.1096 | 0.052 | 0.168 | 0.1108 | 0.0958 | 0.1399 | 0.0951 | 0.1197 | 0.048 | 0.1197 | 0.1831 | 0.0998 | 0.1739 | 0.109 | 0.048 | 0.2349 | 0.048 | 0.1213 | 0.1616 | 0.048 | 0.1563 | 0.1265 | 0.1077 | 0.1594 | 0.0637 | 0.1161 | 0.0951 | 0.1157 | 0.2234 | 0.172 | 0.048 | 0.1632 | 0.1197 | 0.1527 | 0.3295 | 0.2339 | 0.4542 | 0.508 | 0.3408 | 0.5425 | 0.5785 | 0.506 | 0.1318 | 0.0759 | 0.2965 | 0.3419 | 0.3942 | 0.1793
Load_TR6_F6_65_tri | customer | 0.2264 | 0.052 | 0.1512 | 0.052 | 0.0768 | 0.2115 | 0.052 | 0.2316 | 0.0567 | 0.1512 | 0.0709 | 0.1182 | 0.1512 | 0.052 | 0.1958 | 0.2672 | 0.1541 | 0.1591 | 0.1549 | 0.0867 | 0.2699 | 0.1512 | 0.1371 | 0.0768 | 0.1264 | 0.1371 | 0.0619 | 0.1933 | 0.0851 | 0.052 | 0.1264 | 0.0768 | 0.057 | 0.2533 | 0.073 | 0.1064 | 0.2033 | 0.052 | 0.1413 | 0.1045 | 0.2027 | 1.3042 | 0.487 | 0.516 | 0.6302 | 0.6205 | 0.607 | 0.2511
Load_TR6_F6_66 | prosumer | 0.081 | 0.2796 | 0.049 | 0.2026 | 0.1579 | 0.049 | 0.1356 | 0.201 | 0.073 | 0.1979 | 0.1626 | 0.1323 | 0.2282 | 0.049 | 0.225 | 0.049 | 0.049 | 0.2283 | 0.1322 | 0.049 | 0.1259 | 0.2346 | 0.049 | 0.2491 | 0.1114 | 0.1627 | 0.1979 | 0.049 | 0.2779 | 0.0827 | 0.1308 | 0.2298 | 0.049 | 0.049 | 0.1308 | 0.2298 | 0.1521 | 0.209 | 0.065 | 0.0906 | 0.27 | 0.049 | 0.3116 | 0.049 | 0.177 | 0.097 | 0.081 | 0.193
Load_TR6_F6_66_dup | customer | 0.3348 | 1.2986 | 0.4244 | 0.1076 | 0.1289 | 0.1935 | 0.043 | 0.1836 | 0.1209 | 0.0688 | 0.207 | 0.1076 | 0.2149 | 0.043 | 0.1074 | 0.336 | 0.1331 | 0.3342 | 0.2144 | 0.1326 | 0.1076 | 0.1055 | 0.156 | 0.1159 | 0.4096 | 0.1471 | 0.0597 | 0.197 | 0.2085 | 0.2727 | 0.0821 | 0.1076 | 0.1211 | 0.1367 | 0.1076 | 0.2149 | 0.0574 | 0.2651 | 0.1015 | 0.3181 | 0.5059 | 0.4299 | 0.4875 | 0.3207 | 0.6321 | 0.4502 | 0.4628 | 0.2833
Load_TR6_F6_66_tri | prosumer | 0.054 | 0.054 | 0.2292 | 0.054 | 0.2053 | 0.0779 | 0.054 | 0.2292 | 0.054 | 0.1735 | 0.1098 | 0.054 | 0.2292 | 0.054 | 0.2556 | 0.342 | 0.2153 | 0.331 | 0.2925 | 0.2425 | 0.3985 | 0.1117 | 0.1667 | 0.1686 | 0.054 | 0.1416 | 0.1416 | 0.0575 | 0.1894 | 0.0938 | 0.0949 | 0.3019 | 0.147 | 0.298 | 0.1404 | 0.137 | 0.2954 | 0.116 | 0.3385 | 0.3565 | 0.399 | 0.5824 | 0.6396 | 0.5397 | 0.6129 | 0.3975 | 0.4286 | 0.0938
Load_TR6_F6_67 | prosumer | 0.06 | 0.2428 | 0.152 | 0.1902 | 0.1849 | 0.2099 | 0.06 | 0.3348 | 0.06 | 0.1904 | 0.2044 | 0.06 | 0.3348 | 0.06 | 0.2889 | 0.1059 | 0.1386 | 0.2562 | 0.06 | 0.0863 | 0.276 | 0.0925 | 0.152 | 0.1126 | 0.06 | 0.2046 | 0.1902 | 0.4171 | 0.2076 | 0.2398 | 0.1257 | 0.1186 | 0.1908 | 0.178 | 0.1774 | 0.2963 | 0.3515 | 0.2009 | 0.6494 | 0.6687 | 1.3503 | 1.3382 | 0.7974 | 1.0016 | 1.3009 | 1.0223 | 0.875 | 0.5216
Load_TR6_F6_67_dup | customer | 0.1833 | 0.1591 | 0.037 | 0.1394 | 0.203 | 0.0541 | 0.2076 | 0.037 | 0.1569 | 0.2078 | 0.0617 | 0.1774 | 0.1694 | 0.1132 | 0.2529 | 0.049 | 0.2049 | 0.1613 | 0.1043 | 0.2446 | 0.1608 | 0.2745 | 0.3399 | 0.9871 | 0.2916 | 0.2177 | 0.1819 | 0.1932 | 0.3153 | 1.7103 | 0.8103 | 0.2615 | 1.2081 | 0.832 | 0.3076 | 0.2111 | 0.2316 | 0.4517 | 0.3119 | 0.5211 | 0.8261 | 1.4494 | 0.44 | 0.3287 | 0.1474 | 0.4401 | 0.2688 | 0.296
Load_TR6_F6_67_tri | prosumer | 0.041 | 0.112 | 0.041 | 0.112 | 0.041 | 0.112 | 0.041 | 0.041 | 0.041 | 0.041 | 0.0804 | 0.0725 | 1.3923 | 0.2898 | 0.0483 | 0.0923 | 0.0648 | 0.041 | 0.112 | 0.041 | 0.041 | 0.112 | 0.041 | 0.041 | 0.042 | 0.1034 | 0.211 | 0.3642 | 0.2427 | 0.3485 | 0.2646 | 0.3924 | 0.4183 | 0.2181 | 0.2788 | 0.3901 | 1.3275 | 1.8435 | 0.731 | 0.2526 | 0.3799 | 0.37 | 0.3221 | 0.3614 | 0.1936 | 0.041 | 0.112 | 0.041
Load_TR6_F6_68 | prosumer | 0.052 | 0.1186 | 0.1613 | 0.052 | 0.2279 | 0.052 | 0.1186 | 0.1613 | 0.052 | 0.052 | 0.1121 | 0.1012 | 0.1678 | 0.1121 | 0.2773 | 0.3113 | 0.5342 | 0.3918 | 0.3089 | 0.244 | 0.052 | 0.052 | 0.0668 | 0.1038 | 0.1613 | 0.1186 | 0.1613 | 0.052 | 0.0927 | 0.1325 | 0.114 | 0.1658 | 0.1066 | 0.1186 | 0.1613 | 0.1186 | 0.1558 | 0.0575 | 0.052 | 0.2169 | 0.0629 | 0.3832 | 0.495 | 0.4527 | 0.2498 | 0.2131 | 0.0668 | 0.0705
Load_TR6_F6_68_dup | customer | 0.041 | 0.1877 | 0.2482 | 0.041 | 0.2542 | 0.1817 | 0.0655 | 0.1529 | 0.1817 | 0.1633 | 0.1178 | 0.3181 | 0.041 | 0.2701 | 0.1658 | 0.0766 | 0.4036 | 0.3181 | 0.1043 | 0.7129 | 1.8022 | 0.8775 | 0.4 | 0.2339 | 0.3309 | 0.041 | 0.1958 | 0.1633 | 0.0973 | 0.1395 | 0.1912 | 0.2447 | 0.041 | 0.2697 | 0.1103 | 0.1349 | 0.3267 | 0.2801 | 0.3054 | 0.2802 | 0.4678 | 0.6157 | 0.3544 | 0.2483 | 0.133 | 0.3226 | 0.1133 | 0.2058
Load_TR6_F6_68_tri | prosumer | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.0552 | 0.128 | 0.18 | 0.1399 | 0.2018 | 0.1592 | 0.053 | 0.1495 | 0.2362 | 0.1711 | 0.093 | 1.3663 | 0.1785 | 0.247 | 0.0998 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.0938 | 0.1275 | 0.1115 | 0.4656 | 0.2979 | 0.1001 | 0.053 | 0.053 | 0.4857 | 0.4521 | 0.7126 | 0.1609
Load_TR6_F6_69 | customer | 0.059 | 0.1475 | 0.1203 | 0.0794 | 0.1884 | 0.059 | 0.059 | 0.2088 | 0.059 | 0.0862 | 0.1816 | 0.059 | 0.059 | 0.2088 | 0.059 | 0.202 | 0.1988 | 0.4981 | 0.2341 | 0.3119 | 0.5542 | 0.4725 | 0.2271 | 0.3887 | 1.5262 | 0.3133 | 0.4614 | 0.4639 | 0.1002 | 0.1913 | 0.5063 | 0.7487 | 0.6873 | 0.8188 | 0.3371 | 0.3087 | 0.4588 | 1.7736 | 0.3947 | 0.4837 | 1.674 | 0.5374 | 0.6608 | 0.9905 | 1.746 | 1.6349 | 0.7602 | 0.0726
Load_TR6_F6_69_dup | customer | 0.1105 | 0.1409 | 0.036 | 0.0658 | 0.1702 | 0.036 | 0.2 | 0.036 | 0.036 | 0.2 | 0.036 | 0.036 | 0.2 | 0.036 | 0.0435 | 0.215 | 0.0435 | 0.0485 | 0.2045 | 0.036 | 0.0509 | 0.1851 | 0.036 | 0.0807 | 0.1552 | 0.036 | 0.036 | 0.2026 | 0.3019 | 1.207 | 0.0909 | 0.1262 | 0.143 | 0.0627 | 0.2383 | 0.0615 | 0.04 | 0.1454 | 0.2401 | 0.271 | 0.4008 | 0.395 | 0.5714 | 0.5932 | 0.4223 | 0.4381 | 0.3057 | 0.305
Load_TR6_F6_69_tri | customer | 0.4989 | 0.6213 | 0.2679 | 0.1765 | 0.1866 | 0.2721 | 0.1794 | 0.255 | 0.1536 | 0.1723 | 0.1689 | 0.2836 | 0.1251 | 0.1437 | 0.2589 | 0.2321 | 0.058 | 0.2118 | 0.2247 | 0.2344 | 0.1437 | 0.2025 | 1.8257 | 2.081 | 0.6405 | 0.4047 | 0.3807 | 0.6716 | 0.1033 | 0.2851 | 0.2021 | 0.0723 | 0.4035 | 0.0694 | 0.2408 | 0.2465 | 0.091 | 0.3428 | 0.5995 | 0.9054 | 0.5255 | 0.9658 | 0.8125 | 0.7217 | 0.8593 | 0.9206 | 0.822 | 0.236
Load_TR6_F6_6_dup | prosumer | 0.1577 | 0.1187 | 0.1892 | 0.1377 | 0.1302 | 0.05 | 0.2417 | 0.1196 | 0.1635 | 0.1977 | 0.05 | 0.05 | 0.1645 | 0.0633 | 0.1888 | 1.5059 | 0.3268 | 0.3363 | 0.2011 | 0.268 | 0.053 | 0.2851 | 0.1226 | 0.1292 | 0.9557 | 2.688 | 2.6528 | 0.3785 | 0.0887 | 0.2531 | 0.1081 | 0.1752 | 0.2222 | 0.7812 | 0.5604 | 0.4968 | 0.073 | 0.2243 | 0.1794 | 0.3821 | 0.4503 | 0.6376 | 1.169 | 0.9949 | 0.8171 | 0.8221 | 0.7545 | 0.7299
Load_TR6_F6_6_tri | customer | 0.1019 | 0.1584 | 0.0898 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.0739 | 0.0742 | 1.0916 | 1.9493 | 0.1718 | 0.1099 | 0.2555 | 0.2679 | 0.0623 | 0.0499 | 0.049 | 2.1216 | 0.5747 | 0.0567 | 0.0684 | 0.2778 | 0.1119 | 0.0671 | 0.2659 | 1.12 | 0.9137 | 0.1035 | 0.0582 | 0.0572 | 1.4034 | 1.0557 | 1.1871 | 0.8472 | 0.2592 | 0.2158 | 0.1981 | 0.4691 | 0.3156 | 0.233 | 0.049
Load_TR6_F6_7 | customer | 0.1521 | 0.041 | 0.2431 | 0.041 | 0.041 | 0.2134 | 0.0707 | 0.0528 | 0.1754 | 0.0969 | 0.0904 | 0.1937 | 0.041 | 0.2431 | 0.041 | 0.1188 | 0.1653 | 0.1129 | 1.9727 | 0.4666 | 0.3996 | 0.4737 | 0.1089 | 0.041 | 0.041 | 0.041 | 0.1712 | 0.057 | 0.1264 | 0.2626 | 0.2035 | 0.1306 | 0.0975 | 0.2341 | 0.1441 | 0.1965 | 0.2996 | 0.4575 | 0.2759 | 0.4943 | 0.041 | 0.1357 | 0.4136 | 0.3023 | 0.5755 | 0.6764 | 0.4409 | 0.4726
Load_TR6_F6_70 | prosumer | 0.1489 | 0.0821 | 0.042 | 0.189 | 0.042 | 0.042 | 0.1222 | 0.1088 | 0.0687 | 0.1623 | 0.042 | 0.1489 | 0.0821 | 0.1394 | 0.1757 | 0.1111 | 0.1686 | 0.1389 | 0.042 | 0.189 | 0.042 | 0.1088 | 0.1222 | 0.042 | 0.042 | 0.1824 | 0.0554 | 0.1715 | 0.1362 | 0.042 | 1.7143 | 0.0621 | 0.1373 | 0.3129 | 0.4083 | 0.3813 | 0.4322 | 1.658 | 0.1556 | 0.0754 | 0.2226 | 0.5597 | 0.4283 | 0.5077 | 0.6936 | 1.3586 | 0.3208 | 0.169
Load_TR6_F6_70_dup | customer | 0.049 | 0.2227 | 0.049 | 0.049 | 0.2227 | 0.049 | 0.049 | 0.1911 | 0.0806 | 0.0885 | 0.1832 | 0.049 | 0.1516 | 0.1201 | 0.049 | 0.2227 | 0.049 | 0.0569 | 0.1641 | 0.1847 | 0.6622 | 0.4922 | 1.9595 | 3.0177 | 1.6081 | 0.049 | 0.2762 | 0.1911 | 0.0502 | 0.0711 | 0.2448 | 0.0556 | 0.2926 | 0.3847 | 0.3656 | 0.3989 | 0.4312 | 0.2791 | 0.242 | 1.3524 | 1.2675 | 0.4609 | 0.7192 | 0.4998 | 0.4661 | 0.3006 | 0.3043 | 0.4833
Load_TR6_F6_70_tri | prosumer | 0.0787 | 0.1963 | 0.1371 | 0.1848 | 0.1772 | 0.0615 | 0.2537 | 0.0969 | 0.05 | 0.1589 | 0.2031 | 0.05 | 0.2115 | 0.1504 | 0.0739 | 0.2881 | 0.05 | 0.2126 | 0.3631 | 0.2712 | 0.3035 | 0.2371 | 0.1525 | 0.1784 | 0.1609 | 0.2485 | 0.3003 | 0.881 | 0.1837 | 0.3193 | 0.2766 | 0.4681 | 0.2953 | 1.064 | 0.3438 | 0.2757 | 0.3545 | 0.2322 | 0.158 | 0.4381 | 0.332 | 0.3963 | 0.4858 | 0.4946 | 0.6232 | 0.8757 | 0.5518 | 0.7945
Load_TR6_F6_71 | prosumer | 0.1379 | 0.0791 | 0.057 | 0.1599 | 0.057 | 0.0791 | 0.1379 | 0.057 | 0.057 | 0.1599 | 0.057 | 0.057 | 0.1526 | 0.0644 | 0.057 | 0.1599 | 0.057 | 0.3124 | 2.2585 | 2.9768 | 0.9672 | 0.057 | 0.057 | 0.1935 | 0.057 | 0.057 | 0.1879 | 0.1329 | 0.0902 | 0.3141 | 0.0864 | 0.057 | 2.458 | 2.8762 | 0.6529 | 0.199 | 0.067 | 0.0627 | 0.2911 | 0.3588 | 0.4137 | 0.57 | 0.6139 | 0.5288 | 0.7143 | 0.7374 | 0.704 | 0.1232
Load_TR6_F6_71_dup | customer | 0.156 | 0.2423 | 0.059 | 0.1837 | 0.0867 | 0.1677 | 0.1682 | 0.1725 | 0.1358 | 0.2044 | 0.0659 | 0.123 | 0.1576 | 0.2215 | 0.1422 | 0.4851 | 0.0798 | 0.0654 | 0.2429 | 0.149 | 0.769 | 1.4466 | 0.187 | 0.1947 | 0.1133 | 0.1698 | 0.4289 | 0.16 | 0.1515 | 1.0742 | 0.5369 | 0.4872 | 0.6143 | 0.5038 | 0.5101 | 2.214 | 1.4007 | 0.3184 | 0.7006 | 0.6332 | 1.5705 | 0.3868 | 0.9106 | 0.5368 | 0.8006 | 0.3586 | 0.2631 | 0.1352
Load_TR6_F6_71_tri | customer | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.1403 | 0.0683 | 0.1676 | 0.095 | 0.0603 | 0.2496 | 0.5504 | 1.1195 | 0.4361 | 0.3277 | 0.2575 | 0.4459 | 0.3291 | 0.4991 | 1.1131 | 0.1818 | 1.0446 | 0.2906 | 0.5625 | 0.6073 | 0.7326 | 0.7114 | 0.4819 | 0.8153 | 0.2891 | 0.055 | 0.055 | 0.055
Load_TR6_F6_72 | customer | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.101 | 0.1178 | 0.1178 | 0.1949 | 0.2174 | 0.1874 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053
Load_TR6_F6_72_dup | customer | 0.1099 | 0.0949 | 0.2178 | 0.0765 | 0.1132 | 0.1349 | 0.1716 | 0.101 | 0.1349 | 0.2206 | 0.052 | 0.1278 | 0.2277 | 0.052 | 0.1274 | 0.1424 | 0.1604 | 0.1952 | 0.0742 | 0.1194 | 0.1349 | 0.1349 | 0.1377 | 0.1952 | 0.0842 | 0.2709 | 0.9023 | 0.2073 | 0.4138 | 0.0636 | 0.1377 | 0.2027 | 0.0671 | 0.183 | 0.1726 | 0.1194 | 0.1985 | 0.0897 | 0.198 | 0.1575 | 0.052 | 0.1377 | 0.165 | 0.1905 | 0.052 | 0.2178 | 0.1377 | 0.2027
Load_TR6_F6_72_tri | prosumer | 0.6389 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1474 | 0.0742 | 0.0919 | 0.1201 | 0.3111 | 0.05 | 0.2771 | 0.0695 | 0.0523 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0522 | 0.3299 | 0.2366 | 0.3456 | 0.0616 | 0.0519 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2573 | 0.2749 | 0.3586 | 0.05 | 0.05 | 0.05 | 0.05
Load_TR6_F6_73 | customer | 0.127 | 0.05 | 0.05 | 0.1578 | 0.05 | 0.1424 | 0.0654 | 0.05 | 0.1578 | 0.05 | 0.1424 | 0.2642 | 0.05 | 0.1578 | 0.05 | 0.0808 | 0.127 | 0.3171 | 0.2135 | 0.32 | 0.1935 | 0.5932 | 0.974 | 0.0581 | 1.0127 | 0.3863 | 1.8655 | 1.3416 | 1.436 | 1.7228 | 0.4947 | 0.1266 | 0.2609 | 1.6403 | 1.2782 | 0.2902 | 0.2698 | 0.2529 | 0.1935 | 0.1919 | 0.6105 | 0.515 | 0.6579 | 0.7414 | 0.05 | 0.05 | 0.05 | 0.1424
Load_TR6_F6_73_dup | prosumer | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.0546 | 0.0653 | 0.0968 | 0.1522 | 0.0629 | 0.3598 | 1.6063 | 0.2192 | 0.2314 | 0.1335 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.3376 | 0.4487 | 0.4591 | 0.4416 | 0.7366 | 0.345 | 0.298 | 0.3475 | 0.053 | 0.0627
Load_TR6_F6_73_tri | prosumer | 1.507 | 0.2281 | 0.1389 | 0.1572 | 0.318 | 0.1442 | 0.055 | 0.3078 | 0.0782 | 0.055 | 0.2477 | 0.2275 | 0.2229 | 0.055 | 0.1618 | 0.2241 | 0.1629 | 0.52 | 0.2801 | 0.7356 | 0.5802 | 0.2341 | 0.1758 | 0.2394 | 0.1442 | 0.1847 | 0.2904 | 0.055 | 0.3342 | 0.141 | 0.055 | 0.1779 | 0.2438 | 0.1183 | 0.2831 | 0.258 | 1.6771 | 1.4958 | 0.927 | 0.4027 | 0.3672 | 0.2547 | 0.4035 | 0.4954 | 1.7856 | 1.6459 | 0.3132 | 0.1442
Load_TR6_F6_74 | customer | 0.552 | 0.5336 | 0.0791 | 0.0852 | 0.047 | 0.1639 | 0.1108 | 0.1769 | 0.034 | 0.1249 | 0.1627 | 0.034 | 0.0535 | 0.2342 | 0.034 | 0.1108 | 0.1769 | 0.1162 | 0.1939 | 0.7136 | 1.6256 | 0.1821 | 0.1692 | 0.0511 | 0.1769 | 0.0894 | 0.0878 | 0.1444 | 0.1108 | 0.1769 | 0.034 | 0.0596 | 0.2216 | 0.0405 | 0.0766 | 0.211 | 0.034 | 0.2277 | 0.06 | 0.0917 | 0.196 | 0.0681 | 0.3383 | 0.2615 | 0.4739 | 0.7498 | 0.4101 | 0.5486
Load_TR6_F6_74_dup | prosumer | 0.6829 | 0.1487 | 0.1433 | 0.054 | 0.054 | 0.1433 | 0.054 | 0.0987 | 0.0987 | 0.054 | 0.1433 | 0.054 | 0.1242 | 0.0731 | 0.054 | 0.054 | 0.1709 | 0.054 | 0.054 | 0.1433 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 1.3204 | 1.0702 | 0.3336 | 0.5809 | 0.2345 | 0.504 | 0.5493 | 0.267 | 0.2337 | 0.1306 | 0.1097 | 0.3133 | 0.1131 | 0.0972 | 0.454 | 0.3174 | 0.4346 | 0.7294 | 0.5623 | 0.672 | 0.5912 | 0.5069 | 0.6457
Load_TR6_F6_74_tri | customer | 0.7337 | 0.4382 | 0.8315 | 0.6654 | 0.4899 | 0.5671 | 0.207 | 0.053 | 0.1706 | 0.302 | 0.1636 | 0.2451 | 0.1169 | 0.1636 | 0.246 | 0.1436 | 0.1359 | 0.067 | 0.5709 | 0.0806 | 0.197 | 0.3682 | 0.1509 | 0.2777 | 0.1251 | 0.2653 | 0.2073 | 0.165 | 0.2782 | 0.0824 | 1.5652 | 0.3238 | 0.7983 | 0.714 | 0.3466 | 0.3934 | 0.5162 | 0.1955 | 0.3509 | 0.6999 | 0.9316 | 0.6246 | 0.4953 | 0.4707 | 1.172 | 0.4837 | 0.7627 | 0.162
Load_TR6_F6_75 | prosumer | 0.102 | 0.1336 | 0.1508 | 0.05 | 0.2343 | 0.05 | 0.05 | 0.128 | 0.1563 | 0.05 | 0.1336 | 0.1378 | 0.063 | 0.2083 | 0.076 | 0.0673 | 0.1942 | 0.0728 | 0.128 | 0.2284 | 0.3522 | 0.3094 | 0.3283 | 0.1982 | 0.05 | 0.2127 | 0.0717 | 0.178 | 0.1063 | 0.05 | 0.2343 | 0.05 | 0.1563 | 0.05 | 0.1432 | 0.1411 | 0.05 | 0.204 | 0.0803 | 0.089 | 0.1953 | 0.05 | 0.05 | 0.377 | 0.2299 | 0.2557 | 0.3889 | 0.4533
Load_TR6_F6_75_dup | prosumer | 0.058 | 0.1998 | 0.0762 | 0.1901 | 0.0859 | 0.058 | 0.218 | 0.058 | 0.1139 | 0.0804 | 0.058 | 0.1998 | 0.0762 | 0.1139 | 0.1621 | 0.058 | 0.1589 | 0.1171 | 0.0853 | 0.1125 | 0.1362 | 0.0762 | 0.1551 | 0.1027 | 0.1261 | 0.1499 | 0.108 | 0.0898 | 0.1907 | 0.0853 | 0.0971 | 0.0971 | 0.1964 | 0.3697 | 0.1048 | 0.1815 | 0.1588 | 0.19 | 0.4683 | 0.4608 | 0.6936 | 0.8142 | 0.6415 | 0.5772 | 0.3928 | 0.5212 | 0.1499 | 0.1352
Load_TR6_F6_75_tri | customer | 0.1604 | 0.146 | 0.0993 | 0.2464 | 0.1486 | 0.2464 | 0.05 | 0.0893 | 0.1793 | 0.1764 | 0.1173 | 0.2214 | 0.1062 | 0.05 | 0.2609 | 0.05 | 1.0832 | 0.1787 | 0.1473 | 0.229 | 0.1154 | 0.1622 | 0.05 | 0.1486 | 0.2183 | 0.078 | 0.4863 | 0.1631 | 0.1437 | 1.6547 | 3.442 | 2.5557 | 0.4685 | 0.2429 | 0.2709 | 0.7899 | 0.4621 | 0.3407 | 0.2981 | 0.5661 | 0.3257 | 0.3186 | 0.4927 | 0.3999 | 0.4253 | 0.4266 | 0.05 | 0.05
Load_TR6_F6_76 | prosumer | 0.133 | 0.1726 | 0.1035 | 0.0899 | 0.2089 | 0.1444 | 0.049 | 0.1799 | 0.1735 | 0.1144 | 0.1435 | 0.1103 | 0.0831 | 0.1653 | 0.188 | 0.0926 | 0.1743 | 0.1471 | 0.2206 | 0.1971 | 0.3999 | 0.0776 | 0.1448 | 0.2017 | 0.4221 | 0.7898 | 0.1798 | 0.3244 | 0.0914 | 0.8639 | 0.494 | 0.2372 | 0.3199 | 0.0495 | 0.1368 | 0.2876 | 0.1581 | 1.5365 | 0.9181 | 0.1858 | 0.3383 | 0.3894 | 0.5756 | 0.768 | 1.7014 | 0.7933 | 0.263 | 0.0563
Load_TR6_F6_76_dup | customer | 0.1229 | 0.1048 | 0.2636 | 0.1733 | 0.0946 | 0.3423 | 0.051 | 0.1986 | 0.2383 | 0.0731 | 0.3254 | 0.0894 | 0.2783 | 0.051 | 0.305 | 0.5349 | 0.0803 | 0.4225 | 0.051 | 0.1342 | 0.3027 | 0.051 | 0.213 | 0.1731 | 0.1018 | 0.228 | 0.2307 | 0.1648 | 0.1763 | 0.1887 | 0.1656 | 0.1303 | 0.1848 | 0.252 | 0.08 | 0.1683 | 0.2396 | 0.051 | 0.2464 | 0.365 | 0.3026 | 0.5671 | 0.3052 | 0.5453 | 0.6002 | 0.7617 | 0.6653 | 0.1586
Load_TR6_F6_76_tri | prosumer | 0.1682 | 0.2022 | 0.054 | 0.2624 | 0.0859 | 0.5013 | 0.5032 | 0.229 | 0.154 | 0.1943 | 0.054 | 0.256 | 0.0923 | 0.054 | 0.2369 | 0.1114 | 0.1915 | 0.1568 | 0.0581 | 0.2657 | 0.0826 | 0.1178 | 0.2428 | 0.054 | 0.2425 | 0.109 | 0.0773 | 0.285 | 0.0595 | 0.2708 | 0.0939 | 0.143 | 0.2666 | 0.1469 | 0.3544 | 0.0599 | 0.3068 | 1.0344 | 0.3307 | 0.737 | 0.5354 | 0.5226 | 0.9581 | 1.6517 | 0.4325 | 0.4977 | 0.1752 | 0.1303
Load_TR6_F6_77 | customer | 0.7686 | 0.1095 | 0.2172 | 0.1095 | 0.033 | 0.1095 | 0.0581 | 0.1921 | 0.0925 | 0.2091 | 0.0581 | 0.1095 | 0.2172 | 0.0585 | 0.2514 | 0.0497 | 0.21 | 0.2476 | 0.0925 | 0.184 | 0.1512 | 0.1252 | 0.1335 | 0.1346 | 0.2214 | 0.3324 | 0.4193 | 0.1346 | 0.033 | 0.0879 | 0.379 | 0.0614 | 0.2287 | 0.5115 | 0.2686 | 0.2853 | 0.0986 | 0.0615 | 0.5209 | 1.4391 | 1.3432 | 0.4148 | 0.2032 | 0.4023 | 0.2672 | 0.5403 | 0.5171 | 0.168
Load_TR6_F6_77_dup | prosumer | 0.2067 | 0.1135 | 0.0562 | 0.2272 | 0.1012 | 0.0848 | 0.2436 | 0.048 | 0.048 | 0.2067 | 0.048 | 0.093 | 0.2282 | 0.0552 | 0.1418 | 0.1129 | 0.1219 | 0.0628 | 0.2538 | 0.1077 | 0.0637 | 0.0985 | 0.2067 | 0.048 | 0.1076 | 0.233 | 0.0954 | 0.048 | 0.2851 | 0.048 | 0.1217 | 0.2067 | 0.048 | 0.1866 | 0.1418 | 0.0573 | 0.2612 | 1.5529 | 1.5819 | 0.7079 | 0.3336 | 0.4709 | 1.0342 | 1.0734 | 0.4469 | 0.687 | 0.9072 | 1.0774
Load_TR6_F6_77_tri | prosumer | 0.3697 | 0.049 | 0.1196 | 0.1776 | 0.0866 | 0.2106 | 0.1243 | 0.1479 | 0.118 | 0.1251 | 0.1408 | 0.1808 | 0.1542 | 0.0498 | 1.1303 | 0.2848 | 0.2394 | 2.6547 | 2.7219 | 1.0703 | 1.3337 | 0.2487 | 0.1682 | 0.1479 | 0.4058 | 0.0747 | 0.3006 | 1.2539 | 0.1659 | 0.1245 | 0.2083 | 1.0122 | 0.2064 | 0.5365 | 1.2464 | 0.0623 | 0.3227 | 0.3625 | 0.0985 | 0.2618 | 0.3077 | 0.3057 | 0.1806 | 0.5383 | 0.587 | 0.4858 | 0.653 | 0.049
Load_TR6_F6_78 | prosumer | 0.2006 | 0.044 | 0.044 | 0.1827 | 0.174 | 0.044 | 0.2332 | 0.1234 | 0.1428 | 0.055 | 0.2962 | 0.0605 | 0.2563 | 0.1003 | 0.044 | 0.1538 | 0.2029 | 0.0879 | 0.3083 | 0.0657 | 0.1538 | 0.0615 | 0.5036 | 0.054 | 0.044 | 0.1538 | 0.3065 | 0.1355 | 0.069 | 0.1758 | 2.4487 | 0.1822 | 1.4102 | 1.289 | 0.0851 | 0.4381 | 0.3872 | 2.4522 | 0.1038 | 0.443 | 0.3028 | 0.4099 | 0.3691 | 0.2709 | 0.179 | 0.4276 | 0.3801 | 0.187
Load_TR6_F6_78_dup | customer | 0.163 | 0.05 | 0.2275 | 0.05 | 0.2033 | 0.0742 | 0.0823 | 0.1952 | 0.05 | 0.05 | 0.0742 | 0.2033 | 0.05 | 0.2275 | 0.05 | 0.1388 | 0.148 | 0.05 | 0.2275 | 0.2784 | 0.171 | 0.1255 | 0.062 | 1.3843 | 0.2022 | 1.5182 | 0.3755 | 0.4601 | 0.3149 | 0.1772 | 0.1193 | 0.0661 | 0.2114 | 0.05 | 0.4362 | 0.0818 | 0.5552 | 0.3192 | 0.12 | 0.3956 | 0.3684 | 0.577 | 0.7043 | 0.3784 | 0.5726 | 0.1673 | 0.1549 | 0.1226
Load_TR6_F6_78_tri | customer | 0.058 | 0.2545 | 0.137 | 0.058 | 0.2518 | 0.1397 | 0.058 | 0.193 | 0.1985 | 0.1709 | 0.058 | 0.1539 | 0.1858 | 0.1888 | 0.0919 | 0.2545 | 0.137 | 0.1745 | 0.217 | 0.058 | 0.4455 | 0.3984 | 0.529 | 0.2712 | 0.2841 | 1.0891 | 0.4307 | 0.2668 | 0.3747 | 0.1401 | 0.3792 | 0.2363 | 0.058 | 0.1923 | 0.1993 | 0.1257 | 0.2658 | 0.0749 | 0.2944 | 0.0802 | 0.4474 | 0.2472 | 0.633 | 0.2734 | 0.5181 | 0.5824 | 0.7108 | 0.5489
Load_TR6_F6_79 | prosumer | 0.2426 | 0.3286 | 0.3281 | 0.2313 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.1846 | 0.2832 | 0.1825 | 0.692 | 0.7799 | 0.2106 | 0.167 | 0.2106 | 0.1887 | 0.3292 | 1.1287 | 0.1342 | 0.1301 | 0.0705 | 0.0705 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.2827 | 0.1486 | 0.0755 | 0.171 | 0.1316 | 0.1852 | 0.1421 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Load_TR6_F6_79_dup | prosumer | 0.1238 | 0.035 | 0.035 | 0.2051 | 0.0885 | 0.0721 | 0.2215 | 0.035 | 0.035 | 0.035 | 0.191 | 0.1026 | 0.035 | 0.2385 | 0.0551 | 0.2359 | 1.1403 | 0.1932 | 0.3129 | 0.2945 | 0.1494 | 0.1631 | 0.0553 | 0.1984 | 0.035 | 0.1665 | 0.1142 | 0.4772 | 0.3645 | 0.1417 | 1.4256 | 1.0311 | 0.2018 | 0.0919 | 0.1613 | 0.0756 | 0.5024 | 0.2269 | 0.2199 | 0.4072 | 0.3589 | 0.391 | 0.035 | 0.1145 | 0.4529 | 0.1593 | 0.139 | 0.1546
Load_TR6_F6_79_tri | prosumer | 0.5746 | 0.5176 | 2.1448 | 0.5845 | 0.6833 | 0.4114 | 0.048 | 0.048 | 0.1128 | 0.101 | 0.1128 | 0.101 | 0.101 | 0.1128 | 0.0657 | 0.1481 | 0.2137 | 1.2125 | 0.3951 | 0.2607 | 0.4337 | 0.2745 | 0.4171 | 0.6796 | 0.2715 | 0.4233 | 0.2255 | 1.333 | 0.628 | 0.1127 | 0.2006 | 0.0715 | 0.1384 | 0.1649 | 0.048 | 0.4418 | 0.048 | 0.1422 | 0.0716 | 0.048 | 0.048 | 0.048 | 0.1658 | 0.048 | 0.3217 | 0.048 | 0.048 | 0.0833
Load_TR6_F6_7_dup | prosumer | 0.055 | 0.3199 | 0.0617 | 0.1259 | 0.3515 | 0.2803 | 0.3727 | 1.3461 | 0.0505 | 0.1046 | 0.037 | 0.037 | 0.1181 | 0.037 | 0.1181 | 0.1474 | 0.3387 | 0.1699 | 1.7919 | 0.9711 | 0.3198 | 0.0902 | 0.1181 | 0.037 | 0.082 | 0.1112 | 0.2524 | 0.0828 | 1.4081 | 0.3186 | 0.3844 | 0.037 | 0.4687 | 0.2444 | 0.2364 | 0.1854 | 0.1782 | 0.1437 | 0.2281 | 0.398 | 0.6401 | 0.7186 | 0.4868 | 0.7422 | 1.3567 | 2.1454 | 0.845 | 0.6389
Load_TR6_F6_7_tri | prosumer | 0.043 | 0.043 | 0.3915 | 0.2192 | 0.2246 | 0.1182 | 0.043 | 0.043 | 0.1182 | 0.043 | 0.0848 | 0.0764 | 0.043 | 0.1182 | 0.043 | 0.0973 | 0.0639 | 0.1566 | 0.9703 | 0.2427 | 0.1873 | 0.2673 | 0.3341 | 1.0896 | 0.4457 | 0.6726 | 1.4895 | 2.0191 | 3.3654 | 1.9333 | 0.0764 | 0.0485 | 0.2104 | 0.1393 | 0.2109 | 0.7416 | 1.9543 | 0.3796 | 0.1343 | 1.1383 | 0.2346 | 0.2736 | 0.3935 | 0.4165 | 0.3473 | 0.1182 | 0.043 | 0.043
Load_TR6_F6_8 | customer | 0.3078 | 0.6133 | 0.1305 | 0.1231 | 0.2202 | 0.1643 | 0.1467 | 0.3208 | 0.1176 | 0.235 | 0.155 | 0.1176 | 0.2533 | 0.2013 | 0.1872 | 0.3003 | 0.2046 | 0.2656 | 0.2848 | 1.0643 | 0.28 | 0.4218 | 0.6082 | 0.3813 | 0.125 | 0.1683 | 0.0885 | 0.2562 | 0.0604 | 0.1667 | 0.2879 | 0.1176 | 0.2183 | 0.1716 | 0.1899 | 0.1569 | 0.1608 | 0.1602 | 0.3485 | 0.053 | 0.2048 | 0.2498 | 0.0961 | 0.3437 | 0.1195 | 0.1166 | 0.2904 | 0.1265
Load_TR6_F6_80 | prosumer | 0.1289 | 0.1534 | 0.1549 | 0.108 | 0.1594 | 0.0722 | 0.2362 | 0.0619 | 0.2334 | 0.044 | 0.134 | 0.1744 | 0.0516 | 0.159 | 0.1442 | 0.1296 | 0.2367 | 0.2346 | 1.9013 | 3.0874 | 1.3577 | 0.9339 | 0.5932 | 0.1413 | 0.1134 | 0.0842 | 0.1418 | 0.134 | 0.3061 | 0.2381 | 0.206 | 0.2978 | 0.0465 | 0.7473 | 0.7334 | 0.2159 | 0.0824 | 0.4366 | 0.2262 | 0.294 | 0.3739 | 0.346 | 0.3132 | 0.2096 | 0.6818 | 0.3797 | 0.4277 | 0.3418
Load_TR6_F6_80_dup | prosumer | 0.2316 | 0.056 | 0.1677 | 0.1198 | 0.056 | 0.1518 | 0.1358 | 0.056 | 0.1677 | 0.1198 | 0.056 | 0.064 | 0.2236 | 0.056 | 0.056 | 0.1198 | 0.1677 | 0.056 | 0.4553 | 0.5333 | 0.3067 | 0.4007 | 0.2209 | 0.4955 | 0.4875 | 0.236 | 0.2565 | 0.3141 | 0.083 | 0.2411 | 0.0743 | 0.226 | 0.5896 | 0.6778 | 2.1056 | 3.097 | 2.6224 | 0.3382 | 0.1717 | 0.2164 | 1.0067 | 3.0857 | 2.4753 | 0.4186 | 0.4417 | 0.1706 | 0.056 | 0.056
Load_TR6_F6_80_tri | customer | 0.2139 | 0.4593 | 0.055 | 0.1638 | 0.055 | 0.055 | 0.125 | 0.0939 | 0.055 | 0.1638 | 0.055 | 0.1405 | 0.0783 | 0.055 | 0.055 | 0.1638 | 0.055 | 0.125 | 0.2254 | 0.055 | 0.1016 | 0.1172 | 0.055 | 0.2076 | 0.1865 | 0.1966 | 1.4683 | 0.7609 | 0.2884 | 0.0939 | 0.055 | 0.2882 | 0.4327 | 0.3842 | 0.4059 | 0.2594 | 0.5426 | 0.2689 | 0.2141 | 0.5307 | 0.9763 | 0.914 | 0.7853 | 0.7762 | 0.7911 | 0.6871 | 0.0628 | 0.156
Load_TR6_F6_81 | prosumer | 0.488 | 0.3739 | 0.2088 | 0.054 | 0.133 | 0.2088 | 0.1286 | 0.1639 | 0.1603 | 0.0759 | 0.2088 | 0.133 | 0.1384 | 0.1244 | 0.054 | 0.0962 | 0.2455 | 0.054 | 0.257 | 0.0847 | 0.054 | 0.2666 | 0.0751 | 0.163 | 0.1787 | 0.3201 | 0.2447 | 0.0759 | 0.1314 | 0.1489 | 0.1233 | 0.1786 | 0.22 | 0.1155 | 0.4894 | 0.3115 | 0.0856 | 0.1883 | 0.1959 | 0.0821 | 0.287 | 0.4311 | 0.112 | 0.1594 | 0.1736 | 0.0715 | 0.2421 | 0.0821
Load_TR6_F6_81_dup | prosumer | 0.3117 | 0.2526 | 0.055 | 0.055 | 0.2256 | 0.0819 | 0.0909 | 0.2167 | 0.055 | 0.2821 | 0.1089 | 0.055 | 0.2526 | 0.055 | 0.107 | 0.2223 | 0.6001 | 0.2823 | 0.2796 | 1.4458 | 0.2121 | 0.4856 | 0.3697 | 0.5585 | 0.2509 | 0.354 | 0.9902 | 1.3454 | 1.4232 | 0.1392 | 0.255 | 0.1089 | 0.0999 | 0.2077 | 0.055 | 0.3812 | 1.0898 | 0.0825 | 0.1539 | 0.4463 | 0.7194 | 0.7874 | 0.7894 | 0.8739 | 0.568 | 0.9417 | 0.6071 | 0.1179
Load_TR6_F6_81_tri | prosumer | 0.096 | 0.2337 | 0.033 | 0.1738 | 0.1436 | 0.1413 | 0.0778 | 0.1011 | 0.2286 | 0.033 | 0.1144 | 0.2153 | 0.033 | 0.1738 | 0.0541 | 0.2451 | 0.3517 | 0.928 | 0.033 | 0.2967 | 0.057 | 0.2646 | 0.1221 | 0.092 | 0.2968 | 0.1031 | 0.1234 | 0.1731 | 0.1605 | 0.129 | 0.1454 | 0.0966 | 0.4575 | 0.2244 | 0.36 | 0.3599 | 0.6117 | 1.0944 | 0.3033 | 0.5384 | 0.2263 | 0.0586 | 0.1482 | 0.033 | 0.1559 | 0.1674 | 0.0394 | 0.2071
Load_TR6_F6_82 | prosumer | 0.1868 | 0.183 | 0.05 | 0.2945 | 0.5435 | 0.152 | 0.2099 | 0.0781 | 0.1868 | 0.1344 | 0.1054 | 0.0681 | 0.2568 | 0.0574 | 0.094 | 0.2273 | 0.05 | 0.18 | 0.1993 | 0.098 | 0.1669 | 0.1063 | 0.05 | 0.2048 | 0.1165 | 0.1696 | 0.1406 | 1.3927 | 0.2237 | 0.182 | 0.4429 | 0.0732 | 0.2453 | 1.2111 | 0.3538 | 0.2055 | 0.2369 | 0.2057 | 0.1162 | 0.5075 | 0.3718 | 0.3054 | 0.5209 | 0.561 | 0.7387 | 0.0574 | 0.2079 | 0.1133
Load_TR6_F6_82_dup | customer | 0.2103 | 0.1774 | 0.2108 | 0.1261 | 0.2925 | 0.1164 | 0.0685 | 0.3653 | 0.06 | 0.1867 | 0.2056 | 0.1186 | 0.2575 | 0.1094 | 0.1104 | 0.1932 | 0.1243 | 0.1867 | 0.1422 | 0.2831 | 0.1261 | 0.13 | 0.2953 | 0.0708 | 0.2221 | 0.2032 | 2.087 | 0.4736 | 0.1371 | 0.195 | 0.1591 | 0.4045 | 0.5915 | 0.206 | 0.4661 | 0.1915 | 0.1739 | 0.2349 | 0.1261 | 0.1649 | 0.22 | 0.0924 | 0.2318 | 0.1935 | 0.0761 | 0.2818 | 0.1416 | 0.2441
Load_TR6_F6_82_tri | customer | 0.3816 | 0.725 | 0.6283 | 0.1576 | 0.1284 | 0.3015 | 0.0735 | 0.2469 | 0.2035 | 0.2087 | 0.0912 | 0.3218 | 0.1286 | 0.1898 | 0.1485 | 0.2168 | 0.1627 | 0.1512 | 0.261 | 0.1622 | 0.1826 | 0.2808 | 0.306 | 0.2001 | 0.053 | 0.392 | 0.0585 | 0.114 | 0.2338 | 0.1839 | 0.2023 | 0.1212 | 0.3292 | 0.0694 | 0.2815 | 0.1689 | 0.053 | 0.2789 | 0.1715 | 0.1077 | 0.2718 | 0.1239 | 0.4095 | 0.7198 | 0.7026 | 0.7129 | 0.2011 | 0.1994
Load_TR6_F6_83 | prosumer | 0.5848 | 0.6175 | 0.0481 | 0.1145 | 0.044 | 0.1186 | 0.044 | 0.1186 | 0.044 | 0.0937 | 0.0689 | 0.0937 | 0.0689 | 0.044 | 0.1186 | 0.044 | 0.1186 | 0.044 | 0.1186 | 0.044 | 0.044 | 0.1166 | 0.0891 | 0.045 | 0.054 | 0.1288 | 0.0564 | 0.0678 | 0.1767 | 0.044 | 0.1186 | 0.044 | 0.277 | 0.095 | 0.087 | 0.7807 | 0.7965 | 0.7302 | 0.3783 | 0.1873 | 0.3354 | 0.2381 | 0.1817 | 0.3686 | 0.2979 | 0.2712 | 0.3179 | 0.044
Load_TR6_F6_83_dup | customer | 0.3164 | 0.1479 | 0.046 | 0.1275 | 0.2323 | 0.046 | 0.129 | 0.2309 | 0.046 | 0.1986 | 0.1631 | 0.1371 | 0.1667 | 0.046 | 0.1479 | 0.129 | 0.2207 | 0.0639 | 0.168 | 0.595 | 0.6125 | 0.4441 | 0.4577 | 0.6638 | 0.1693 | 0.2236 | 0.139 | 0.2226 | 0.1731 | 0.0712 | 0.4136 | 0.1918 | 0.3458 | 0.4727 | 0.1512 | 0.296 | 0.2229 | 0.1699 | 0.5608 | 0.3071 | 0.3958 | 0.4561 | 0.4361 | 0.3612 | 0.6015 | 0.4034 | 0.2204 | 0.4602
Load_TR6_F6_83_tri | prosumer | 0.0605 | 0.1848 | 0.1348 | 0.1615 | 0.1491 | 0.2267 | 0.0693 | 0.2086 | 0.0428 | 0.1047 | 0.1074 | 0.426 | 0.0704 | 0.1956 | 1.0388 | 1.6863 | 1.432 | 0.1645 | 0.2344 | 0.0389 | 0.2629 | 0.1129 | 0.034 | 0.1645 | 0.1981 | 0.1383 | 0.1835 | 0.2346 | 0.1655 | 0.1942 | 0.187 | 0.1526 | 0.2295 | 0.0611 | 0.3527 | 0.13 | 0.1454 | 0.1831 | 0.1771 | 0.1467 | 0.1496 | 0.1019 | 0.2299 | 0.078 | 0.2923 | 0.4951 | 0.0914 | 0.0518
Load_TR6_F6_8_dup | prosumer | 0.3379 | 0.052 | 0.289 | 0.1077 | 0.1016 | 0.2541 | 0.093 | 0.1551 | 0.2416 | 0.052 | 0.2277 | 0.169 | 0.2415 | 0.2745 | 0.3316 | 0.4695 | 0.3233 | 0.2317 | 0.3228 | 0.3136 | 0.1634 | 0.9055 | 0.6534 | 0.8715 | 0.9121 | 0.1922 | 0.2252 | 0.0794 | 0.052 | 0.2079 | 0.0999 | 0.1409 | 0.1938 | 0.203 | 0.052 | 0.1683 | 0.0725 | 0.6285 | 1.0438 | 0.3596 | 0.2108 | 0.1371 | 0.1136 | 0.1272 | 0.2079 | 0.1136 | 0.1272 | 0.1792
Load_TR6_F6_8_tri | prosumer | 0.084 | 0.1506 | 0.044 | 0.1373 | 0.0973 | 0.044 | 0.1106 | 0.1239 | 0.044 | 0.1573 | 0.0773 | 0.044 | 0.1906 | 0.044 | 0.064 | 0.1706 | 0.044 | 0.044 | 0.1944 | 0.6506 | 0.7751 | 0.1239 | 0.0533 | 0.1579 | 0.1029 | 0.1881 | 0.7824 | 0.4534 | 0.3136 | 0.0515 | 0.1053 | 0.2228 | 0.044 | 0.2368 | 0.7344 | 2.5742 | 0.7202 | 0.0742 | 0.2181 | 1.3551 | 0.044 | 0.044 | 0.1439 | 0.0906 | 0.104 | 0.1306 | 0.044 | 0.1706
Load_TR6_F6_9 | customer | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.1076 | 0.052 | 0.052 | 0.1653 | 0.1311 | 0.096 | 0.052 | 0.052 | 0.052 | 0.064 | 0.1397 | 0.1592 | 0.054 | 0.4435 | 0.0547 | 0.062 | 0.099 | 0.1939 | 0.2703 | 0.1484 | 0.0915 | 0.2688 | 0.123 | 0.1105 | 0.2194 | 0.4573 | 0.604 | 0.4751 | 0.6807 | 0.8292 | 0.8359 | 0.618 | 0.4633 | 0.4774
Load_TR6_F6_9_dup | customer | 0.2064 | 0.1245 | 0.1582 | 0.1418 | 0.134 | 0.1737 | 0.109 | 0.2411 | 0.0897 | 0.1005 | 0.2304 | 0.055 | 0.055 | 0.055 | 0.2759 | 0.055 | 0.158 | 0.1728 | 0.1245 | 0.0756 | 0.2398 | 0.0704 | 0.2406 | 0.0902 | 0.109 | 0.1737 | 0.1032 | 0.1245 | 0.2064 | 0.055 | 0.1245 | 0.2064 | 0.055 | 0.207 | 0.1238 | 0.055 | 0.0589 | 0.1757 | 0.6901 | 0.4409 | 0.903 | 0.3902 | 0.5311 | 0.5967 | 0.4265 | 1.099 | 0.4718 | 0.7836
Load_TR6_F6_9_tri | customer | 0.2522 | 0.057 | 0.2256 | 0.0836 | 0.128 | 0.1812 | 0.0747 | 0.2344 | 0.057 | 0.2522 | 0.057 | 0.057 | 0.1901 | 1.2204 | 0.2301 | 0.1812 | 0.108 | 0.5179 | 0.1754 | 0.1589 | 0.0699 | 1.0475 | 0.8288 | 1.9315 | 0.4225 | 0.5142 | 0.1377 | 0.1635 | 0.1457 | 0.057 | 0.2256 | 0.0836 | 0.057 | 0.2078 | 0.2264 | 0.1942 | 0.4163 | 0.6415 | 0.3353 | 0.3832 | 0.3797 | 0.6907 | 0.4104 | 0.992 | 0.5511 | 0.818 | 0.6639 | 0.3058

## 5. Raw batt charge
Raw batt charge
Verbatim copy of Charge_kW (TR6_analysis_data.xlsx). One row per half-hour, one column per battery (kW).
period | hour | BES_TR6_one38_B | BES_TR6_one242_B | BES_TR6_one252_C | BES_TR6_one260_C | BES_TR6_one280_A | BES_TR6_one287_B | BES_TR6_one299_B | BES_TR6_one313_A | BES_TR6_one320_B | BES_TR6_one346_C | BES_TR6_one416_C | BES_TR6_one446_B | BES_TR6_one477_A | BES_TR6_one480_A | BES_TR6_one482_B | BES_TR6_one521_C | BES_TR6_one537_A | BES_TR6_one559_C | BES_TR6_one570_B | BES_TR6_one590_A | BES_TR6_one605_A | BES_TR6_one614_B | BES_TR6_one73_A | BES_TR6_one76_A | BES_TR6_one137_A | BES_TR6_one176_A | BES_TR6_four149_B | BES_TR6_four163_C | BES_TR6_four171_A | BES_TR6_four184_B | BES_TR6_four200_A | BES_TR6_four239_A | BES_TR6_four259_B | BES_TR6_four288_B | BES_TR6_four289_B | BES_TR6_four301_C | BES_TR6_four317_B | BES_TR6_four354_B | BES_TR6_four358_C | BES_TR6_four65_B | BES_TR6_four384_B | BES_TR6_four385_A | BES_TR6_four396_B | BES_TR6_four423_C | BES_TR6_four446_B | BES_TR6_four451_C | BES_TR6_four466_C | BES_TR6_four558_C | BES_TR6_four70_B | BES_TR6_four573_A | BES_TR6_four664_A | BES_TR6_four675_C | BES_TR6_four710_C | BES_TR6_four727_B | BES_TR6_four732_B | BES_TR6_four818_B | BES_TR6_four821_A | BES_TR6_four832_A | BES_TR6_four840_A | BES_TR6_four957_A | BES_TR6_four978_A | BES_TR6_four988_A | BES_TR6_four1013_B | BES_TR6_four1027_A | BES_TR6_four1063_C | BES_TR6_four1103_C | BES_TR6_four1140_A | BES_TR6_four1152_B | BES_TR6_four1220_C | BES_TR6_five147_dup_C | BES_TR6_five149_A | BES_TR6_five168_A | BES_TR6_five170_A | BES_TR6_five170_dup_A | BES_TR6_five186_C | BES_TR6_five186_dup_C | BES_TR6_five194_C | BES_TR6_five199_dup_C | BES_TR6_five67_C | BES_TR6_five67_dup_C | BES_TR6_five223_A | BES_TR6_five223_dup_A | BES_TR6_five242_dup_A | BES_TR6_five243_B | BES_TR6_five243_dup_B | BES_TR6_five284_C | BES_TR6_five284_dup_C | BES_TR6_five285_B | BES_TR6_five285_dup_B | BES_TR6_five303_B | BES_TR6_five78_A | BES_TR6_five78_dup_A | BES_TR6_five394_C | BES_TR6_five394_dup_C | BES_TR6_five421_A | BES_TR6_five445_dup_C | BES_TR6_five457_B | BES_TR6_five494_B | BES_TR6_five499_B | BES_TR6_five92_dup_A | BES_TR6_five512_dup_A | BES_TR6_five513_B | BES_TR6_five513_dup_B | BES_TR6_five520_C | BES_TR6_five520_dup_C | BES_TR6_five537_C | BES_TR6_five537_dup_C | BES_TR6_five551_C | BES_TR6_five585_A | BES_TR6_five588_dup_A | BES_TR6_five108_dup_B | BES_TR6_five649_A | BES_TR6_five663_C | BES_TR6_five663_dup_C | BES_TR6_five670_dup_C | BES_TR6_five704_A | BES_TR6_five733_C | BES_TR6_five735_A | BES_TR6_five735_dup_A | BES_TR6_five748_B | BES_TR6_five117_dup_B | BES_TR6_five750_B | BES_TR6_five778_dup_B | BES_TR6_five793_A | BES_TR6_five881_C | BES_TR6_five905_B | BES_TR6_five118_B | BES_TR6_five118_dup_B | BES_TR6_five123_B | BES_TR6_five123_dup_B | BES_TR6_five129_C | BES_TR6_six64_A | BES_TR6_six64_dup_A | BES_TR6_six154_dup_C | BES_TR6_six154_tri_C | BES_TR6_six173_C | BES_TR6_six173_dup_C | BES_TR6_six191_B | BES_TR6_six191_dup_B | BES_TR6_six203_A | BES_TR6_six203_dup_A | BES_TR6_six203_tri_A | BES_TR6_six232_C | BES_TR6_six238_A | BES_TR6_six238_tri_A | BES_TR6_six249_dup_B | BES_TR6_six269_tri_C | BES_TR6_six68_C | BES_TR6_six68_dup_C | BES_TR6_six68_tri_C | BES_TR6_six289_C | BES_TR6_six289_tri_C | BES_TR6_six317_dup_C | BES_TR6_six317_tri_C | BES_TR6_six326_tri_A | BES_TR6_six329_A | BES_TR6_six329_tri_A | BES_TR6_six342_A | BES_TR6_six349_dup_A | BES_TR6_six349_tri_A | BES_TR6_six350_dup_B | BES_TR6_six350_tri_B | BES_TR6_six362_tri_C | BES_TR6_six365_tri_C | BES_TR6_six378_dup_A | BES_TR6_six378_tri_A | BES_TR6_six75_tri_A | BES_TR6_six385_B | BES_TR6_six385_tri_B | BES_TR6_six387_dup_A | BES_TR6_six392_C | BES_TR6_six410_tri_A | BES_TR6_six431_dup_C | BES_TR6_six431_tri_C | BES_TR6_six441_dup_A | BES_TR6_six441_tri_A | BES_TR6_six484_dup_B | BES_TR6_six501_dup_A | BES_TR6_six512_dup_B | BES_TR6_six512_tri_B | BES_TR6_six82_A | BES_TR6_six82_dup_A | BES_TR6_six523_dup_C | BES_TR6_six571_C | BES_TR6_six571_tri_C | BES_TR6_six583_dup_A | BES_TR6_six591_C | BES_TR6_six591_dup_C | BES_TR6_six595_tri_B | BES_TR6_six625_A | BES_TR6_six643_A | BES_TR6_six646_B | BES_TR6_six646_dup_B | BES_TR6_six651_dup_C | BES_TR6_six651_tri_C | BES_TR6_six87_dup_A | BES_TR6_six652_dup_A | BES_TR6_six652_tri_A | BES_TR6_six665_tri_B | BES_TR6_six667_A | BES_TR6_six667_tri_A | BES_TR6_six699_C | BES_TR6_six699_dup_C | BES_TR6_six699_tri_C | BES_TR6_six721_A | BES_TR6_six723_B | BES_TR6_six723_dup_B | BES_TR6_six740_A | BES_TR6_six740_dup_A | BES_TR6_six740_tri_A | BES_TR6_six758_B | BES_TR6_six758_dup_B | BES_TR6_six784_dup_B | BES_TR6_six784_tri_B | BES_TR6_six90_B | BES_TR6_six90_dup_B | BES_TR6_six799_tri_B | BES_TR6_six801_C | BES_TR6_six801_dup_C | BES_TR6_six801_tri_C | BES_TR6_six807_A | BES_TR6_six844_C | BES_TR6_six844_dup_C | BES_TR6_six844_tri_C | BES_TR6_six852_B | BES_TR6_six860_C | BES_TR6_six860_dup_C | BES_TR6_six869_C | BES_TR6_six869_tri_C | BES_TR6_six885_A | BES_TR6_six885_tri_A | BES_TR6_six894_B | BES_TR6_six894_tri_B | BES_TR6_six105_dup_A | BES_TR6_six105_tri_A | BES_TR6_six914_A | BES_TR6_six914_tri_A | BES_TR6_six921_B | BES_TR6_six929_tri_A | BES_TR6_six938_dup_A | BES_TR6_six938_tri_A | BES_TR6_six945_dup_C | BES_TR6_six952_A | BES_TR6_six952_dup_A | BES_TR6_six967_B | BES_TR6_six967_tri_B | BES_TR6_six974_dup_C | BES_TR6_six974_tri_C | BES_TR6_six979_A | BES_TR6_six990_B | BES_TR6_six990_dup_B | BES_TR6_six990_tri_B | BES_TR6_six111_dup_C | BES_TR6_six111_tri_C | BES_TR6_six1006_C | BES_TR6_six1006_dup_C | BES_TR6_six1020_A | BES_TR6_six1020_dup_A | BES_TR6_six1020_tri_A | BES_TR6_six1025_B | BES_TR6_six1064_C | BES_TR6_six1064_tri_C
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011 | 0.003 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4.5 | 0 | 0.116 | 0 | 0 | 0.001 | 0.053 | 0 | 0 | 0.082 | 0.108 | 0.175 | 0.145 | 0 | 0.047 | 0.073 | 0 | 0.145 | 0.116 | 0.072 | 0 | 0.063 | 0.093 | 0.068 | 0.198 | 0.107 | 0.019 | 0 | 0 | 0.127 | 0.124 | 0.092 | 0.073 | 0.066 | 0 | 0.039 | 0.127 | 0.094 | 0.155 | 0.122 | 0.119 | 0.061 | 0.092 | 0.035 | 0.067 | 0.105 | 0 | 0.033 | 0 | 0.182 | 0 | 0 | 0.078 | 0.183 | 0.118 | 0.032 | 0.055 | 0.097 | 0.071 | 0.06 | 0 | 0.151 | 0.073 | 0 | 0 | 0 | 0.038 | 0 | 0.037 | 0.202 | 0.05 | 0 | 0.175 | 0.016 | 0.036 | 0.047 | 0.04 | 0.071 | 0.092 | 0.12 | 0.183 | 0.032 | 0.175 | 0.053 | 0 | 0.059 | 0.154 | 0.137 | 0.008 | 0.062 | 0.133 | 0 | 0.186 | 0.181 | 0.071 | 0.135 | 0.09 | 0.118 | 0 | 0.041 | 0.155 | 0.017 | 0 | 0.023 | 0.024 | 0.082 | 0.056 | 0.156 | 0.118 | 0.18 | 0 | 0 | 0 | 0.163 | 0.096 | 0.137 | 0.058 | 0 | 0 | 0 | 0.074 | 0.185 | 0 | 0.058 | 0.068 | 0.118 | 0.094 | 0 | 0 | 0 | 0.095 | 0.07 | 0.148 | 0.023 | 0.034 | 0.036 | 0.098 | 0.072 | 0.103 | 0 | 0.184 | 0.124 | 0.132 | 0.177 | 0.123 | 0.033 | 0.175 | 0.069 | 0.12 | 0.193 | 0 | 0.177 | 0.105 | 0.089 | 0.088 | 0 | 0.026 | 0 | 0 | 0 | 0 | 0.132 | 0 | 0 | 0.055 | 0 | 0 | 0.066 | 0 | 0 | 0 | 0.001 | 0.118 | 0.11 | 0.039 | 0.145 | 0.156 | 0.178 | 0 | 0.044 | 0.183 | 0.166 | 0.003 | 0.179 | 0.187 | 0 | 0.128 | 0.013 | 0 | 0.025 | 0.103 | 0 | 0.064 | 0 | 0.021 | 0 | 0.142 | 0.084 | 0 | 0.182 | 0.184 | 0.104 | 0.079 | 0.101 | 0.171 | 0.06 | 0 | 0.031 | 0 | 0 | 0.097 | 0 | 0.122 | 0.142 | 0.133 | 0.124 | 0.035 | 0.091 | 0.007 | 0 | 0 | 0.109 | 0.101 | 0.055 | 0.078 | 0.094 | 0.029 | 0.113 | 0.035 | 0.059 | 0.042 | 0.192 | 0.006 | 0.121 | 0.128 | 0.19 | 0 | 0.074 | 0.073 | 0.183 | 0.18 | 0.061 | 0.091 | 0.037 | 0.094 | 0.031 | 0 | 0 | 0 | 0.119 | 0.178 | 0.198 | 0.073 | 0.181 | 0 | 0.159 | 0 | 0.157 | 0 | 0.2 | 0.098 | 0.081 | 0.012
11 | 5 | 0.286 | 0.294 | 0.105 | 0.081 | 0.126 | 0.293 | 0.217 | 0.235 | 0.048 | 0.212 | 0.281 | 0.373 | 0.141 | 0.353 | 0.337 | 0.171 | 0.221 | 0.181 | 0.321 | 0.155 | 0.116 | 0.171 | 0.021 | 0.426 | 0.407 | 0.075 | 0.358 | 0.173 | 0.266 | 0.01 | 0.235 | 0.188 | 0.404 | 0.062 | 0.351 | 0.221 | 0.19 | 0.207 | 0.273 | 0.153 | 0.106 | 0.235 | 0.121 | 0.266 | 0.231 | 0.201 | 0.172 | 0.182 | 0.41 | 0.303 | 0.204 | 0.403 | 0.306 | 0.347 | 0.287 | 0.41 | 0.158 | 0.125 | 0.175 | 0.105 | 0.104 | 0.133 | 0.05 | 0 | 0.104 | 0.149 | 0.122 | 0.242 | 0.318 | 0.372 | 0.343 | 0.128 | 0.246 | 0.398 | 0.255 | 0.081 | 0.011 | 0.16 | 0.413 | 0.411 | 0.118 | 0.403 | 0.358 | 0.191 | 0.1 | 0.338 | 0.281 | 0.103 | 0.177 | 0.23 | 0.21 | 0.383 | 0.409 | 0.179 | 0.307 | 0.303 | 0.182 | 0.085 | 0.289 | 0.289 | 0.422 | 0.341 | 0.388 | 0.417 | 0.075 | 0.137 | 0.299 | 0.264 | 0.408 | 0.136 | 0.104 | 0 | 0.204 | 0.147 | 0.301 | 0.296 | 0.04 | 0.408 | 0.117 | 0.165 | 0.413 | 0.125 | 0.387 | 0.324 | 0.083 | 0.237 | 0.361 | 0.113 | 0.192 | 0.239 | 0.185 | 0.339 | 0.002 | 0.261 | 0.292 | 0.299 | 0.124 | 0.368 | 0.341 | 0.287 | 0.296 | 0.183 | 0.405 | 0.412 | 0.073 | 0.245 | 0.241 | 0.292 | 0.421 | 0.403 | 0.296 | 0.416 | 0.205 | 0.231 | 0.01 | 0.294 | 0.195 | 0.009 | 0.391 | 0.175 | 0.235 | 0.234 | 0.074 | 0.205 | 0.053 | 0.163 | 0.1 | 0.081 | 0.119 | 0.093 | 0.239 | 0.386 | 0.299 | 0.125 | 0.317 | 0.204 | 0.361 | 0 | 0.291 | 0.091 | 0.366 | 0.316 | 0.407 | 0.306 | 0 | 0.19 | 0.121 | 0 | 0.414 | 0.319 | 0.265 | 0.236 | 0.291 | 0.289 | 0.057 | 0.252 | 0.227 | 0.145 | 0.229 | 0.412 | 0.29 | 0.353 | 0.248 | 0.387 | 0.175 | 0.271 | 0.003 | 0.393 | 0.248 | 0.122 | 0.24 | 0.156 | 0.254 | 0.285 | 0.415 | 0.411 | 0.171 | 0.282 | 0.362 | 0.104 | 0.335 | 0.394 | 0.01 | 0.284 | 0.158 | 0.411 | 0.278 | 0.299 | 0.352 | 0.257 | 0.381 | 0.003 | 0.293 | 0.424 | 0.377 | 0.131 | 0.258 | 0.404 | 0.411 | 0.408 | 0 | 0.145 | 0.039 | 0.288 | 0.145 | 0.177 | 0.356 | 0.09 | 0.05 | 0.406 | 0.27 | 0.233 | 0.234 | 0.211 | 0.27 | 0.175 | 0.253 | 0.352 | 0.347 | 0.356 | 0.277 | 0.123
12 | 5.5 | 0.36 | 0.352 | 0.313 | 0.077 | 0.32 | 0.469 | 0.336 | 0.58 | 0.601 | 0.478 | 0.691 | 0.694 | 0.197 | 0.542 | 0.546 | 0.404 | 0.348 | 0.518 | 0.685 | 0.236 | 0.241 | 0.408 | 0.234 | 0.707 | 0.648 | 0.469 | 0.537 | 0.172 | 0.69 | 0.43 | 0.411 | 0.328 | 0.607 | 0.262 | 0.501 | 0.416 | 0.425 | 0.6 | 0.7 | 0.701 | 0.42 | 0.359 | 0.226 | 0.476 | 0.595 | 0.168 | 0.096 | 0.244 | 0.691 | 0.406 | 0.471 | 0.542 | 0.692 | 0.592 | 0.689 | 0.691 | 0.38 | 0.504 | 0.315 | 0.242 | 0.56 | 0.212 | 0.198 | 0.15 | 0 | 0.278 | 0.262 | 0.281 | 0.711 | 0.614 | 0.588 | 0.677 | 0.661 | 0.694 | 0.258 | 0.111 | 0.507 | 0.411 | 0.694 | 0.692 | 0.181 | 0.684 | 0.414 | 0.137 | 0.274 | 0.511 | 0.43 | 0.321 | 0.301 | 0.515 | 0.297 | 0.646 | 0.69 | 0.411 | 0.517 | 0.607 | 0.411 | 0.215 | 0.384 | 0.617 | 0.679 | 0.632 | 0.706 | 0.66 | 0.477 | 0.102 | 0.629 | 0.687 | 0.689 | 0.175 | 0.213 | 0.128 | 0.608 | 0.445 | 0.357 | 0.344 | 0.405 | 0.516 | 0.222 | 0.504 | 0.694 | 0.23 | 0.523 | 0.686 | 0.417 | 0.194 | 0.405 | 0.219 | 0.241 | 0.689 | 0.325 | 0.532 | 0.132 | 0.286 | 0.502 | 0.572 | 0.417 | 0.69 | 0.695 | 0.604 | 0.506 | 0.685 | 0.686 | 0.693 | 0.332 | 0.684 | 0.553 | 0.502 | 0.702 | 0.465 | 0.594 | 0.545 | 0.504 | 0.407 | 0.202 | 0.504 | 0.265 | 0.146 | 0.596 | 0.181 | 0.51 | 0.36 | 0.232 | 0.294 | 0.22 | 0.322 | 0.321 | 0.167 | 0.114 | 0 | 0.17 | 0.495 | 0.348 | 0.23 | 0.527 | 0.601 | 0.588 | 0.173 | 0.426 | 0.677 | 0.511 | 0.568 | 0.678 | 0.696 | 0.132 | 0.307 | 0.589 | 0.226 | 0.54 | 0.549 | 0.499 | 0.163 | 0.456 | 0.322 | 0.415 | 0.509 | 0.354 | 0.327 | 0.691 | 0.693 | 0.329 | 0 | 0.623 | 0.452 | 0.315 | 0.323 | 0.354 | 0.486 | 0.466 | 0.416 | 0.35 | 0.498 | 0.578 | 0.479 | 0.696 | 0.692 | 0.41 | 0.499 | 0.57 | 0.27 | 0.522 | 0.559 | 0.265 | 0.616 | 0.407 | 0.538 | 0.642 | 0.61 | 0.688 | 0.682 | 0.669 | 0.084 | 0.501 | 0.705 | 0.665 | 0.129 | 0.692 | 0.685 | 0.692 | 0.689 | 0.143 | 0.41 | 0.14 | 0.357 | 0.353 | 0.115 | 0.556 | 0.19 | 0.496 | 0.687 | 0.639 | 0.455 | 0.573 | 0.42 | 0.475 | 0.307 | 0.609 | 0.687 | 0.527 | 0.674 | 0.463 | 0
13 | 6 | 0.733 | 0.621 | 0.432 | 0.366 | 0.6 | 0.699 | 0.465 | 0.574 | 0.572 | 0.736 | 0.917 | 1 | 0.314 | 0.984 | 0.823 | 0.52 | 0.791 | 0.701 | 0.917 | 0.612 | 0.486 | 0.533 | 0.336 | 1.013 | 0.858 | 0.563 | 0.738 | 0.43 | 0.996 | 0.364 | 0.602 | 0.481 | 0.774 | 0.149 | 0.847 | 0.739 | 0.545 | 0.848 | 0.788 | 0.77 | 0.603 | 0.428 | 0.33 | 0.679 | 0.863 | 0.374 | 0.477 | 0.363 | 0.997 | 0.668 | 0.684 | 0.961 | 0.909 | 0.702 | 0.995 | 0.87 | 0.607 | 0.514 | 0.468 | 0.261 | 0.852 | 0.481 | 0.277 | 0.199 | 0.271 | 0.608 | 0.372 | 0.615 | 0.904 | 0.905 | 0.692 | 0.911 | 0.809 | 0.992 | 0.732 | 0.346 | 0.549 | 0.526 | 1 | 0.998 | 0.198 | 0.906 | 0.764 | 0.484 | 0.467 | 0.867 | 0.795 | 0.193 | 0 | 0.67 | 0.511 | 0.961 | 0.996 | 0.545 | 0.747 | 0.784 | 0.714 | 0.397 | 0.636 | 0.986 | 0.857 | 0.867 | 0.858 | 0.877 | 0.64 | 0.476 | 0.925 | 0.804 | 0.995 | 0.377 | 0.345 | 0.038 | 0.833 | 0.77 | 0.749 | 0.736 | 0.179 | 0.944 | 0.225 | 0.573 | 1 | 0.238 | 0.907 | 0.876 | 0.643 | 0.574 | 0.812 | 0.559 | 0.579 | 0.995 | 0.478 | 0.866 | 0.202 | 0.731 | 0.671 | 1.006 | 0.471 | 0.996 | 0.84 | 0.925 | 0.736 | 0.847 | 0.992 | 0.989 | 0.374 | 0.853 | 0.932 | 0.598 | 0.881 | 0.983 | 0.992 | 1.003 | 0.58 | 0.598 | 0.115 | 0.638 | 0.441 | 0.149 | 0.827 | 0.447 | 0.744 | 0.527 | 0.347 | 0.321 | 0.26 | 0.351 | 0.393 | 0.431 | 0.339 | 0.334 | 0.536 | 0.962 | 0.739 | 0.345 | 0.757 | 0.752 | 1.01 | 0.036 | 0.731 | 0.993 | 0.879 | 0.937 | 0.918 | 0.817 | 0.215 | 0.74 | 0.565 | 0.466 | 0.94 | 0.88 | 0.571 | 0.603 | 0.634 | 0.729 | 0.415 | 0.902 | 0.57 | 0.333 | 0.997 | 0.999 | 0.673 | 0 | 0.908 | 0.986 | 0.468 | 0.411 | 0.439 | 1.002 | 0.903 | 0.489 | 0.553 | 0.701 | 0.883 | 0.705 | 0.849 | 0.883 | 0.569 | 0.612 | 0.748 | 0.503 | 0.926 | 0.993 | 0.28 | 0.842 | 0.689 | 0.998 | 0.874 | 0.82 | 0.819 | 0.713 | 0 | 0.094 | 0.658 | 0.93 | 1.005 | 0.311 | 0.836 | 0.895 | 0.998 | 0.995 | 0.301 | 0.531 | 0.33 | 0.71 | 0.572 | 0.432 | 0.689 | 0.37 | 0.53 | 0.993 | 1.013 | 0.685 | 0.806 | 0.464 | 0.865 | 0.3 | 0.909 | 0.795 | 1.015 | 0.791 | 0.717 | 0.454
14 | 6.5 | 0.815 | 0.911 | 0.57 | 0.556 | 0.794 | 0.745 | 0.76 | 1.126 | 0 | 0.856 | 1.251 | 1.274 | 0.524 | 0 | 1.011 | 0.731 | 1.009 | 0.88 | 1.271 | 0.753 | 0.473 | 0 | 0.609 | 1.323 | 1.304 | 0.783 | 0.84 | 0.486 | 1.243 | 0.779 | 0.746 | 0.636 | 1.301 | 0.315 | 1.04 | 0.863 | 0.81 | 1.011 | 1.282 | 1.214 | 0.633 | 0.796 | 0.306 | 0.862 | 0.971 | 0.649 | 0.632 | 0.63 | 1.307 | 0.805 | 0.807 | 1.104 | 1.292 | 1.131 | 1.145 | 1.307 | 0.683 | 0.941 | 0.623 | 0.473 | 0.803 | 0.465 | 0.626 | 0.324 | 0.357 | 0.656 | 0.627 | 0.809 | 1.327 | 1.308 | 1.127 | 1.087 | 1.194 | 1.146 | 0.81 | 0.297 | 0.817 | 0.796 | 1.296 | 1.308 | 0.405 | 1.3 | 1.093 | 0.398 | 0.622 | 1.138 | 1.029 | 0.629 | 0 | 0.977 | 0.433 | 1.27 | 1.257 | 0.774 | 0.979 | 1.107 | 0.761 | 0.552 | 0.922 | 1.123 | 1.319 | 1.311 | 1.237 | 1.314 | 0.775 | 0.505 | 1.206 | 1.29 | 1.305 | 0.585 | 0.336 | 0.282 | 1.031 | 1.156 | 0.811 | 0.968 | 0.79 | 1.131 | 0.453 | 0.95 | 1.31 | 0.401 | 0.605 | 1.302 | 0.771 | 0.704 | 1.145 | 0.667 | 0.748 | 1.197 | 0.633 | 1.057 | 0.363 | 0.831 | 0.941 | 1.168 | 0.564 | 1.235 | 1.311 | 1.271 | 0.968 | 1.308 | 1.302 | 1.309 | 0.434 | 1.278 | 1.08 | 0.964 | 1.27 | 1.055 | 1.263 | 1.287 | 0.966 | 0.753 | 0.428 | 0.966 | 0.602 | 0.456 | 1.216 | 0.616 | 0.976 | 0.666 | 0.372 | 0.728 | 0.376 | 0.63 | 0.629 | 0.379 | 0.455 | 0.314 | 0.8 | 1.272 | 0.855 | 0.461 | 0.989 | 1.105 | 1.32 | 0.409 | 0.963 | 1.208 | 1.15 | 1.119 | 1.304 | 1.312 | 0.355 | 0.769 | 1.021 | 0.546 | 1.311 | 1.311 | 0.968 | 0.646 | 0.963 | 0.955 | 0.692 | 1.111 | 0.788 | 0.628 | 1.183 | 1.265 | 0.962 | 0.716 | 1.191 | 1.221 | 0.623 | 1.039 | 0.673 | 1.245 | 1.312 | 0.801 | 0.801 | 0.855 | 1.142 | 0.961 | 1.312 | 1.294 | 0.763 | 0.921 | 1.146 | 0.636 | 1.257 | 1.118 | 0.584 | 1.232 | 0.893 | 1.238 | 1.249 | 1.309 | 1.304 | 1.298 | 1.068 | 0.227 | 0.838 | 1.321 | 1.24 | 0.37 | 1.207 | 1.293 | 1.308 | 1.305 | 0.624 | 0.775 | 0.301 | 0.904 | 0.683 | 0.625 | 1.133 | 0.629 | 0.918 | 1.173 | 1.119 | 0.906 | 1.083 | 0.805 | 1.029 | 0.623 | 1.233 | 1.303 | 1.184 | 1.3 | 0.974 | 0.483
15 | 7 | 1.093 | 1.13 | 0.569 | 0.755 | 0.736 | 0.978 | 0.824 | 1.314 | 1.198 | 1.028 | 1.302 | 1.574 | 0.489 | 1.455 | 1.129 | 0.793 | 1.186 | 1.211 | 1.526 | 0.776 | 0.795 | 0.989 | 0.748 | 1.631 | 1.612 | 1.194 | 1.014 | 0.649 | 1.48 | 0.946 | 0.854 | 0.79 | 1.424 | 0.648 | 1.388 | 1.14 | 0.765 | 1.409 | 1.544 | 1.469 | 0.997 | 0.988 | 0.207 | 1.058 | 0.673 | 0.578 | 0.786 | 0.646 | 1.615 | 1.151 | 1.127 | 1.557 | 1.564 | 1.386 | 1.503 | 1.488 | 0.98 | 1.121 | 0.777 | 0.405 | 1.387 | 0.79 | 0.532 | 0.409 | 0.357 | 0.916 | 0.626 | 0.771 | 1.567 | 1.445 | 1.285 | 1.52 | 1.559 | 1.618 | 1.188 | 0.578 | 1.2 | 0.988 | 1.549 | 1.616 | 0.57 | 1.608 | 1.259 | 0.579 | 0.753 | 1.362 | 1.287 | 0.557 | 0.77 | 1.171 | 0 | 1.619 | 1.614 | 0.988 | 0.978 | 1.416 | 1.181 | 0.762 | 1.023 | 1.602 | 1.499 | 1.619 | 1.604 | 1.457 | 1.157 | 0.678 | 1.394 | 1.585 | 1.613 | 0.585 | 0.771 | 0.359 | 1.368 | 1.472 | 1.212 | 1.163 | 0.742 | 1.582 | 0.497 | 0.695 | 1.618 | 0.396 | 0.611 | 1.494 | 0.951 | 0.899 | 1.245 | 0.861 | 0.825 | 1.492 | 0.642 | 1.407 | 0.334 | 1.082 | 1.13 | 1.524 | 0.994 | 1.566 | 1.405 | 1.441 | 1.199 | 1.338 | 1.61 | 1.556 | 0.749 | 1.608 | 1.337 | 1.162 | 1.578 | 1.608 | 1.436 | 1.566 | 1.142 | 0.839 | 0.571 | 1.197 | 0.721 | 0.423 | 1.423 | 0.629 | 1.155 | 0.987 | 0.364 | 0.988 | 0.567 | 0.784 | 0.707 | 0.664 | 0.225 | 0.454 | 0.897 | 1.399 | 1.078 | 0.57 | 1.22 | 1.334 | 1.512 | 0.503 | 0.8 | 1.544 | 1.319 | 1.592 | 1.496 | 1.49 | 0.567 | 1.093 | 1.189 | 0.551 | 1.413 | 1.581 | 1.129 | 0.655 | 1.053 | 0.949 | 0.859 | 1.549 | 0.98 | 0.393 | 1.557 | 1.617 | 1.037 | 1.563 | 1.56 | 1.537 | 0.741 | 1.246 | 0.923 | 1.454 | 1.458 | 0 | 0.946 | 1.197 | 1.113 | 1.216 | 1.527 | 1.477 | 0.987 | 1.029 | 1.416 | 0.736 | 1.368 | 0 | 0.656 | 1.546 | 0.95 | 1.532 | 1.618 | 1.441 | 1.41 | 1.377 | 1.618 | 0.139 | 1.11 | 1.548 | 1.623 | 0.449 | 1.592 | 1.609 | 1.616 | 1.613 | 0.671 | 0.987 | 0.549 | 1.087 | 0.853 | 0.596 | 1.316 | 0 | 1.205 | 1.383 | 1.611 | 1.184 | 1.334 | 0.977 | 1.314 | 0.777 | 1.612 | 1.559 | 1.612 | 1.572 | 1.131 | 0
16 | 7.5 | 0.217 | 1.429 | 0.895 | 0.747 | 0.977 | 1.255 | 0 | 1.53 | 1.353 | 0.498 | 1.059 | 1.7 | 0.673 | 1.918 | 1.447 | 0.895 | 1.431 | 1.443 | 1.814 | 1.191 | 0.741 | 1.113 | 0.763 | 0.308 | 1.559 | 1.414 | 1.296 | 0.839 | 1.626 | 0.957 | 1.055 | 0.944 | 1.918 | 0.871 | 1.636 | 1.406 | 1.017 | 1.679 | 1.759 | 1.615 | 0.963 | 1.055 | 0.624 | 1.428 | 1.269 | 0.889 | 0.708 | 0.887 | 0.663 | 1.272 | 1.353 | 1.821 | 1.158 | 1.528 | 1.922 | 1.486 | 1.168 | 1.337 | 0.903 | 0.704 | 1.516 | 0.915 | 0.652 | 0 | 0.393 | 1.187 | 0.624 | 0.938 | 0.91 | 1.925 | 1.584 | 1.794 | 1.601 | 1.466 | 1.361 | 0.581 | 1.263 | 1.105 | 0.864 | 0.546 | 0.685 | 1.129 | 1.598 | 0.843 | 0.84 | 1.56 | 1.662 | 0.785 | 0.739 | 1.402 | 0.837 | 1.132 | 1.592 | 1.097 | 0.564 | 1.601 | 1.381 | 0.705 | 1.346 | 1.759 | 1.439 | 1.618 | 1.668 | 1.495 | 1.219 | 0.864 | 1.749 | 1.801 | 0.594 | 0.743 | 0.844 | 0.346 | 1.67 | 1.509 | 1.232 | 1.306 | 0.998 | 1.843 | 0.645 | 1.027 | 0.514 | 0.536 | 1.738 | 1.452 | 1.215 | 1.072 | 1.591 | 1.076 | 1.158 | 1.849 | 0.938 | 1.677 | 0.417 | 1.426 | 1.408 | 1.801 | 1.167 | 1.211 | 1.845 | 1.926 | 1.431 | 1.875 | 1.919 | 0.865 | 0.701 | 1.917 | 0.707 | 1.258 | 1.192 | 1.723 | 1.726 | 1.365 | 1.35 | 0 | 0.487 | 1.429 | 0.792 | 0.567 | 1.897 | 0.931 | 1.379 | 1.18 | 0.67 | 1.147 | 0.566 | 0.928 | 0.933 | 0.923 | 0.474 | 0.694 | 1.185 | 1.92 | 0.443 | 0.595 | 1.452 | 1.604 | 1.369 | 0 | 1.033 | 1.733 | 1.586 | 1.69 | 0 | 1.525 | 0.378 | 1.331 | 0 | 0.755 | 1.919 | 1.687 | 1.329 | 1.182 | 1.426 | 1.355 | 1.02 | 1.861 | 1.1 | 0.895 | 1.495 | 0.574 | 1.354 | 1.889 | 1.761 | 1.815 | 0.541 | 1.793 | 0.982 | 1.871 | 1.929 | 1.163 | 1.115 | 1.429 | 1.344 | 1.424 | 1.403 | 0.469 | 1.117 | 1.388 | 1.607 | 1 | 1.791 | 0.999 | 0.767 | 1.806 | 1.007 | 1.52 | 1.523 | 1.926 | 1.633 | 1.869 | 1.882 | 0.182 | 1.279 | 1.827 | 1.536 | 0.629 | 1.687 | 1.207 | 1.2 | 0.594 | 0.763 | 1.18 | 0.673 | 1.423 | 1.142 | 0.876 | 1.615 | 0.703 | 1.327 | 1.792 | 1.35 | 1.333 | 1.505 | 1.064 | 1.598 | 0.867 | 1.878 | 1.752 | 1.729 | 1.747 | 1.437 | 0
17 | 8 | 0.781 | 1.408 | 0.889 | 0.945 | 1.021 | 1.237 | 1.29 | 1.893 | 1.578 | 0 | 0.539 | 0 | 0.893 | 1.587 | 0.654 | 1.198 | 0.662 | 0.559 | 1.214 | 1.267 | 0.846 | 1.107 | 1.006 | 0 | 0 | 1.55 | 1.5 | 0 | 0 | 0.664 | 1.341 | 1.089 | 0.995 | 0.948 | 0.472 | 1.42 | 0.344 | 0.957 | 1.501 | 0.955 | 1.228 | 1.362 | 0 | 0.183 | 1.636 | 1 | 1.078 | 1.014 | 0 | 1.639 | 1.53 | 0.163 | 0 | 0.695 | 0.109 | 0 | 1.106 | 1.616 | 1.052 | 0.717 | 1.623 | 0.85 | 0 | 0.459 | 0.404 | 1.185 | 0.856 | 1.375 | 0 | 0.216 | 1.349 | 1.675 | 0.685 | 0 | 1.041 | 0.75 | 1.475 | 1.362 | 0 | 0 | 0.458 | 0 | 1.02 | 0.94 | 0.827 | 0.155 | 1.309 | 0.818 | 0.661 | 0.912 | 1.099 | 0 | 0 | 1.362 | 1.635 | 1.675 | 1.514 | 1.076 | 1.587 | 0.092 | 0 | 0 | 0.4 | 0 | 1.611 | 0.735 | 0 | 0.073 | 0 | 0.855 | 0.883 | 0.433 | 0.467 | 1.343 | 1.444 | 1.415 | 1.243 | 0.299 | 0.793 | 1.457 | 0 | 0.492 | 2.077 | 0 | 1.576 | 1.239 | 1.235 | 1.227 | 1.243 | 0.144 | 1.086 | 0.171 | 0.672 | 1.496 | 1.205 | 0 | 1.238 | 0 | 0.315 | 0.19 | 0.507 | 0.312 | 0.879 | 0 | 0.99 | 1.21 | 2.033 | 1.509 | 0 | 0.881 | 0 | 0 | 1.36 | 1.202 | 0.72 | 1.55 | 0.885 | 0.796 | 1.618 | 1.076 | 0.719 | 1.207 | 0.632 | 1.145 | 0.757 | 0 | 1.028 | 0.972 | 0.651 | 0.529 | 1.288 | 0.262 | 1.344 | 0.801 | 0.151 | 1.933 | 0 | 0.72 | 1.387 | 0.734 | 0 | 0.489 | 0.434 | 0 | 0 | 1.498 | 1.521 | 1.059 | 0.356 | 0.928 | 1.6 | 1.211 | 1.502 | 0.953 | 1.146 | 0.362 | 1.354 | 0.934 | 0 | 0 | 1.562 | 1.912 | 0.192 | 0.215 | 1.076 | 2.056 | 0 | 0 | 0.78 | 1.279 | 1.367 | 1.151 | 1.463 | 0.544 | 0 | 1.445 | 1.109 | 1.538 | 0.234 | 1.05 | 0.29 | 0.941 | 0.692 | 0.114 | 1.46 | 0 | 0 | 0.181 | 0.114 | 0.676 | 0.474 | 0.032 | 0.997 | 1.086 | 0 | 0.681 | 0.281 | 0 | 0 | 0 | 0.969 | 1.244 | 0.655 | 1.539 | 1.241 | 0.941 | 0.855 | 0.893 | 1.495 | 0.203 | 0 | 1.485 | 1.351 | 1.371 | 1.005 | 0.964 | 0.734 | 0.354 | 0.006 | 0.809 | 1.58 | 0
18 | 8.5 | 0.592 | 0 | 0.548 | 1.21 | 1.217 | 0.505 | 0.522 | 0.578 | 1.731 | 0 | 0 | 0 | 0.117 | 1.38 | 0 | 1.49 | 0 | 1.864 | 0 | 1.4 | 1.224 | 0.668 | 1.113 | 0 | 0 | 1.801 | 0.149 | 0.656 | 0 | 0.793 | 0.47 | 1.225 | 0 | 1.108 | 0 | 0 | 1.345 | 0 | 0 | 0 | 1.212 | 0.939 | 0.205 | 0 | 0 | 0 | 1.201 | 1.099 | 0 | 0.117 | 0.765 | 0 | 0 | 0 | 0 | 0 | 0.968 | 1.636 | 1.212 | 0.915 | 0 | 1.047 | 0.967 | 0.805 | 0 | 1.198 | 1.155 | 1.092 | 0 | 0 | 0 | 0 | 0 | 0 | 1.199 | 0.874 | 1.057 | 0.702 | 0 | 0 | 0.737 | 0 | 0 | 1.024 | 0.072 | 0 | 0 | 0.908 | 1.214 | 0 | 1.335 | 0 | 0 | 0.639 | 0.158 | 0 | 0.362 | 1.025 | 0.986 | 0 | 0 | 0 | 0 | 0 | 0.755 | 0 | 0 | 0 | 0 | 1.122 | 1.186 | 0.577 | 0 | 0 | 0.324 | 0.136 | 0.729 | 0 | 0.895 | 1.539 | 0 | 0.698 | 1.063 | 0 | 1.185 | 1.496 | 0 | 1.343 | 1.462 | 0 | 1.222 | 0 | 0.826 | 0.653 | 0 | 0 | 1.312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.143 | 0 | 1.017 | 0 | 0 | 0 | 0 | 0 | 0 | 1.345 | 0.867 | 0.804 | 0.967 | 0.503 | 0 | 1.02 | 0 | 1.437 | 0.57 | 1.149 | 0.893 | 0.352 | 1.191 | 1.026 | 0.758 | 0.905 | 1.045 | 0 | 0.44 | 0.903 | 0 | 0.281 | 0 | 0.734 | 1.847 | 0 | 0 | 0 | 0.829 | 0 | 0.615 | 0.765 | 1.863 | 0.924 | 0 | 0 | 0 | 0.447 | 1.643 | 1.351 | 1.158 | 0 | 1.467 | 1.224 | 0 | 0 | 0.796 | 1.585 | 0 | 0 | 1.191 | 0.83 | 0.384 | 0 | 0 | 0.978 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0.897 | 1.694 | 0 | 1.501 | 0 | 0.688 | 1.017 | 0 | 0.795 | 0 | 0 | 0 | 0 | 0 | 0 | 0.242 | 0 | 0 | 0 | 0.812 | 0 | 0 | 0 | 0 | 0.748 | 1.531 | 0.878 | 0.041 | 1.438 | 1.112 | 0 | 0 | 0.448 | 0 | 0 | 0.69 | 0 | 0.906 | 0 | 1.212 | 0 | 0 | 0 | 0 | 0.536 | 1.104
19 | 9 | 1.76 | 0 | 0 | 1.12 | 0.889 | 0 | 1.579 | 0.14 | 0 | 2.015 | 0 | 0 | 1.135 | 0.372 | 0 | 0.695 | 0.324 | 0.494 | 0 | 0 | 0.229 | 0.544 | 1.251 | 0 | 0 | 0.1 | 0 | 1.139 | 0 | 1.521 | 0 | 0.175 | 0 | 1.316 | 0 | 0 | 0.317 | 0 | 0 | 0 | 0.174 | 0 | 0.857 | 0.574 | 0 | 1.354 | 0.274 | 1.335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.104 | 0.258 | 0.906 | 0 | 1.296 | 0.991 | 0.888 | 0.659 | 0.903 | 0.929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.856 | 0.091 | 0 | 0 | 0 | 0.648 | 0 | 0 | 0.481 | 0.767 | 0 | 0 | 1.065 | 1.33 | 0 | 1.526 | 0 | 0 | 0 | 0 | 0 | 0 | 1.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.384 | 0 | 0 | 0 | 1.109 | 0.804 | 0.469 | 0 | 0 | 0 | 0 | 1.169 | 0 | 0.87 | 0.182 | 0 | 0.796 | 0 | 0 | 0 | 0.326 | 0 | 0.864 | 0.134 | 0 | 0.164 | 0 | 0.999 | 0 | 0 | 0 | 0.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.774 | 0.536 | 0 | 1.205 | 0.874 | 0 | 1.294 | 0 | 0.025 | 0.924 | 0 | 0.83 | 0.213 | 0.683 | 1.296 | 0.805 | 0 | 0.026 | 0 | 0.763 | 0.99 | 0 | 0 | 0 | 0.77 | 0.446 | 0 | 0 | 0 | 0 | 0 | 0.788 | 0 | 1.5 | 1.287 | 0 | 0 | 0 | 1.642 | 0 | 1.045 | 1.139 | 0 | 0.109 | 1.231 | 0 | 0 | 0 | 0 | 0 | 0 | 0.502 | 0 | 0.778 | 0 | 0 | 1.086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.316 | 0 | 0.761 | 1.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.383 | 0 | 0 | 0 | 0.996 | 0 | 0 | 0 | 0 | 1.104 | 0.022 | 0.91 | 0 | 0.212 | 1.326 | 0 | 0 | 0 | 0 | 0 | 0.925 | 0 | 0 | 0 | 0.929 | 0 | 0 | 0 | 0 | 0 | 1.15
20 | 9.5 | 0.976 | 0 | 0 | 1.305 | 0 | 0 | 0.045 | 0 | 0 | 1.78 | 0 | 0 | 1.356 | 0 | 0 | 0 | 1.809 | 0 | 0 | 0 | 1.291 | 0.685 | 0 | 0 | 0 | 0 | 0 | 1.157 | 0 | 0 | 0 | 0 | 0 | 1.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.806 | 1.519 | 0 | 1.303 | 0 | 0.141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.076 | 0 | 0.019 | 1.086 | 1.058 | 0.801 | 0 | 0.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.065 | 0 | 0 | 0 | 0 | 0.361 | 0 | 0 | 1.046 | 1.121 | 0 | 0 | 1.394 | 1.429 | 0 | 0.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.365 | 0 | 0 | 0 | 1.141 | 1.39 | 0.685 | 0 | 0 | 0 | 0 | 1.063 | 0 | 1.056 | 0 | 0 | 0.978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.835 | 0 | 0 | 0.987 | 0 | 0.098 | 0 | 0 | 0 | 0 | 0.901 | 1.434 | 0 | 1.222 | 0.844 | 0 | 0 | 0 | 0.995 | 0.71 | 0 | 0 | 0 | 0.964 | 0 | 0 | 0 | 0 | 0 | 0 | 0.817 | 0 | 0 | 1.331 | 0 | 0 | 0 | 0.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.152 | 0 | 1.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.498 | 0 | 0 | 0 | 0.923 | 0 | 0 | 0 | 0 | 0.748 | 0 | 0.884 | 0 | 0 | 1.217 | 0 | 0.413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.401 | 0 | 0 | 0 | 0 | 0 | 1.444
21 | 10 | 0 | 0 | 1.512 | 0 | 0 | 0 | 1.114 | 0 | 0 | 0.103 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.198 | 0 | 0 | 0 | 0 | 1.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.653 | 0.011 | 0 | 0 | 0.844 | 1.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.175 | 0 | 0 | 1.233 | 1.01 | 0.746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.909 | 0 | 0 | 0 | 0 | 0.683 | 0 | 0 | 0 | 0.845 | 0 | 0 | 1.079 | 1.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.396 | 0 | 0 | 0 | 0.0003 | 0.523 | 0.728 | 0 | 0 | 0 | 0 | 0 | 0 | 0.538 | 0 | 0 | 1.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.838 | 0 | 0 | 0.927 | 0 | 0 | 0 | 0 | 0.568 | 0 | 0.811 | 1.165 | 0 | 0.063 | 0.981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.739 | 0 | 0 | 0 | 0 | 0 | 0 | 1.112 | 0 | 0 | 0.156 | 0 | 0 | 0 | 0.496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.475 | 0 | 0 | 0.794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.733 | 0 | 0 | 0 | 0.882 | 0 | 0.012 | 0 | 0 | 0.99 | 0 | 0.825 | 0 | 0 | 0.354 | 0 | 0.236 | 0 | 0 | 0 | 0 | 0 | 0 | 0.546 | 0 | 0 | 0 | 0 | 0 | 0 | 1.307
22 | 10.5 | 0 | 0 | 1.515 | 0 | 0 | 0 | 0.361 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.322 | 0 | 0 | 0 | 0 | 0.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.427 | 0.936 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.156 | 0 | 0 | 0 | 0 | 0 | 0.658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.064 | 0 | 0 | 1.072 | 0 | 0 | 0 | 0 | 1.028 | 0 | 0.206 | 0 | 0 | 0 | 0.508 | 0.939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.968 | 0 | 0 | 0 | 0 | 0 | 0 | 0.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.864 | 0 | 0.24 | 0 | 0 | 0 | 0 | 1.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.529
23 | 11 | 0 | 0 | 1.441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.084 | 0.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.469 | 0 | 0.119 | 0 | 0 | 0 | 0 | 0 | 1.183 | 0 | 0 | 0 | 0 | 0 | 0 | 1.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014 | 0 | 1.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 11.5 | 0 | 0 | 1.628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.235 | 0 | 0 | 0 | 0 | 0 | 0 | 1.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.306 | 1.209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.563 | 0 | 0 | 0.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.126 | 0 | 0 | 0.681 | 0 | 0 | 0 | 0 | 0 | 0 | 1.22 | 0 | 0 | 0 | 0.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 12 | 0 | 0 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.326 | 0 | 0 | 0 | 0 | 0 | 0 | 1.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98 | 0 | 0 | 0 | 1.21 | 0 | 0 | 0 | 0.024 | 0 | 0 | 0 | 0 | 0 | 0 | 0.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.051 | 0 | 0 | 0 | 0 | 0.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.622 | 0 | 0 | 0 | 0 | 0.799 | 0 | 0 | 0 | 1.199 | 0 | 0 | 0 | 0.896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.453
27 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.158 | 0 | 0 | 0 | 1.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.882 | 0 | 0 | 0 | 0 | 0 | 0.338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.413 | 0 | 0 | 0 | 0 | 0.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.312 | 0 | 0 | 0 | 0 | 0.704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.268 | 0 | 0 | 0 | 0 | 0.709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.383 | 0 | 0 | 0 | 0.838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.193 | 0 | 0.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0 | 0 | 0.757 | 0 | 0 | 0 | 0.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.347 | 0 | 0 | 0 | 0.365 | 0 | 0 | 0 | 0.849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.213 | 0.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.425 | 0 | 0 | 0 | 0.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.528 | 0 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.225 | 0.513 | 0 | 0 | 0 | 0 | 0.162 | 0 | 0 | 0.356 | 0 | 0 | 0 | 0.347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.562 | 0 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 18 | 0.568 | 0.207 | 0 | 0 | 0 | 0.41 | 0 | 0 | 0 | 0 | 0.356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063 | 0 | 0 | 0.128 | 0 | 0 | 0.336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.249 | 0 | 0 | 0.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.101 | 0.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48 | 0 | 0 | 0 | 0 | 0.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023 | 0 | 0 | 0.057 | 0 | 0 | 0 | 0.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.362 | 0 | 0 | 0.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027 | 0.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.147 | 0.216 | 0 | 0 | 0 | 0 | 0.098 | 0 | 0.232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.325 | 0 | 0.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.105 | 0.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32 | 0 | 0 | 0 | 0.185 | 0 | 0 | 0 | 0
39 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 0 | 0.04 | 0 | 0 | 0.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.329 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.094 | 0 | 0.069 | 0 | 0 | 0 | 0 | 0 | 0.234 | 0 | 0 | 0 | 0 | 0.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.245 | 0 | 0.076 | 0 | 0.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052 | 0.172 | 0 | 0 | 0 | 0 | 0.012 | 0 | 0.012 | 0 | 0 | 0.065 | 0 | 0 | 0
40 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 6. Raw batt discharge
Raw batt discharge
Verbatim copy of Discharge_kW (TR6_analysis_data.xlsx). One row per half-hour, one column per battery (kW).
period | hour | BES_TR6_one38_B | BES_TR6_one242_B | BES_TR6_one252_C | BES_TR6_one260_C | BES_TR6_one280_A | BES_TR6_one287_B | BES_TR6_one299_B | BES_TR6_one313_A | BES_TR6_one320_B | BES_TR6_one346_C | BES_TR6_one416_C | BES_TR6_one446_B | BES_TR6_one477_A | BES_TR6_one480_A | BES_TR6_one482_B | BES_TR6_one521_C | BES_TR6_one537_A | BES_TR6_one559_C | BES_TR6_one570_B | BES_TR6_one590_A | BES_TR6_one605_A | BES_TR6_one614_B | BES_TR6_one73_A | BES_TR6_one76_A | BES_TR6_one137_A | BES_TR6_one176_A | BES_TR6_four149_B | BES_TR6_four163_C | BES_TR6_four171_A | BES_TR6_four184_B | BES_TR6_four200_A | BES_TR6_four239_A | BES_TR6_four259_B | BES_TR6_four288_B | BES_TR6_four289_B | BES_TR6_four301_C | BES_TR6_four317_B | BES_TR6_four354_B | BES_TR6_four358_C | BES_TR6_four65_B | BES_TR6_four384_B | BES_TR6_four385_A | BES_TR6_four396_B | BES_TR6_four423_C | BES_TR6_four446_B | BES_TR6_four451_C | BES_TR6_four466_C | BES_TR6_four558_C | BES_TR6_four70_B | BES_TR6_four573_A | BES_TR6_four664_A | BES_TR6_four675_C | BES_TR6_four710_C | BES_TR6_four727_B | BES_TR6_four732_B | BES_TR6_four818_B | BES_TR6_four821_A | BES_TR6_four832_A | BES_TR6_four840_A | BES_TR6_four957_A | BES_TR6_four978_A | BES_TR6_four988_A | BES_TR6_four1013_B | BES_TR6_four1027_A | BES_TR6_four1063_C | BES_TR6_four1103_C | BES_TR6_four1140_A | BES_TR6_four1152_B | BES_TR6_four1220_C | BES_TR6_five147_dup_C | BES_TR6_five149_A | BES_TR6_five168_A | BES_TR6_five170_A | BES_TR6_five170_dup_A | BES_TR6_five186_C | BES_TR6_five186_dup_C | BES_TR6_five194_C | BES_TR6_five199_dup_C | BES_TR6_five67_C | BES_TR6_five67_dup_C | BES_TR6_five223_A | BES_TR6_five223_dup_A | BES_TR6_five242_dup_A | BES_TR6_five243_B | BES_TR6_five243_dup_B | BES_TR6_five284_C | BES_TR6_five284_dup_C | BES_TR6_five285_B | BES_TR6_five285_dup_B | BES_TR6_five303_B | BES_TR6_five78_A | BES_TR6_five78_dup_A | BES_TR6_five394_C | BES_TR6_five394_dup_C | BES_TR6_five421_A | BES_TR6_five445_dup_C | BES_TR6_five457_B | BES_TR6_five494_B | BES_TR6_five499_B | BES_TR6_five92_dup_A | BES_TR6_five512_dup_A | BES_TR6_five513_B | BES_TR6_five513_dup_B | BES_TR6_five520_C | BES_TR6_five520_dup_C | BES_TR6_five537_C | BES_TR6_five537_dup_C | BES_TR6_five551_C | BES_TR6_five585_A | BES_TR6_five588_dup_A | BES_TR6_five108_dup_B | BES_TR6_five649_A | BES_TR6_five663_C | BES_TR6_five663_dup_C | BES_TR6_five670_dup_C | BES_TR6_five704_A | BES_TR6_five733_C | BES_TR6_five735_A | BES_TR6_five735_dup_A | BES_TR6_five748_B | BES_TR6_five117_dup_B | BES_TR6_five750_B | BES_TR6_five778_dup_B | BES_TR6_five793_A | BES_TR6_five881_C | BES_TR6_five905_B | BES_TR6_five118_B | BES_TR6_five118_dup_B | BES_TR6_five123_B | BES_TR6_five123_dup_B | BES_TR6_five129_C | BES_TR6_six64_A | BES_TR6_six64_dup_A | BES_TR6_six154_dup_C | BES_TR6_six154_tri_C | BES_TR6_six173_C | BES_TR6_six173_dup_C | BES_TR6_six191_B | BES_TR6_six191_dup_B | BES_TR6_six203_A | BES_TR6_six203_dup_A | BES_TR6_six203_tri_A | BES_TR6_six232_C | BES_TR6_six238_A | BES_TR6_six238_tri_A | BES_TR6_six249_dup_B | BES_TR6_six269_tri_C | BES_TR6_six68_C | BES_TR6_six68_dup_C | BES_TR6_six68_tri_C | BES_TR6_six289_C | BES_TR6_six289_tri_C | BES_TR6_six317_dup_C | BES_TR6_six317_tri_C | BES_TR6_six326_tri_A | BES_TR6_six329_A | BES_TR6_six329_tri_A | BES_TR6_six342_A | BES_TR6_six349_dup_A | BES_TR6_six349_tri_A | BES_TR6_six350_dup_B | BES_TR6_six350_tri_B | BES_TR6_six362_tri_C | BES_TR6_six365_tri_C | BES_TR6_six378_dup_A | BES_TR6_six378_tri_A | BES_TR6_six75_tri_A | BES_TR6_six385_B | BES_TR6_six385_tri_B | BES_TR6_six387_dup_A | BES_TR6_six392_C | BES_TR6_six410_tri_A | BES_TR6_six431_dup_C | BES_TR6_six431_tri_C | BES_TR6_six441_dup_A | BES_TR6_six441_tri_A | BES_TR6_six484_dup_B | BES_TR6_six501_dup_A | BES_TR6_six512_dup_B | BES_TR6_six512_tri_B | BES_TR6_six82_A | BES_TR6_six82_dup_A | BES_TR6_six523_dup_C | BES_TR6_six571_C | BES_TR6_six571_tri_C | BES_TR6_six583_dup_A | BES_TR6_six591_C | BES_TR6_six591_dup_C | BES_TR6_six595_tri_B | BES_TR6_six625_A | BES_TR6_six643_A | BES_TR6_six646_B | BES_TR6_six646_dup_B | BES_TR6_six651_dup_C | BES_TR6_six651_tri_C | BES_TR6_six87_dup_A | BES_TR6_six652_dup_A | BES_TR6_six652_tri_A | BES_TR6_six665_tri_B | BES_TR6_six667_A | BES_TR6_six667_tri_A | BES_TR6_six699_C | BES_TR6_six699_dup_C | BES_TR6_six699_tri_C | BES_TR6_six721_A | BES_TR6_six723_B | BES_TR6_six723_dup_B | BES_TR6_six740_A | BES_TR6_six740_dup_A | BES_TR6_six740_tri_A | BES_TR6_six758_B | BES_TR6_six758_dup_B | BES_TR6_six784_dup_B | BES_TR6_six784_tri_B | BES_TR6_six90_B | BES_TR6_six90_dup_B | BES_TR6_six799_tri_B | BES_TR6_six801_C | BES_TR6_six801_dup_C | BES_TR6_six801_tri_C | BES_TR6_six807_A | BES_TR6_six844_C | BES_TR6_six844_dup_C | BES_TR6_six844_tri_C | BES_TR6_six852_B | BES_TR6_six860_C | BES_TR6_six860_dup_C | BES_TR6_six869_C | BES_TR6_six869_tri_C | BES_TR6_six885_A | BES_TR6_six885_tri_A | BES_TR6_six894_B | BES_TR6_six894_tri_B | BES_TR6_six105_dup_A | BES_TR6_six105_tri_A | BES_TR6_six914_A | BES_TR6_six914_tri_A | BES_TR6_six921_B | BES_TR6_six929_tri_A | BES_TR6_six938_dup_A | BES_TR6_six938_tri_A | BES_TR6_six945_dup_C | BES_TR6_six952_A | BES_TR6_six952_dup_A | BES_TR6_six967_B | BES_TR6_six967_tri_B | BES_TR6_six974_dup_C | BES_TR6_six974_tri_C | BES_TR6_six979_A | BES_TR6_six990_B | BES_TR6_six990_dup_B | BES_TR6_six990_tri_B | BES_TR6_six111_dup_C | BES_TR6_six111_tri_C | BES_TR6_six1006_C | BES_TR6_six1006_dup_C | BES_TR6_six1020_A | BES_TR6_six1020_dup_A | BES_TR6_six1020_tri_A | BES_TR6_six1025_B | BES_TR6_six1064_C | BES_TR6_six1064_tri_C
1 | 0 | 0.493 | 0.114 | 0.058 | 0.135 | 0.233 | 0.308 | 0.202 | 0.103 | 0.243 | 0.05 | 0.051 | 0.314 | 1.144 | 2.281 | 0.108 | 0.19 | 0.453 | 0.381 | 0.929 | 0.043 | 0.14 | 0.114 | 0.173 | 0.035 | 0.062 | 0.503 | 0.046 | 0.234 | 0.052 | 0.108 | 0.053 | 0.159 | 0.674 | 0.147 | 0.213 | 0.07 | 0.063 | 0.5 | 0.069 | 0.209 | 0.117 | 0.097 | 0.117 | 0.098 | 0.054 | 0.228 | 0.047 | 0.049 | 0.055 | 0.043 | 0.081 | 0.15 | 0.155 | 0.15 | 0.132 | 0.159 | 0.166 | 0.53 | 0.056 | 0.127 | 0.132 | 0.214 | 0.173 | 0.261 | 0.183 | 0.613 | 0.109 | 0.094 | 0.031 | 0.221 | 0.378 | 0.353 | 0.229 | 0.13 | 0.378 | 0.107 | 0.22 | 0.129 | 0.048 | 0.05 | 2.391 | 0.095 | 0.046 | 0.04 | 0.522 | 0.133 | 0.197 | 0.655 | 0.245 | 0.116 | 0.059 | 0.391 | 0.526 | 0.053 | 0.365 | 0.042 | 0.134 | 0.056 | 0.553 | 0.227 | 0.119 | 0.047 | 0.401 | 0.126 | 0.169 | 0.123 | 0.09 | 0.184 | 0.053 | 0.138 | 0.285 | 1.792 | 0.168 | 0.062 | 0.363 | 0.102 | 0.426 | 0.226 | 0.168 | 0.76 | 0.048 | 0.048 | 0.807 | 0.073 | 0.206 | 0.176 | 0.162 | 0.159 | 0.205 | 0.119 | 0.046 | 0.055 | 0.678 | 0.119 | 0.139 | 0.108 | 0.19 | 0.052 | 0.094 | 0.217 | 0.05 | 0.05 | 0.41 | 0.049 | 0.185 | 1.565 | 1.492 | 0.054 | 0.04 | 0.058 | 0.257 | 0.086 | 0.124 | 0.057 | 0.282 | 0.588 | 0.036 | 0.209 | 0.709 | 0.211 | 0.042 | 0.054 | 0.214 | 0.053 | 0.058 | 0.049 | 0.05 | 0.215 | 0.156 | 0.192 | 0.144 | 0.178 | 0.61 | 0.048 | 0.029 | 0.367 | 0.062 | 0.16 | 0.901 | 0.313 | 0.038 | 0.09 | 0.129 | 0.117 | 0.594 | 0.211 | 0.145 | 0.156 | 0.354 | 0.706 | 0.05 | 1.071 | 0.152 | 1.028 | 0.273 | 0.046 | 0.061 | 0.086 | 0.201 | 0.049 | 0.288 | 0.045 | 0.055 | 0.164 | 0.056 | 0.962 | 0.19 | 0.046 | 0.046 | 0.38 | 0.048 | 0.052 | 0.34 | 0.033 | 0.046 | 0.158 | 0.054 | 0.599 | 0.072 | 0.144 | 0.165 | 0.131 | 0.149 | 0.048 | 0.149 | 0.148 | 0.11 | 0.081 | 0.054 | 0.06 | 0.041 | 0.052 | 0.053 | 0.055 | 0.043 | 0.149 | 0.079 | 0.138 | 0.639 | 0.053 | 1.507 | 0.683 | 0.102 | 0.058 | 0.133 | 0.168 | 0.207 | 0.37 | 0.201 | 0.243 | 0.124 | 0.575 | 0.338 | 0.084 | 0.129 | 0.232 | 0.488 | 0.312 | 0.096 | 0.187 | 0.585 | 0.061
2 | 0.5 | 0.55 | 0.052 | 0.058 | 0.253 | 0.185 | 0.053 | 0.263 | 0.265 | 0.048 | 0.095 | 0.113 | 0.466 | 0.537 | 0.11 | 0.09 | 0.157 | 0.045 | 0.171 | 0.523 | 0.125 | 0.206 | 0.052 | 0.136 | 0.035 | 0.222 | 0.278 | 0.134 | 0.143 | 0.052 | 0.265 | 0.053 | 0.122 | 0.123 | 0.047 | 0.103 | 0.07 | 0.039 | 0.157 | 0.267 | 0.155 | 0.044 | 0.112 | 0.402 | 0.053 | 0.187 | 0.125 | 0.245 | 0.239 | 0.126 | 0.225 | 0.261 | 0.108 | 0.05 | 0.121 | 0.244 | 0.051 | 0.048 | 0.727 | 0.056 | 0.036 | 0.176 | 0.043 | 0.149 | 0.15 | 0.24 | 0.2 | 0.152 | 0.04 | 0.127 | 0.05 | 0.382 | 0.503 | 0.084 | 0.13 | 0.216 | 0.047 | 0.104 | 0.053 | 0.048 | 0.05 | 0 | 0.104 | 0.167 | 0.109 | 0.097 | 0.05 | 0.055 | 0.693 | 0.388 | 0.041 | 0.293 | 0.047 | 0.447 | 0.131 | 0.039 | 0.127 | 0.172 | 0.201 | 0.135 | 0.07 | 0.135 | 0.234 | 0.091 | 0.126 | 0.073 | 0.232 | 0.198 | 0.068 | 0.053 | 0.205 | 0.237 | 0.37 | 0.084 | 0.339 | 0.037 | 0.16 | 0.059 | 0.053 | 0.056 | 0.052 | 0.048 | 0.155 | 0.464 | 0.155 | 0.056 | 0.128 | 0.14 | 0.256 | 0.052 | 0.053 | 0.046 | 0.116 | 0.297 | 0.1 | 0.054 | 0.197 | 0.047 | 0.088 | 0.15 | 0.189 | 0.05 | 0.129 | 0.486 | 0.11 | 0.128 | 0.058 | 0.198 | 0.188 | 0.096 | 0.303 | 0.056 | 0.156 | 0.102 | 0.057 | 0.203 | 0.781 | 0.153 | 0.103 | 0.856 | 0.056 | 0.115 | 0.118 | 0.046 | 0.121 | 0.058 | 0.049 | 0.131 | 0.225 | 0.054 | 0.174 | 0.049 | 0.101 | 0.23 | 0.048 | 0.029 | 0.447 | 0.192 | 0.25 | 0.795 | 0.05 | 0.038 | 0.049 | 0.082 | 0.085 | 0.572 | 0.046 | 0.198 | 0.293 | 0.295 | 0.136 | 0.222 | 1.043 | 0.404 | 1.174 | 0.049 | 0.159 | 0.061 | 0.156 | 0.051 | 0.049 | 0.375 | 0.305 | 0.127 | 0.048 | 0.056 | 0.556 | 0.261 | 0.107 | 0.31 | 0.125 | 0.21 | 0.052 | 0.053 | 0.033 | 0.199 | 0.119 | 0.172 | 0.544 | 0.042 | 0.23 | 0.047 | 0.055 | 0.17 | 0.091 | 0.139 | 0.106 | 0.052 | 0.28 | 0.054 | 0.243 | 0.112 | 0.119 | 0.053 | 0.32 | 0.043 | 0.082 | 0.196 | 0.079 | 0.05 | 0.053 | 0.228 | 0.149 | 0.134 | 0.2 | 0.173 | 0.202 | 0.113 | 0.049 | 0.044 | 0.329 | 0.035 | 0.518 | 0.052 | 0.151 | 0.153 | 0.056 | 0.374 | 0.253 | 0.234 | 0.183 | 0.618 | 0.185
3 | 1 | 0.15 | 0.077 | 0.315 | 0.114 | 0.213 | 0.121 | 0.193 | 0.231 | 0.327 | 0.117 | 0.125 | 0.048 | 0.165 | 0 | 0.058 | 0.196 | 0.262 | 1.176 | 0.076 | 0.065 | 0.038 | 0.121 | 0.114 | 0.035 | 0.054 | 0.606 | 0.157 | 0.058 | 0.168 | 0.021 | 0.053 | 0.043 | 0.26 | 0.297 | 0.053 | 0.194 | 0.039 | 0.197 | 0.613 | 0.099 | 0.191 | 0.053 | 0.097 | 0.103 | 0.084 | 0.03 | 0.258 | 0.049 | 0.063 | 0.043 | 0.056 | 0.098 | 0.05 | 0.057 | 0.053 | 0.178 | 0.166 | 0.129 | 0.056 | 0.106 | 0.238 | 0.043 | 0.151 | 0.092 | 0.152 | 0.047 | 0.052 | 0.04 | 0.048 | 0.213 | 0.061 | 0.71 | 0.319 | 0.112 | 0.054 | 0.16 | 0.289 | 0.12 | 0.048 | 0.05 | 0 | 0.058 | 0.211 | 0.165 | 0.13 | 0.086 | 0.388 | 0.479 | 0.269 | 0.116 | 0.059 | 0.047 | 0.052 | 0.053 | 0.039 | 0.139 | 0.112 | 0.152 | 0.18 | 0.148 | 0.039 | 0.056 | 0.254 | 0.044 | 0.243 | 0.056 | 0.04 | 0.244 | 0.053 | 0.095 | 0.198 | 0.118 | 0.157 | 0.104 | 0.037 | 0.05 | 0.219 | 0.123 | 0.056 | 0.157 | 0.048 | 0.048 | 0.435 | 0.056 | 0.196 | 0.223 | 0.193 | 0.087 | 0.198 | 0.306 | 0.046 | 0.131 | 0.133 | 0.198 | 0.101 | 0.121 | 0.177 | 0.135 | 0.193 | 0.049 | 0.05 | 0.195 | 0.583 | 0.049 | 0.275 | 0.101 | 0.054 | 0.054 | 0.159 | 0.1 | 0.056 | 0.045 | 0.052 | 0.057 | 0.129 | 0.052 | 0.036 | 0.222 | 0.679 | 0.056 | 0.042 | 0.054 | 0.183 | 0.053 | 0.161 | 0.148 | 0.05 | 0.05 | 0.054 | 0.079 | 0.144 | 0.128 | 0.104 | 0.048 | 0.029 | 0.172 | 0.038 | 0.208 | 0.695 | 0.273 | 0.139 | 0.221 | 0.111 | 0.054 | 0.563 | 0.316 | 0.171 | 0.121 | 0.214 | 0.149 | 0.05 | 0.058 | 0.647 | 0.057 | 0.297 | 0.119 | 0.134 | 0.044 | 0.208 | 0.049 | 0.216 | 0.088 | 0.218 | 0.309 | 0.056 | 0.835 | 0.079 | 0.191 | 0.057 | 0.048 | 0.048 | 0.052 | 0.162 | 0.033 | 0.046 | 0.189 | 0.079 | 0.548 | 0.042 | 0.161 | 0.221 | 0.087 | 0.22 | 0.163 | 0.083 | 0.05 | 0.168 | 0.049 | 0.229 | 0.152 | 0.041 | 0.161 | 0.053 | 0.062 | 0.391 | 0.042 | 0.137 | 0.057 | 0.05 | 0.053 | 0.139 | 0.143 | 0.151 | 0.076 | 0.104 | 0.054 | 0.056 | 0.12 | 0.044 | 0.328 | 0.035 | 1.299 | 0.289 | 0.044 | 0.155 | 0.168 | 0.209 | 0.055 | 0.033 | 0.05 | 0.048 | 0.135
4 | 1.5 | 0.201 | 0.151 | 0.058 | 0.158 | 0.055 | 0.053 | 0.06 | 0.384 | 0.151 | 0.05 | 0.051 | 0.119 | 0.12 | 0 | 0.058 | 0.06 | 0.236 | 0.272 | 0.226 | 0.051 | 0.114 | 0.052 | 0.144 | 0.035 | 0.15 | 0.284 | 0.052 | 0.122 | 0.132 | 0.094 | 0.053 | 0.043 | 0.131 | 0.076 | 0.053 | 0.047 | 0.11 | 0.049 | 0.706 | 0.229 | 0.077 | 0.156 | 0.052 | 0.085 | 0.084 | 0.296 | 0.37 | 0.204 | 0.051 | 0.084 | 0.13 | 0.108 | 0.05 | 0.2 | 0.181 | 0.051 | 0.048 | 0.152 | 0.056 | 0.063 | 0.105 | 0.097 | 0.262 | 0.319 | 0.223 | 0.257 | 0.209 | 0.094 | 0.082 | 0.058 | 0.225 | 0.369 | 0.052 | 0.107 | 0.054 | 0.1 | 0.074 | 0.061 | 0.13 | 0.05 | 0 | 0.132 | 0.046 | 0.063 | 0.057 | 0.117 | 0.07 | 0.091 | 0.054 | 0.041 | 0.208 | 0.047 | 0.052 | 0.053 | 0.039 | 0.351 | 0.081 | 0.101 | 0.181 | 0.148 | 0.191 | 0.127 | 0.036 | 0.051 | 0.146 | 0.113 | 0.113 | 0.055 | 0.053 | 0.159 | 0.23 | 0.11 | 0.084 | 0.14 | 0.207 | 0.124 | 0.316 | 0.153 | 0.168 | 0.125 | 0.048 | 0.048 | 0.373 | 0.056 | 0.206 | 0.128 | 0.156 | 0.253 | 0.121 | 0.053 | 0.046 | 0.051 | 0.203 | 0.112 | 0.092 | 0.196 | 0.06 | 0.052 | 0.182 | 0.088 | 0.05 | 0.104 | 0.638 | 0.11 | 0.084 | 0.173 | 0.269 | 0.188 | 0.04 | 0.219 | 0.056 | 0.197 | 0.091 | 0.057 | 0.103 | 0.052 | 0.036 | 0.103 | 0.147 | 0.056 | 0.042 | 0.068 | 0.077 | 0.083 | 0.106 | 0.074 | 0.05 | 0.291 | 0.164 | 0.229 | 0.049 | 0.225 | 0.164 | 0.048 | 0.029 | 0.544 | 0.153 | 0.057 | 0 | 0.131 | 0.038 | 0.154 | 0.101 | 0.223 | 0.058 | 0.089 | 0.348 | 0.222 | 0.047 | 0.186 | 0.16 | 0.219 | 0.676 | 0.131 | 0.099 | 0.288 | 0.061 | 0.198 | 0.076 | 0.049 | 0.056 | 0.051 | 0.055 | 0.069 | 0.056 | 0.037 | 0.259 | 0.073 | 0.118 | 0.166 | 0.048 | 0.052 | 0.243 | 0.069 | 0.158 | 0.138 | 0.082 | 0.656 | 0.206 | 0.153 | 0.122 | 0.163 | 0.177 | 0.126 | 0.034 | 0.05 | 0.111 | 0.203 | 0.054 | 0.19 | 0.112 | 0.052 | 0.053 | 0.126 | 0.219 | 0.189 | 0.185 | 0.16 | 0.05 | 0.053 | 0.157 | 0.054 | 0.05 | 0.19 | 0.09 | 0.262 | 0.227 | 0.178 | 0.183 | 0.231 | 0.205 | 0 | 0.108 | 0.137 | 0.108 | 0.12 | 0.054 | 0.055 | 0.174 | 0.294 | 0.114 | 0.161
5 | 2 | 0.08 | 0.052 | 0.289 | 0.264 | 0.162 | 0.053 | 0.192 | 0.536 | 0.129 | 0.14 | 0.186 | 0.057 | 0.202 | 0 | 0.058 | 0.193 | 0.045 | 0.071 | 0.057 | 0.205 | 0.13 | 0.052 | 0.048 | 0.035 | 0.134 | 0.191 | 0.157 | 0.255 | 0.052 | 0.202 | 0.053 | 0.043 | 0.142 | 0.21 | 0.148 | 0.218 | 0.039 | 0.049 | 0.521 | 0.193 | 0.044 | 0.053 | 0.142 | 0.053 | 0.187 | 0.057 | 0.598 | 0.083 | 0.051 | 0.184 | 0.211 | 0.156 | 0.15 | 0.071 | 0.194 | 0.076 | 0.048 | 0.198 | 0.056 | 0.036 | 0.078 | 0.159 | 0.158 | 0.059 | 0.141 | 0.061 | 0.052 | 0.135 | 0.093 | 0.089 | 0.061 | 0.235 | 0.064 | 0.152 | 0.054 | 0.051 | 0.132 | 0.095 | 0.048 | 0.05 | 0 | 0.067 | 0.046 | 0.117 | 0.057 | 0.05 | 0.107 | 0.16 | 0.054 | 0.116 | 0.144 | 0.128 | 0.052 | 0.131 | 0.039 | 0.463 | 0.216 | 0.111 | 0.057 | 0.062 | 0.063 | 0.163 | 0.247 | 0.201 | 0.062 | 0.048 | 0.162 | 0.171 | 0.053 | 0.188 | 0.149 | 0.002 | 0.05 | 0.16 | 0.037 | 0.138 | 0.059 | 0.214 | 0.056 | 0.068 | 0.048 | 0.155 | 0.312 | 0.137 | 0.056 | 0.051 | 0.125 | 0.055 | 0.133 | 0.053 | 0.046 | 0.117 | 0.039 | 0.22 | 0.106 | 0.056 | 0.138 | 0.076 | 0.12 | 0.172 | 0.05 | 0.098 | 0.173 | 0.049 | 0.247 | 0.058 | 0.187 | 0.054 | 0.175 | 0.199 | 0.093 | 0.045 | 0.135 | 0.057 | 0.21 | 0.148 | 0.112 | 0.154 | 0 | 0.211 | 0.042 | 0.24 | 0.115 | 0.091 | 0.092 | 0.049 | 0.05 | 0.15 | 0.054 | 0.104 | 0.111 | 0.063 | 0.17 | 0.048 | 0.029 | 0.231 | 0.101 | 0.29 | 0 | 0.189 | 0.038 | 0.094 | 0.092 | 0.067 | 0.291 | 0.089 | 0.154 | 0.083 | 0.124 | 0.174 | 0.113 | 0 | 0.512 | 0 | 0.049 | 0.057 | 0.356 | 0.044 | 0.051 | 0.049 | 0.056 | 0.342 | 0.177 | 0.048 | 0.056 | 0 | 0.17 | 0.199 | 0.161 | 0.048 | 0.072 | 0.072 | 0.087 | 0.069 | 0.088 | 0.13 | 0.089 | 0.043 | 0.042 | 0.096 | 0.082 | 0.055 | 0.048 | 0.206 | 0.191 | 0.204 | 0.096 | 0.158 | 0.205 | 0.185 | 0.041 | 0.228 | 0.053 | 0.351 | 0.225 | 0.042 | 0.177 | 0.057 | 0.05 | 0.053 | 0.318 | 0.054 | 0.234 | 0.086 | 0.209 | 0.086 | 0.101 | 0.087 | 0.174 | 0.055 | 0.089 | 0 | 0.102 | 0.097 | 0.159 | 0.056 | 0.133 | 0.226 | 0.144 | 0.543 | 0.044 | 0.149
6 | 2.5 | 0.216 | 0.175 | 0.084 | 0.08 | 0.055 | 0.053 | 0.125 | 0.455 | 0.142 | 0.072 | 0.051 | 0.119 | 0.197 | 0 | 0.058 | 0.16 | 0.334 | 0.152 | 0.057 | 0.103 | 0.053 | 0.121 | 0.21 | 0.035 | 0.078 | 0.174 | 0.128 | 0.058 | 0.248 | 0.097 | 0.053 | 0.043 | 0.217 | 0.164 | 0.07 | 0.047 | 0.039 | 0.184 | 0.215 | 0.183 | 0.215 | 0.126 | 0.075 | 0.053 | 0.054 | 0.192 | 0.116 | 0.049 | 0.051 | 0.043 | 0.056 | 0.206 | 0.055 | 0.129 | 0.057 | 0.153 | 0.048 | 0.129 | 0.056 | 0.052 | 0.297 | 0.043 | 0.185 | 0.347 | 0.148 | 0.115 | 0.052 | 0.04 | 0.031 | 0.182 | 0.061 | 0.139 | 0.331 | 0.048 | 0.12 | 0.194 | 0.223 | 0.087 | 0.048 | 0.05 | 0 | 0.1 | 0.225 | 0.141 | 0.068 | 0.154 | 0.234 | 0.05 | 0.054 | 0.041 | 0.059 | 0.047 | 0.052 | 0.053 | 0.039 | 0.542 | 0.076 | 0.056 | 0.266 | 0.117 | 0.039 | 0.047 | 0.064 | 0.044 | 0.328 | 0.259 | 0.04 | 0.141 | 0.053 | 0.081 | 0.155 | 0 | 0.163 | 0.206 | 0.13 | 0.05 | 0.059 | 0.062 | 0.168 | 0.213 | 0.048 | 0.048 | 0 | 0.091 | 0.346 | 0.216 | 0.176 | 0.214 | 0.187 | 0.306 | 0.046 | 0.064 | 0.152 | 0.106 | 0.087 | 0.042 | 0.099 | 0.147 | 0.135 | 0.265 | 0.05 | 0.28 | 0.056 | 0.086 | 0.112 | 0.217 | 0.054 | 0.155 | 0.08 | 0.141 | 0.221 | 0.045 | 0.052 | 0.057 | 0.172 | 0.052 | 0.077 | 0.216 | 0 | 0.056 | 0.111 | 0.134 | 0.145 | 0.053 | 0.174 | 0.049 | 0.131 | 0.121 | 0.164 | 0.198 | 0.082 | 0.12 | 0.091 | 0.048 | 0.029 | 0.333 | 0.038 | 0.16 | 0 | 0.136 | 0.139 | 0.281 | 0.054 | 0.1 | 0.13 | 0.304 | 0.184 | 0.287 | 0.185 | 0.047 | 0.074 | 0 | 0 | 0 | 0.223 | 0.046 | 0.632 | 0.044 | 0.117 | 0.049 | 0.142 | 0.051 | 0.167 | 0.247 | 0.056 | 0 | 0.154 | 0.046 | 0.063 | 0.166 | 0.143 | 0.177 | 0.087 | 0.033 | 0.046 | 0.05 | 0.054 | 0 | 0.087 | 0.304 | 0.091 | 0.055 | 0.22 | 0.126 | 0.146 | 0.05 | 0.14 | 0.049 | 0.078 | 0.21 | 0.112 | 0.052 | 0.053 | 0.28 | 0.118 | 0.042 | 0.061 | 0.079 | 0.05 | 0.053 | 0.042 | 0.143 | 0.05 | 0.058 | 0.144 | 0.501 | 0.085 | 0.211 | 0.044 | 0.055 | 0.072 | 0 | 0.254 | 0.044 | 0.072 | 0.152 | 0.209 | 0.082 | 0.141 | 0.152 | 0.119 | 0.227
7 | 3 | 0.163 | 0.052 | 0.212 | 0.223 | 0.144 | 0.072 | 0.148 | 0.262 | 0.093 | 0.05 | 0.137 | 0.057 | 0.026 | 0 | 0.139 | 0.092 | 0.052 | 0.038 | 0.207 | 0.165 | 0.191 | 0.052 | 0.136 | 0.035 | 0.206 | 0.164 | 0.134 | 0.192 | 0.052 | 0.021 | 0.053 | 0.043 | 0.09 | 0.104 | 0.137 | 0.117 | 0.063 | 0.062 | 0 | 0.08 | 0.052 | 0.082 | 0.052 | 0.053 | 0.076 | 0.08 | 0.051 | 0.135 | 0.051 | 0.159 | 0.056 | 0.051 | 0.05 | 0.143 | 0.119 | 0.057 | 0.166 | 0.373 | 0.056 | 0.116 | 0.067 | 0.09 | 0.168 | 0.068 | 0.279 | 0.047 | 0.052 | 0.19 | 0.031 | 0.05 | 0.21 | 0.048 | 0.06 | 0.063 | 0.268 | 0.16 | 0.108 | 0.053 | 0.062 | 0.05 | 0 | 0.1 | 0.153 | 0.12 | 0.159 | 0.05 | 0.1 | 0.208 | 0.054 | 0.041 | 0.185 | 0.047 | 0.052 | 0.105 | 0.039 | 0.21 | 0.072 | 0.156 | 0.108 | 0.18 | 0.127 | 0.243 | 0.148 | 0.089 | 0.053 | 0.105 | 0.089 | 0.112 | 0.053 | 0.212 | 0.193 | 0 | 0.078 | 0.14 | 0.114 | 0.212 | 0.234 | 0.186 | 0.056 | 0.052 | 0.048 | 0.048 | 0 | 0.056 | 0.056 | 0.134 | 0.105 | 0.233 | 0.052 | 0.053 | 0.046 | 0.109 | 0.039 | 0.211 | 0.068 | 0.134 | 0.047 | 0.052 | 0.135 | 0.123 | 0.05 | 0.05 | 0.044 | 0.073 | 0.039 | 0.058 | 0.137 | 0.088 | 0.04 | 0.244 | 0.056 | 0.197 | 0.052 | 0.057 | 0.076 | 0.148 | 0.048 | 0.087 | 0 | 0.183 | 0.046 | 0.115 | 0.046 | 0.121 | 0.058 | 0.173 | 0.05 | 0.31 | 0.054 | 0.169 | 0.049 | 0.245 | 0.217 | 0.048 | 0.029 | 0.295 | 0.16 | 0.21 | 0 | 0.22 | 0.038 | 0.049 | 0.087 | 0.046 | 0.101 | 0.058 | 0.235 | 0.167 | 0.079 | 0.18 | 0.199 | 0 | 0 | 0 | 0.057 | 0.231 | 0.081 | 0.044 | 0.166 | 0.049 | 0.198 | 0.159 | 0.105 | 0.13 | 0.056 | 0 | 0.204 | 0.243 | 0.236 | 0.048 | 0.048 | 0.052 | 0.195 | 0.033 | 0.199 | 0.242 | 0.054 | 0 | 0.161 | 0.094 | 0.192 | 0.195 | 0.177 | 0.048 | 0.034 | 0.127 | 0.095 | 0.136 | 0.054 | 0.06 | 0.041 | 0.119 | 0.053 | 0.373 | 0.043 | 0.122 | 0.254 | 0.138 | 0.05 | 0.053 | 0 | 0.054 | 0.05 | 0.218 | 0.049 | 0.503 | 0.244 | 0.124 | 0.233 | 0.055 | 0.221 | 0 | 0.093 | 0.111 | 0.236 | 0.136 | 0.129 | 0.091 | 0.078 | 0.21 | 0.044 | 0.069
8 | 3.5 | 0.05 | 0.049 | 0.159 | 0.227 | 0.053 | 0.1 | 0.167 | 0.155 | 0.332 | 0.047 | 0.097 | 0.124 | 0 | 0 | 0.055 | 0.258 | 0.097 | 0.129 | 0.091 | 0.133 | 0.036 | 0.119 | 0.208 | 0.032 | 0.051 | 0.19 | 0.145 | 0.184 | 0.2 | 0.27 | 0.051 | 0.041 | 0.13 | 0.167 | 0.078 | 0.145 | 0.084 | 0.12 | 0 | 0.22 | 0.164 | 0.051 | 0.101 | 0.132 | 0.192 | 0.11 | 0.213 | 0.151 | 0.048 | 0.107 | 0.25 | 0.307 | 0.073 | 0.054 | 0.249 | 0.168 | 0.046 | 0.154 | 0.054 | 0.035 | 0.242 | 0.165 | 0.051 | 0.228 | 0.045 | 0.17 | 0.2 | 0.038 | 0.078 | 0.218 | 0.073 | 0.033 | 0.172 | 0.193 | 0.051 | 0.046 | 0.279 | 0.127 | 0.113 | 0.047 | 0 | 0.055 | 0.043 | 0.144 | 0.055 | 0.047 | 0.164 | 0.054 | 0.052 | 0.088 | 0.057 | 0.044 | 0.049 | 0.077 | 0.036 | 0.137 | 0.259 | 0.195 | 0.119 | 0.059 | 0.124 | 0.044 | 0.16 | 0.16 | 0.232 | 0.068 | 0.183 | 0.151 | 0.05 | 0.089 | 0.234 | 0 | 0.061 | 0.224 | 0.034 | 0.047 | 0.299 | 0.173 | 0.055 | 0.154 | 0.045 | 0.154 | 0 | 0.157 | 0.195 | 0.049 | 0.177 | 0.053 | 0.05 | 0.206 | 0.044 | 0.07 | 0.177 | 0.09 | 0.122 | 0.194 | 0.188 | 0.132 | 0.252 | 0.046 | 0.047 | 0.192 | 0 | 0.046 | 0.149 | 0.16 | 0 | 0.105 | 0.1 | 0.205 | 0.254 | 0.042 | 0.116 | 0.055 | 0.293 | 0.049 | 0.139 | 0.181 | 0 | 0.083 | 0.039 | 0.215 | 0.212 | 0.051 | 0.201 | 0.047 | 0.066 | 0.058 | 0.053 | 0.045 | 0.142 | 0.104 | 0.071 | 0.047 | 0.026 | 0 | 0.09 | 0.215 | 0 | 0.176 | 0.035 | 0.288 | 0.102 | 0.152 | 0.082 | 0.139 | 0.168 | 0.228 | 0.093 | 0.12 | 0.047 | 0 | 0 | 0 | 0.188 | 0.184 | 0.128 | 0.042 | 0.048 | 0.046 | 0.053 | 0.042 | 0.236 | 0.045 | 0.054 | 0 | 0.18 | 0.078 | 0.128 | 0.069 | 0.046 | 0.174 | 0.153 | 0.03 | 0.043 | 0.116 | 0.115 | 0 | 0.039 | 0.181 | 0.08 | 0.052 | 0.133 | 0.263 | 0.186 | 0.123 | 0.116 | 0.198 | 0.226 | 0.331 | 0.038 | 0.16 | 0.05 | 0.824 | 0.04 | 0.108 | 0.093 | 0.054 | 0.047 | 0.05 | 0 | 0.097 | 0.127 | 0.055 | 0.178 | 0.227 | 0.045 | 0.146 | 0.121 | 0.052 | 0.032 | 0 | 0.152 | 0.122 | 0.059 | 0.054 | 0.16 | 0.213 | 0.098 | 0.075 | 0.116 | 0.207
9 | 4 | 0.16 | 0.132 | 0.101 | 0.041 | 0.131 | 0.016 | 0.021 | 0 | 0.055 | 0.108 | 0.001 | 0 | 0 | 0 | 0.014 | 0.029 | 0.354 | 0.0004 | 0.091 | 0.035 | 0.166 | 0.021 | 0.023 | 0 | 0.108 | 0 | 0.047 | 0.097 | 0.047 | 0.07 | 0.022 | 0.018 | 0.192 | 0.022 | 0.009 | 0.01 | 0.008 | 0.079 | 0 | 0.149 | 0.07 | 0.125 | 0.095 | 0.016 | 0.01 | 0.095 | 0.059 | 0.024 | 0.001 | 0.039 | 0.339 | 0.001 | 0.079 | 0.142 | 0.003 | 0.001 | 0.017 | 0 | 0.031 | 0.017 | 0.179 | 0.018 | 0.097 | 0.167 | 0.126 | 0.115 | 0.034 | 0.091 | 0.043 | 0.29 | 0.017 | 0 | 0.002 | 0 | 0.224 | 0.194 | 0.129 | 0.022 | 0.017 | 0.0003 | 0 | 0.092 | 0.184 | 0.083 | 0.145 | 0.006 | 0.142 | 0 | 0.029 | 0.029 | 0.142 | 0 | 0.002 | 0.022 | 0.002 | 0.031 | 0.059 | 0.066 | 0.112 | 0.169 | 0 | 0 | 0.014 | 0 | 0.024 | 0.184 | 0.027 | 0.052 | 0.003 | 0.065 | 0.187 | 0 | 0.082 | 0.089 | 0.17 | 0.116 | 0.028 | 0.044 | 0.037 | 0.087 | 0 | 0.029 | 0 | 0.018 | 0.166 | 0.268 | 0.024 | 0.137 | 0.129 | 0.1 | 0.021 | 0.083 | 0.134 | 0.18 | 0.017 | 0 | 0.016 | 0.038 | 0.024 | 0.213 | 0.013 | 0.133 | 0 | 0 | 0.228 | 0 | 0 | 0.097 | 0.102 | 0.082 | 0.006 | 0.064 | 0.07 | 0.026 | 0.046 | 0.015 | 0.011 | 0.034 | 0 | 0.095 | 0.005 | 0.023 | 0.027 | 0.022 | 0.046 | 0.024 | 0.088 | 0.257 | 0.09 | 0.295 | 0.018 | 0.189 | 0.233 | 0.029 | 0 | 0 | 0.087 | 0.09 | 0 | 0.177 | 0.095 | 0.034 | 0.004 | 0.072 | 0 | 0.104 | 0.168 | 0.196 | 0.052 | 0.143 | 0.013 | 0 | 0 | 0 | 0.175 | 0.108 | 0.034 | 0.019 | 0.001 | 0 | 0.232 | 0.189 | 0.005 | 0.266 | 0.031 | 0 | 0.111 | 0.036 | 0.43 | 0.111 | 0.017 | 0.034 | 0.127 | 0.06 | 0.087 | 0.114 | 0.023 | 0 | 0 | 0.16 | 0.156 | 0.069 | 0.225 | 0.016 | 0.066 | 0.0003 | 0 | 0.023 | 0.004 | 0.01 | 0 | 0.04 | 0.016 | 0 | 0.068 | 0.05 | 0.0003 | 0.007 | 0.0003 | 0.003 | 0 | 0.068 | 0.138 | 0.077 | 0.142 | 0.129 | 0.004 | 0.093 | 0.105 | 0.005 | 0 | 0 | 0.192 | 0.013 | 0.19 | 0.143 | 0.111 | 0.005 | 0.179 | 0.137 | 0.007 | 0.018
10 | 4.5 | 0.007 | 0 | 0.131 | 0.17 | 0 | 0 | 0.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0 | 0 | 0 | 0.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007 | 0.138 | 0 | 0 | 0 | 0 | 0 | 0.088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.117 | 0 | 0.122 | 0 | 0.018 | 0.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013 | 0 | 0 | 0.055 | 0.037 | 0.126 | 0 | 0.036 | 0 | 0 | 0 | 0.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056 | 0 | 0 | 0 | 0.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.132 | 0.013 | 0 | 0 | 0 | 0 | 0 | 0.141 | 0.036 | 0.081 | 0 | 0 | 0.068 | 0 | 0 | 0 | 0 | 0.078 | 0.008 | 0.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074 | 0 | 0 | 0 | 0 | 0.131 | 0 | 0.036 | 0.124 | 0 | 0.032 | 0 | 0.161 | 0.073 | 0 | 0.06 | 0.038 | 0 | 0.043 | 0.022 | 0.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0 | 0.017 | 0 | 0 | 0 | 0.02 | 0 | 0 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.006 | 0.055 | 0 | 0.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.078 | 0.003 | 0.009 | 0 | 0 | 0 | 0 | 0 | 0.012 | 0 | 0.004 | 0 | 0.05 | 0 | 0 | 0 | 0
11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055
13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0 | 0 | 0 | 0 | 0.602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.206
16 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.294 | 0 | 0 | 0 | 0 | 0.076 | 0 | 0 | 0 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.699
17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
18 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0.474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.976 | 0 | 0.513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 9 | 0 | 0 | 1.435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 9.5 | 0 | 0 | 1.726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0.928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.554 | 0 | 0 | 0 | 0 | 0.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0.412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.492 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.406 | 0 | 0.443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.955 | 0 | 0 | 0.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.505 | 0 | 0 | 0 | 0 | 0 | 0 | 1.384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.065 | 0 | 0 | 0 | 0.989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.358 | 0 | 0 | 0 | 0 | 0 | 0.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.663 | 0 | 0 | 0 | 0 | 0 | 0 | 0.241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.463 | 0 | 0 | 0.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.173 | 0 | 1.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0.057 | 0 | 0 | 0 | 0 | 0 | 1.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065 | 0 | 0 | 0 | 0 | 0.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.313 | 0 | 0 | 0 | 0.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 17 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0.099 | 0 | 0 | 0 | 0.238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.746 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038 | 0 | 0.136 | 0 | 0 | 0.742 | 0 | 0 | 0 | 0 | 1.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045 | 0.943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.796 | 0 | 0.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.336 | 0 | 0 | 0 | 0 | 0 | 0
36 | 17.5 | 0.511 | 0.187 | 0 | 0 | 0 | 1.454 | 0 | 0 | 0 | 0 | 0.855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.541 | 0 | 0 | 1.528 | 0 | 0 | 0 | 0 | 0.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.612 | 1.182 | 0 | 0.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.054 | 0 | 0.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36 | 0 | 0 | 0 | 0 | 0.626 | 0.009 | 0 | 0 | 0 | 0 | 0.656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.808 | 0 | 2.484 | 0 | 0 | 0 | 0 | 0 | 0
37 | 18 | 0 | 0 | 0 | 0.316 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.669 | 0 | 0 | 1.703 | 0 | 0 | 0 | 0.553 | 0 | 1.604 | 0.125 | 0 | 0 | 0 | 1.014 | 0 | 0 | 0 | 0 | 0 | 0.442 | 0 | 1.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.226 | 2.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.186 | 0.282 | 0 | 0 | 0 | 0 | 0.067 | 0 | 0 | 0 | 0 | 0 | 0.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0.209 | 0 | 0.322 | 0.266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.284 | 0 | 0 | 0 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.794 | 0.328 | 0 | 0 | 0 | 0 | 0.089 | 0 | 0 | 0 | 0 | 0.887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.887 | 0.421 | 0 | 0 | 0 | 2.084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.405 | 0 | 0 | 0 | 1.031 | 0.086 | 0 | 0 | 0 | 0 | 1.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.143 | 0 | 2.161 | 0 | 0.167 | 0 | 0 | 0.104 | 0
38 | 18.5 | 0 | 0 | 0 | 1.313 | 0.572 | 0 | 0 | 0 | 0 | 0 | 0.67 | 0 | 0.447 | 1.753 | 0 | 0.034 | 0 | 0 | 0 | 0 | 0 | 1.408 | 0 | 0.089 | 0 | 0.505 | 0 | 0.08 | 0 | 0 | 0 | 0 | 2.225 | 0.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014 | 0 | 0 | 0 | 0.249 | 0 | 0 | 0 | 0 | 0 | 0 | 0.316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.116 | 0 | 0 | 0 | 0 | 0.317 | 0 | 0.884 | 0 | 0 | 0 | 0 | 1.183 | 0 | 0 | 0.021 | 3.231 | 0 | 0 | 0 | 0 | 0 | 0.102 | 0 | 0 | 0 | 0 | 0.489 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027 | 0 | 0 | 0 | 0 | 0 | 0.256 | 0 | 0 | 0 | 0 | 0.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.603 | 0.032 | 0 | 0 | 0 | 0 | 0 | 1.149 | 0.764 | 0 | 0 | 0 | 0 | 1.209 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.102 | 0 | 0 | 0.098 | 0 | 0 | 0 | 0.031 | 0 | 0 | 0.042 | 0 | 0 | 0.059 | 0.854 | 0 | 0 | 0 | 0.217 | 0 | 0.518 | 0.185 | 1.493 | 0 | 0 | 0 | 0 | 0.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.405 | 0 | 0.667 | 0 | 0 | 0 | 0 | 1.096 | 0 | 0.213 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022 | 0 | 0 | 0 | 0.827 | 0.136 | 0.023 | 0 | 0 | 1.878 | 0.056 | 0.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.213 | 0 | 0 | 0 | 0 | 1.421 | 0 | 0 | 0 | 0 | 1.18 | 0 | 0 | 0 | 1.142 | 0.719 | 1.001 | 0.047 | 1.979 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023 | 0 | 0 | 0.464 | 0 | 0.257 | 0
39 | 19 | 0.093 | 0 | 0.18 | 1.978 | 0.304 | 0.261 | 0 | 0.046 | 0.15 | 0 | 0.945 | 0 | 0.107 | 0 | 0.278 | 0.104 | 0 | 0 | 0.001 | 1.387 | 0.014 | 0.327 | 1.93 | 0.007 | 0 | 0.198 | 0.166 | 0.185 | 0.053 | 0.196 | 0 | 0 | 0 | 0.085 | 0 | 0.017 | 0.152 | 0 | 0.237 | 0.17 | 0 | 0.48 | 0.346 | 0 | 0.126 | 0.085 | 1.791 | 0 | 0 | 0.062 | 0.057 | 0 | 0.912 | 0.883 | 0 | 0.103 | 0 | 0.241 | 0 | 0 | 0 | 0.509 | 0.055 | 0.314 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0.327 | 0.26 | 0.04 | 0.495 | 0 | 0 | 0 | 0 | 0.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.118 | 1.76 | 0 | 0 | 0 | 0 | 0 | 0.068 | 0.144 | 0 | 0 | 0 | 0.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0.117 | 0 | 0.176 | 0.173 | 0 | 0 | 0 | 0.024 | 0.311 | 1.747 | 0 | 0.129 | 0.226 | 0.017 | 0.395 | 0 | 0 | 0.479 | 0.325 | 0.177 | 0 | 0 | 0 | 0.017 | 2.665 | 0 | 0.153 | 0 | 0.098 | 0.006 | 0.131 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.025 | 1.393 | 0 | 0 | 2.777 | 0 | 0 | 0 | 0.22 | 0 | 0 | 0.077 | 0 | 1.434 | 0.303 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0.2 | 0.598 | 2.173 | 0.112 | 0.529 | 0 | 0.175 | 0 | 0 | 0 | 0 | 0.109 | 0.225 | 0 | 0 | 0.036 | 0 | 0 | 1.503 | 0 | 1.916 | 0.513 | 0.258 | 0 | 0 | 0.273 | 0 | 0.112 | 0 | 0 | 0 | 0.172 | 0 | 0 | 0.114 | 0 | 0 | 0 | 0.003 | 0.974 | 0.126 | 0 | 0 | 0 | 0.335 | 0 | 0 | 0 | 0 | 0 | 0.218 | 0 | 0 | 0.055 | 0 | 0 | 0.36 | 0 | 0.901 | 0 | 0 | 0 | 0 | 0.281 | 0.363 | 0 | 0 | 0 | 0 | 0.017 | 0 | 0 | 0 | 0 | 0.743 | 0 | 0 | 0.192 | 0.688 | 0.147 | 1.26 | 0 | 0 | 0 | 0 | 0 | 0.676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.102 | 0
40 | 19.5 | 0.501 | 0.13 | 0.865 | 0.245 | 0.317 | 0.229 | 0.213 | 0.363 | 1.457 | 0.082 | 2.36 | 0 | 0.272 | 0 | 0.157 | 0.289 | 0.134 | 0.497 | 0.565 | 0.356 | 0 | 0.327 | 0.285 | 0.096 | 0.115 | 1.293 | 0.344 | 0.585 | 0.351 | 1.3 | 0 | 0 | 0.499 | 0.535 | 0.251 | 0.43 | 0.406 | 0 | 0.964 | 0.392 | 0 | 0.083 | 0.475 | 0.342 | 0.572 | 0.275 | 0.234 | 0.004 | 0 | 0.563 | 0.154 | 0.212 | 2.653 | 0.431 | 0.428 | 0.617 | 0.29 | 0.167 | 0.101 | 0.1 | 0 | 0.474 | 0.682 | 0.103 | 0.417 | 0.312 | 0 | 0 | 0.381 | 0 | 0.727 | 0.314 | 0.001 | 0.821 | 0.565 | 0.172 | 0.271 | 0.376 | 0.85 | 0 | 0.015 | 0.007 | 0.238 | 0.111 | 0.474 | 0.102 | 0.276 | 0 | 0.191 | 0.507 | 0.046 | 0 | 0.054 | 0.598 | 0.538 | 0.573 | 0 | 0.105 | 0.476 | 0 | 0.108 | 0.156 | 0.256 | 0.361 | 0.287 | 0.308 | 0.006 | 0.609 | 0.168 | 0.215 | 0.732 | 0.428 | 0.006 | 0 | 0.034 | 0.718 | 0.579 | 2.463 | 0.163 | 0.344 | 0.384 | 0.008 | 0.526 | 0.103 | 0.391 | 0.136 | 0.938 | 0.37 | 0.317 | 0.375 | 0 | 0.32 | 1.985 | 0.227 | 0.337 | 0.189 | 0.306 | 0.223 | 0.353 | 0.379 | 0.083 | 0.326 | 0 | 0.315 | 0 | 0.552 | 0.334 | 0.282 | 0.029 | 2.884 | 0.651 | 0.218 | 0 | 1.235 | 0.273 | 0.503 | 0.199 | 0.164 | 1.322 | 0.291 | 0 | 0.261 | 0.006 | 0.387 | 0.018 | 0.107 | 1.538 | 0.456 | 0.991 | 0.417 | 1.369 | 0 | 0.351 | 0.17 | 1.264 | 0.112 | 0.429 | 0.17 | 0.74 | 0.145 | 0.358 | 0.023 | 0 | 0.078 | 0.452 | 0 | 0.467 | 0.316 | 0.281 | 0 | 0.387 | 0 | 0.255 | 0.329 | 0.04 | 0.351 | 0.242 | 0.174 | 0 | 0 | 0.401 | 0.08 | 1.368 | 0.191 | 0.285 | 0.183 | 0.618 | 0.103 | 0.253 | 0 | 0.231 | 0.283 | 0.396 | 0 | 0.181 | 0.275 | 0.346 | 1.191 | 0.296 | 0.366 | 0.031 | 0.115 | 0.545 | 0.439 | 0.68 | 0.247 | 0.435 | 0 | 0.249 | 0.562 | 0.145 | 0.19 | 0.385 | 0.291 | 1.031 | 0.035 | 0.331 | 0.252 | 0 | 0.342 | 0.349 | 0.387 | 0.049 | 0.38 | 0.119 | 0.683 | 0.614 | 0.208 | 0.363 | 0.078 | 0.3 | 0 | 0.252 | 1.288 | 0.2 | 0.163 | 0 | 0.339 | 0.431 | 0.4 | 0.107 | 0.093
41 | 20 | 1.018 | 0.203 | 0.666 | 0.59 | 0.607 | 0.32 | 0.294 | 0.443 | 1.103 | 0.035 | 2.425 | 0.064 | 0.376 | 0.073 | 0.255 | 0.462 | 0.599 | 0.602 | 0.377 | 0.506 | 0.127 | 0.468 | 0.367 | 0.015 | 0.034 | 2.832 | 1.674 | 0.586 | 0.487 | 0.312 | 0.052 | 0.033 | 0.487 | 0.561 | 0.399 | 0.415 | 2.373 | 0.032 | 0.942 | 0.59 | 0.211 | 0.377 | 0.777 | 0.434 | 0.58 | 0.606 | 0.537 | 0.22 | 0.031 | 0.426 | 0.201 | 0.528 | 2.875 | 1.449 | 0.472 | 1.083 | 0.141 | 0.533 | 0.305 | 0.248 | 0.317 | 0.72 | 1.646 | 0 | 0.998 | 0.228 | 0.559 | 0.177 | 0.836 | 0.03 | 1.416 | 0.464 | 0.275 | 1.526 | 0.314 | 0.04 | 0.331 | 0.585 | 0.116 | 0.126 | 0.048 | 0.17 | 0.029 | 0.099 | 0.819 | 0.149 | 0.653 | 0 | 0.231 | 0.345 | 0.101 | 0.09 | 0.435 | 0.55 | 0.573 | 0.743 | 0.207 | 0.146 | 0.486 | 0.136 | 0.019 | 0.979 | 0.415 | 0.514 | 0.196 | 1.693 | 0.12 | 0.593 | 0.385 | 0.304 | 1.659 | 0.789 | 0.973 | 0.131 | 0.115 | 1.733 | 0.605 | 1.664 | 0.194 | 0.563 | 0.53 | 0.102 | 0.561 | 0.659 | 0.209 | 0.108 | 0.286 | 0.278 | 0.348 | 0.493 | 0.036 | 0.336 | 0.245 | 0.481 | 0.415 | 0.322 | 0.528 | 0.113 | 0.307 | 0.134 | 0.035 | 0.485 | 0.036 | 0.739 | 0.238 | 0.537 | 0.415 | 0.269 | 0.317 | 1.13 | 1.17 | 0.393 | 0.143 | 0.346 | 0.047 | 0.458 | 0.276 | 0.164 | 0.599 | 0.046 | 0.1 | 2.006 | 0.206 | 0.768 | 0.153 | 0.051 | 0.232 | 0.628 | 0.402 | 0.384 | 2.028 | 0.262 | 2.153 | 0.302 | 0.494 | 0.26 | 0.502 | 0.042 | 0.553 | 0.203 | 0.415 | 0.177 | 0.034 | 0.081 | 0.555 | 0.222 | 0.392 | 0.29 | 0.392 | 0.154 | 0.651 | 1.391 | 0.65 | 2.01 | 0.377 | 0.773 | 0.419 | 0.621 | 0.122 | 0.161 | 0.539 | 0.149 | 0.397 | 0.096 | 1.519 | 0.368 | 0.771 | 0.224 | 0.422 | 0.036 | 0.186 | 0.775 | 0.566 | 0.047 | 0.12 | 0.431 | 0.459 | 0.309 | 0.35 | 0.517 | 0.09 | 0.328 | 0.573 | 0.303 | 0.666 | 1.19 | 0.559 | 0.25 | 0.379 | 1.331 | 0.36 | 0.058 | 0.283 | 0.62 | 0.215 | 0.215 | 0.312 | 0.394 | 0.03 | 0.439 | 0.357 | 0.305 | 0.188 | 0.679 | 0.326 | 0.525 | 0.316 | 0.298 | 0.288 | 0.122 | 0.339 | 0.033 | 0.191 | 0.032 | 0.357 | 0.997 | 0.267 | 0.7 | 0.207 | 0.352 | 0.321 | 0.14
42 | 20.5 | 0.664 | 0.434 | 0.594 | 0.527 | 0.701 | 0.188 | 0.373 | 0.749 | 0.711 | 0.072 | 0 | 0.048 | 0.501 | 0.195 | 0.288 | 0.288 | 0.576 | 1.463 | 0.368 | 1.257 | 0.107 | 0.424 | 0.44 | 0.035 | 0.166 | 0 | 1.702 | 0.508 | 0.6 | 0.397 | 0.053 | 0.043 | 0.928 | 0.564 | 0.403 | 0.642 | 0.648 | 0.197 | 1.896 | 0.535 | 0.044 | 0.342 | 0.208 | 0.378 | 0.533 | 0.383 | 0.408 | 0.049 | 0.051 | 0.542 | 0.512 | 2.055 | 0.515 | 1.018 | 2.509 | 0.724 | 0.127 | 0.66 | 0.294 | 1.056 | 0.133 | 1.022 | 2.248 | 0 | 0.727 | 0.659 | 0.447 | 0.04 | 0.727 | 0.12 | 0.98 | 0.631 | 0.052 | 0.864 | 0.437 | 0.071 | 0.993 | 1.832 | 0.108 | 0.483 | 0.055 | 1.781 | 0.046 | 0.04 | 0.735 | 0.05 | 1.325 | 0 | 0.299 | 0.488 | 0.179 | 0.226 | 0.437 | 0.391 | 0.74 | 0.609 | 0.092 | 0.075 | 0.577 | 0.141 | 0.039 | 0.783 | 0.773 | 0.945 | 0.29 | 1.899 | 0.062 | 0.39 | 0.363 | 0.481 | 0.617 | 0.343 | 0.857 | 0.288 | 0.037 | 0.556 | 0.706 | 0.077 | 0.216 | 0.751 | 0.44 | 0.094 | 0.518 | 0.426 | 0.445 | 0.257 | 0.524 | 0.243 | 0.38 | 0.797 | 0.046 | 0.1 | 0 | 0.465 | 0.285 | 0.378 | 0.478 | 0.252 | 0.264 | 0.114 | 0.05 | 0.48 | 0.056 | 2.73 | 0.508 | 0.733 | 0.517 | 0.352 | 0.347 | 0 | 1.15 | 0.305 | 0.069 | 0.303 | 0.054 | 0.607 | 0.37 | 0.096 | 0.935 | 0.211 | 0.042 | 1.591 | 0.046 | 0.717 | 0.106 | 0.055 | 2.048 | 0.643 | 1.276 | 0.754 | 0.527 | 0.07 | 2.465 | 0.189 | 0.567 | 0.196 | 0.308 | 0.274 | 0.483 | 0.56 | 0.538 | 0.097 | 0.054 | 0.178 | 0.651 | 0.064 | 0.716 | 0.6 | 0.535 | 0.186 | 0.852 | 0.617 | 0.6 | 0.901 | 0.516 | 0.419 | 0.335 | 0.548 | 0.142 | 0.11 | 0.758 | 0.231 | 0.314 | 0.195 | 0.135 | 0.766 | 0.637 | 0.401 | 0.517 | 0.233 | 0.942 | 0.456 | 0.761 | 0.101 | 0.224 | 0.638 | 0.91 | 0.453 | 0.363 | 0.421 | 0.369 | 0.528 | 0.805 | 0.048 | 0.777 | 0.235 | 0.506 | 0.049 | 0.582 | 1.338 | 0.37 | 0.383 | 0.1 | 0.719 | 0.274 | 0.56 | 0.396 | 0.57 | 0.257 | 0.442 | 0.255 | 0.435 | 0.05 | 0.814 | 0.389 | 0.523 | 0.471 | 0.306 | 0.41 | 0.055 | 0.391 | 0.048 | 0.137 | 0.044 | 0.346 | 0.02 | 0.431 | 0.787 | 0.059 | 0.305 | 0.238 | 0.102
43 | 21 | 0.745 | 0.376 | 0.537 | 0.444 | 1.045 | 0.343 | 0.44 | 0.448 | 0.245 | 0.14 | 0 | 0.106 | 0.476 | 0.205 | 0.337 | 1.272 | 0.211 | 0.458 | 0.317 | 0.52 | 0.091 | 0.561 | 0.402 | 0.035 | 0.118 | 0 | 0.604 | 0.792 | 0.846 | 0.57 | 0.053 | 0.043 | 0.81 | 0.615 | 0.313 | 0.411 | 0.651 | 0.049 | 0.945 | 0.758 | 0.111 | 0.463 | 0.682 | 0.451 | 0.455 | 0.482 | 0.398 | 0.204 | 0.051 | 0.765 | 0.458 | 0.304 | 0.217 | 0.901 | 0.846 | 0.647 | 0.259 | 0.212 | 0.523 | 1.047 | 0.132 | 0.906 | 0.915 | 0 | 0.969 | 0.303 | 1.052 | 0.04 | 0.685 | 0.151 | 0.696 | 0.7 | 0.228 | 0.493 | 0.738 | 0.213 | 0.281 | 0.525 | 0.071 | 0.506 | 0.055 | 1.476 | 0.153 | 0.102 | 0.546 | 0.05 | 3.07 | 0 | 0.299 | 0.54 | 0.173 | 0.292 | 0.999 | 0.515 | 0.701 | 0.671 | 0.2 | 0.178 | 1.295 | 0.062 | 0.087 | 0.633 | 0.572 | 0.653 | 0.285 | 0.888 | 0.04 | 0.453 | 2.122 | 0.691 | 0.801 | 0.342 | 0.299 | 0.14 | 0.044 | 0.545 | 0.721 | 0.183 | 0.29 | 0.638 | 0.6 | 0.048 | 0.483 | 0.598 | 0.507 | 0.094 | 1.496 | 0.479 | 0.473 | 0.717 | 0.046 | 0.1 | 0 | 0.761 | 0.115 | 0.592 | 0.261 | 0.698 | 0.047 | 0.198 | 0.05 | 0.603 | 0.056 | 2.956 | 0.472 | 0.531 | 0.752 | 0.501 | 0.487 | 0 | 0.662 | 0.521 | 0.052 | 0.389 | 0.218 | 1.615 | 0.503 | 0.168 | 0.743 | 0.261 | 0.115 | 0.902 | 0.145 | 0.517 | 1.009 | 0.166 | 1.487 | 0.66 | 0.664 | 0.415 | 0.446 | 0.141 | 1.923 | 0.242 | 0.595 | 0.369 | 0.557 | 0.184 | 0.537 | 0.516 | 0.347 | 0.568 | 0.36 | 0.121 | 0.496 | 0.202 | 0.834 | 0.233 | 0.562 | 0.174 | 0.56 | 1.244 | 0.557 | 0.968 | 0.454 | 0.291 | 0.134 | 0.385 | 0.051 | 0.049 | 0.634 | 0.56 | 0.349 | 0.366 | 0.298 | 0.264 | 0.969 | 0.529 | 0.576 | 0.127 | 1.132 | 0.52 | 0.639 | 0.033 | 0.374 | 1.169 | 1.203 | 0.552 | 0.162 | 0.454 | 0.213 | 0.367 | 0.622 | 0.284 | 0.98 | 0.702 | 0.132 | 0.312 | 0.64 | 0.797 | 0.322 | 0.495 | 0.053 | 0.487 | 0.393 | 0.428 | 0.486 | 0.614 | 0.275 | 0.737 | 0.403 | 0.729 | 0.05 | 0.642 | 0.576 | 0.958 | 1.034 | 0.181 | 0.369 | 0.055 | 0.035 | 0.166 | 0.114 | 0.144 | 0.313 | 0 | 0.112 | 0.789 | 0.148 | 0.521 | 0.182 | 0.23
44 | 21.5 | 0.711 | 0.55 | 0.488 | 0.829 | 0.867 | 0.562 | 0.356 | 0.517 | 0.048 | 0.05 | 0 | 0.07 | 0.451 | 0.092 | 0.308 | 0.136 | 0.278 | 0.376 | 0.412 | 0.571 | 0.152 | 0.59 | 0.5 | 0.035 | 0.054 | 0 | 1.3 | 0.586 | 0.6 | 0.589 | 0.053 | 0.043 | 0.944 | 0.269 | 0.272 | 0.434 | 0.582 | 0.218 | 0.736 | 0.624 | 0.233 | 0.353 | 0.53 | 0.469 | 0.721 | 0.44 | 0.701 | 0.083 | 0.102 | 0.449 | 0.333 | 0.345 | 0 | 0.57 | 0.464 | 0.501 | 0.153 | 0.319 | 0.3 | 0.537 | 0.249 | 0.601 | 0.425 | 0 | 0.596 | 0.321 | 1.163 | 0.06 | 0.414 | 0.05 | 1.744 | 0.302 | 0.052 | 1.562 | 0.724 | 0.478 | 0.057 | 0.321 | 0.048 | 0.614 | 0.306 | 1.019 | 0.079 | 0.102 | 0.553 | 0.05 | 1.709 | 0 | 0.599 | 0.594 | 0.154 | 0.529 | 2.823 | 0.502 | 0.498 | 0.154 | 0.081 | 0.056 | 1.253 | 0.235 | 0.167 | 0.8 | 0.498 | 0.545 | 0.244 | 0.24 | 0.235 | 0.083 | 0.801 | 0.377 | 0.736 | 0.607 | 0.182 | 0.086 | 0.147 | 0.407 | 0.671 | 0.179 | 0.24 | 0.117 | 0.387 | 0.056 | 0.637 | 0.614 | 0.405 | 0.051 | 0.197 | 0.749 | 0.298 | 0.119 | 0.101 | 0.082 | 0 | 0.614 | 0.096 | 0.41 | 0.047 | 0.26 | 0.224 | 0.053 | 0.05 | 0.576 | 0.056 | 0.432 | 0.281 | 0.622 | 0.519 | 0.586 | 0.286 | 0 | 0.607 | 0.74 | 0.072 | 0.613 | 0.163 | 0.591 | 0.611 | 0.053 | 1.07 | 0.212 | 0.042 | 0.582 | 0.115 | 0.619 | 1.062 | 0.055 | 0.614 | 0.402 | 0.172 | 0.524 | 0.35 | 0.211 | 0.105 | 0.241 | 0.47 | 0.367 | 0.615 | 0.089 | 0.86 | 0.351 | 0.707 | 0.738 | 0.406 | 0.268 | 0.17 | 0.203 | 0.805 | 0.092 | 0.425 | 0.129 | 0.488 | 0.634 | 0.719 | 0.873 | 0.435 | 0.463 | 0.061 | 0.823 | 0.191 | 0.049 | 0.282 | 0.376 | 0.794 | 0.999 | 0.364 | 0.879 | 0.695 | 0.336 | 0.355 | 0.406 | 0.48 | 0.53 | 0.776 | 0.041 | 0.258 | 0.995 | 0.433 | 0.549 | 0.404 | 0.419 | 0.369 | 0.397 | 0.802 | 0.048 | 0.701 | 0.443 | 0.076 | 0.049 | 0.54 | 1.002 | 0.361 | 0.453 | 0.053 | 0.742 | 0.417 | 0.508 | 0.495 | 0.529 | 0.359 | 0.345 | 0.495 | 0.562 | 0.377 | 0.577 | 0.768 | 1.652 | 1.073 | 0.538 | 0.271 | 0.055 | 0.115 | 0.048 | 0.127 | 0.091 | 0.21 | 0 | 0.159 | 0.874 | 0.033 | 0.561 | 0.369 | 0.078
45 | 22 | 0.675 | 0.591 | 0.58 | 0.883 | 0.926 | 0.061 | 0.201 | 0.588 | 0.222 | 0.089 | 0 | 0.119 | 0.129 | 0.197 | 0.317 | 0.289 | 0.133 | 0.475 | 0.729 | 0.358 | 0.14 | 0.565 | 0.444 | 0.035 | 0.054 | 0 | 0.037 | 0.856 | 0.919 | 1.269 | 0.053 | 0.043 | 0.805 | 0.288 | 0.331 | 0.443 | 0.039 | 0.264 | 0.88 | 0.767 | 0.405 | 0.609 | 0.531 | 0.65 | 0.639 | 0.206 | 0.555 | 0.049 | 0.051 | 0.539 | 0.13 | 0.235 | 0 | 0.788 | 0.562 | 0.504 | 0.193 | 0.469 | 0.31 | 0.784 | 0.188 | 0.67 | 0 | 0 | 1.725 | 0.146 | 0.963 | 0.169 | 0.144 | 0.221 | 0.99 | 0.221 | 0.175 | 0.385 | 0.654 | 0.326 | 0.934 | 0.462 | 0.087 | 0.124 | 0.364 | 0.51 | 0.192 | 0.04 | 0.969 | 0.149 | 0 | 0 | 0.32 | 0.559 | 0.175 | 0.348 | 2.424 | 0.449 | 0.435 | 0.443 | 0.104 | 0.525 | 0.798 | 0.062 | 0.039 | 0.521 | 0.51 | 0.703 | 0.385 | 0.064 | 0.04 | 0.146 | 0.492 | 0.514 | 0.743 | 0.369 | 0.388 | 0.279 | 0.512 | 0.705 | 0.742 | 0.1 | 0.45 | 0.165 | 0.513 | 0.147 | 0.758 | 0.149 | 0.549 | 0.17 | 0.193 | 0.516 | 0.271 | 0.119 | 0.234 | 0.051 | 0 | 0.41 | 0.096 | 0.251 | 0.093 | 0.161 | 0.166 | 0.119 | 0.05 | 0.494 | 0.478 | 0 | 0.246 | 0.433 | 0.888 | 0.696 | 0.434 | 0 | 0.46 | 0.824 | 0.368 | 0.679 | 0.069 | 0.439 | 0.216 | 0.234 | 1.069 | 0.197 | 0.046 | 0.054 | 0.046 | 0.818 | 0.058 | 0.166 | 0.334 | 0.551 | 0 | 0.696 | 0.12 | 0.055 | 0 | 0.321 | 0.383 | 0.449 | 0.593 | 0.368 | 1.147 | 0.986 | 0.131 | 0.933 | 0.437 | 0.47 | 0.058 | 0.15 | 0.686 | 0.138 | 0.605 | 0.136 | 0.473 | 1.096 | 0.891 | 0.609 | 0.927 | 0.533 | 0.093 | 0.416 | 0.092 | 0.049 | 0.079 | 0.547 | 0.093 | 0.391 | 0.346 | 1.269 | 1.114 | 0.32 | 0.276 | 0.387 | 0.465 | 0.48 | 0.637 | 0.097 | 0.378 | 0.817 | 0.442 | 0.365 | 0.369 | 0.438 | 0.059 | 1.034 | 0.9 | 0.096 | 0.76 | 0.321 | 0.296 | 0.177 | 0.613 | 1.301 | 0.194 | 0.25 | 0.486 | 1.357 | 0.347 | 0.694 | 0.623 | 0.714 | 0.05 | 0.298 | 1.786 | 0.672 | 0.23 | 0.393 | 1.701 | 0.432 | 0.447 | 0.587 | 0.179 | 0.055 | 0.453 | 0.322 | 0.208 | 0.104 | 0.682 | 0 | 0.174 | 0.568 | 0.156 | 0.739 | 0.298 | 0.292
46 | 22.5 | 0.873 | 1.476 | 0.693 | 0.049 | 0.945 | 0.083 | 0.116 | 0.513 | 0.182 | 0.123 | 0 | 0.057 | 0.174 | 0.124 | 0.446 | 1.455 | 0.069 | 0.227 | 0.513 | 0.217 | 0.148 | 0.897 | 0.651 | 0.035 | 0.235 | 0 | 0 | 0.798 | 1.418 | 0.628 | 0.053 | 0.043 | 0.203 | 0.085 | 0.27 | 0.507 | 0.039 | 0.11 | 0.571 | 1.205 | 0.109 | 0.375 | 0.165 | 0.422 | 0.51 | 0.297 | 0.21 | 0.049 | 0.051 | 0.574 | 0.056 | 0.176 | 0 | 0.799 | 0.341 | 0.82 | 0.225 | 0.152 | 0.463 | 0.402 | 0.084 | 0.831 | 0 | 0 | 0.708 | 0.047 | 0.694 | 0.04 | 0.031 | 0.05 | 0.293 | 0.186 | 0.132 | 0.401 | 0.825 | 0.266 | 0.137 | 0.686 | 0.053 | 0.702 | 0.259 | 0.319 | 0.153 | 0.074 | 0.69 | 0.055 | 0 | 0 | 0.665 | 0.352 | 0.082 | 0.322 | 0 | 0.23 | 0.558 | 0.454 | 0.081 | 0.407 | 0.266 | 0.164 | 0.039 | 0.853 | 0.208 | 0.614 | 0.234 | 0.554 | 0.123 | 0.248 | 0.178 | 0.482 | 0.793 | 0.057 | 0.335 | 0.098 | 0.311 | 0.449 | 0.368 | 0.179 | 0.311 | 0.116 | 0.494 | 0.048 | 0.655 | 0.079 | 0.271 | 0.18 | 0.156 | 0.834 | 0.451 | 0.167 | 0.352 | 0.205 | 0 | 0.668 | 0.212 | 0.366 | 0.145 | 0.228 | 0.047 | 0.049 | 0.05 | 0.586 | 0.39 | 0 | 0.143 | 0.144 | 0.425 | 0.461 | 0.765 | 0 | 0.056 | 0.499 | 0.374 | 0.481 | 0.313 | 0.631 | 0.153 | 0.142 | 0.001 | 0.07 | 0.111 | 0.203 | 0.046 | 0.737 | 0.188 | 0.049 | 0.202 | 0.235 | 0 | 0.33 | 0.049 | 0.261 | 0 | 0.847 | 0.462 | 0.439 | 0.545 | 0.049 | 0.674 | 0.42 | 0.038 | 0.352 | 0.445 | 0.107 | 0.273 | 0.072 | 0 | 0.171 | 0.513 | 0.142 | 0.074 | 0.114 | 0.873 | 0.886 | 0.814 | 0.593 | 0.102 | 0.788 | 0.051 | 0.049 | 0.162 | 0.52 | 0.204 | 0.309 | 0.268 | 0.412 | 0.98 | 0.666 | 0.074 | 0.49 | 0.35 | 0.426 | 0.677 | 0.033 | 0.211 | 0.822 | 0.348 | 0.361 | 0.301 | 0.275 | 0.182 | 0.305 | 0.762 | 0.236 | 0.893 | 0.199 | 0.342 | 0.097 | 0.397 | 0.561 | 0.041 | 0.213 | 0.452 | 2.145 | 0.118 | 1.359 | 0.876 | 0.737 | 0.05 | 0.347 | 0.388 | 0.591 | 0.256 | 0.521 | 0.793 | 0.498 | 0.687 | 0.486 | 0.428 | 0.055 | 0.159 | 0.048 | 0.114 | 0.131 | 0.38 | 0 | 0.072 | 0.942 | 0.167 | 0.057 | 0.271 | 0.495
47 | 23 | 0.794 | 0.297 | 0.073 | 0 | 0.538 | 0.091 | 0.097 | 0.713 | 0.197 | 0.05 | 0 | 0.128 | 0.06 | 0.845 | 0.396 | 0.868 | 0.18 | 0.185 | 0.435 | 0.205 | 0.095 | 0 | 0.798 | 0.035 | 0.104 | 0 | 0 | 0.872 | 0.886 | 0.685 | 0.053 | 0.043 | 0 | 0.047 | 0.371 | 0.478 | 0.039 | 0.136 | 0 | 0.093 | 0.158 | 0.667 | 0.052 | 0.133 | 0.586 | 0.066 | 0.108 | 0.239 | 0.051 | 0.043 | 0.251 | 0.108 | 0 | 0.016 | 0.612 | 0.294 | 0.208 | 0.243 | 0.26 | 0.129 | 0.243 | 0.999 | 0 | 0 | 0.526 | 0.107 | 0.059 | 0.122 | 0.031 | 0.12 | 0 | 0.394 | 0.271 | 0.626 | 0.826 | 0.362 | 0.151 | 0.683 | 0.126 | 0.414 | 0.055 | 0.142 | 0.046 | 0.093 | 1.179 | 0.066 | 0 | 0 | 0.054 | 0.041 | 0.059 | 0.614 | 0 | 0.053 | 0.283 | 0.36 | 0.261 | 0.848 | 0.203 | 0.133 | 0.079 | 0.563 | 0.144 | 0.239 | 0.503 | 0.23 | 0.14 | 0.055 | 0.053 | 0.536 | 0.784 | 0.224 | 0.041 | 0.201 | 0.883 | 0.364 | 0 | 0.137 | 0.368 | 0.221 | 0.673 | 0.048 | 0.582 | 0.068 | 0.173 | 0.185 | 0.05 | 0.356 | 0.11 | 0.335 | 0.131 | 0.103 | 0 | 0.386 | 0.366 | 0.155 | 0.047 | 0.331 | 0.047 | 0.049 | 0.05 | 0.495 | 2.033 | 0 | 0.152 | 0.217 | 0.161 | 0.37 | 0.056 | 0 | 0.056 | 0.435 | 0.43 | 0.31 | 0.054 | 0.059 | 0.036 | 0.197 | 0 | 0.056 | 0.07 | 0.157 | 0.192 | 0.702 | 0.079 | 0.049 | 0 | 0.115 | 0 | 0.261 | 0.144 | 0.091 | 0 | 0.289 | 0.185 | 0.44 | 0.038 | 0.117 | 1.002 | 0.38 | 0.139 | 0.486 | 0.29 | 0.169 | 0.148 | 0.334 | 0 | 0.206 | 0.129 | 0.142 | 0.199 | 0 | 0.848 | 0.27 | 0.611 | 0.546 | 0.118 | 0.274 | 0.166 | 0.049 | 0.178 | 0.344 | 0.141 | 0.168 | 0.273 | 0.621 | 0.18 | 0.046 | 0.163 | 0.25 | 0.048 | 0.161 | 0.667 | 0.105 | 1.244 | 0.754 | 0.082 | 0.103 | 0.458 | 0.201 | 1.538 | 0.506 | 0.58 | 0.048 | 0.226 | 0.222 | 0.394 | 0.081 | 0.429 | 0 | 0.112 | 0.067 | 0.713 | 0.811 | 0.043 | 0.321 | 0.552 | 0.704 | 0.05 | 0.053 | 0 | 0.507 | 0.389 | 0.15 | 0.263 | 0.175 | 0.269 | 0.653 | 0.38 | 0.055 | 0.139 | 0.048 | 0.127 | 0.044 | 0.428 | 0 | 0.242 | 0.607 | 0.039 | 0.208 | 0.318 | 0.091
48 | 23.5 | 0.175 | 0.052 | 0.3 | 0 | 0 | 0.057 | 0.099 | 0.891 | 0.252 | 0.162 | 0 | 0.048 | 0.331 | 0.34 | 0.475 | 0.081 | 0.21 | 0.038 | 0.384 | 0.678 | 0.202 | 0 | 0.512 | 0.035 | 0.054 | 0 | 0 | 0.838 | 0.241 | 0.245 | 0.053 | 0.043 | 0 | 0.047 | 0.059 | 0.557 | 0.11 | 0.049 | 0 | 0.251 | 0.091 | 0.464 | 0.165 | 0.089 | 0.372 | 0.192 | 0.071 | 0.049 | 0.051 | 0.142 | 0.091 | 0.051 | 0 | 0 | 0.191 | 0.153 | 0.212 | 0.107 | 0.106 | 0.036 | 0.225 | 0.134 | 0 | 0 | 0.385 | 0.055 | 0.202 | 0.108 | 0.144 | 0.151 | 0 | 0.626 | 0.068 | 0 | 0.647 | 0.557 | 0.187 | 0.338 | 0.048 | 0.341 | 0.055 | 0.058 | 0.132 | 0.173 | 0.704 | 0.138 | 0 | 0 | 0.054 | 0.041 | 0.059 | 0.442 | 0 | 0.131 | 0.279 | 0.337 | 0.04 | 0.323 | 0.158 | 0.062 | 0.175 | 0.047 | 0.275 | 0.209 | 0.565 | 0.295 | 0.052 | 0.118 | 0.053 | 0.222 | 0 | 0.057 | 0.151 | 0.172 | 0.757 | 0.205 | 0 | 0.179 | 0.624 | 0.052 | 0.513 | 0.086 | 0.323 | 0.161 | 0.346 | 0.641 | 0.194 | 0.136 | 0.052 | 0.128 | 0.081 | 0.055 | 0 | 0.055 | 0.424 | 0.298 | 0.047 | 0.211 | 0.343 | 0.181 | 0.05 | 0.328 | 0.486 | 0 | 0.088 | 0.058 | 0.295 | 0.192 | 0.199 | 0 | 0.129 | 0.548 | 0.409 | 0.057 | 0.32 | 0.141 | 0.048 | 0.179 | 0 | 0.077 | 0.087 | 0.061 | 0.725 | 0.321 | 0.058 | 0.068 | 0 | 0.279 | 0 | 0.164 | 0.049 | 0.22 | 0 | 0.048 | 0.029 | 0.253 | 0.153 | 0.23 | 0.063 | 0.055 | 0.038 | 0.569 | 0.125 | 0.601 | 0.058 | 0.046 | 0 | 0.193 | 0.047 | 0.218 | 0.05 | 0 | 0.055 | 0 | 0.83 | 0.235 | 0.077 | 0.072 | 0.117 | 0.049 | 0.056 | 0.244 | 0.069 | 0.225 | 0.341 | 0.168 | 0.938 | 0.176 | 0.176 | 0.048 | 0.167 | 0.187 | 0.134 | 0.033 | 0.224 | 0.73 | 0.089 | 0.074 | 0.109 | 0.149 | 1.405 | 0.171 | 0.991 | 0.233 | 0 | 0.572 | 0.179 | 0.193 | 0.094 | 0 | 0.041 | 0.071 | 0.161 | 0 | 0.043 | 0.169 | 0.794 | 0.123 | 0.05 | 0.063 | 0 | 0.646 | 0.453 | 0.135 | 0.056 | 0.13 | 0 | 0.049 | 0.187 | 0.055 | 0.155 | 0.083 | 0.179 | 0.171 | 0.342 | 0 | 0.082 | 0.118 | 0.207 | 0.113 | 0.044 | 0.052

## 7. PV allocation (per period)
TR6 PV allocation — per half-hour
VIOLET = aggregated live from the raw sheets 3–6 (SUM / SUMIF). AMBER = priority split (MIN formulas): PV → prosumer load → battery → customer load → export.
period | hour (h) | PV (kW) | prosumer load (kW) | customer load (kW) | batt charge (kW) | batt discharge (kW) | batt net =chg−dis | PV→ prosumer | PV→ battery | PV→ customer | PV→ export | customer ←grid
1 | 0 | 0 | 63.538 | 58.8824 | 0 | 63.492 | -63.492 | 0 | 0 | 0 | 0 | 58.8824
2 | 0.5 | 0 | 46.2847 | 52.9115 | 0 | 45.655 | -45.655 | 0 | 0 | 0 | 0 | 52.9115
3 | 1 | 0 | 41.3772 | 37.2163 | 0 | 39.568 | -39.568 | 0 | 0 | 0 | 0 | 37.2163
4 | 1.5 | 0 | 37.7649 | 36.4015 | 0 | 34.879 | -34.879 | 0 | 0 | 0 | 0 | 36.4015
5 | 2 | 0 | 34.5654 | 34.8459 | 0 | 32.15 | -32.15 | 0 | 0 | 0 | 0 | 34.8459
6 | 2.5 | 0 | 33.7339 | 33.9527 | 0 | 31.599 | -31.599 | 0 | 0 | 0 | 0 | 33.9527
7 | 3 | 0 | 31.6651 | 33.9904 | 0 | 28.728 | -28.728 | 0 | 0 | 0 | 0 | 33.9904
8 | 3.5 | 0.6879 | 34.9888 | 34.817 | 0 | 30.153 | -30.153 | 0.6879 | 0 | 0 | 0 | 34.817
9 | 4 | 9.9708 | 29.6935 | 32.1085 | 0.09 | 17.9106 | -17.8206 | 9.9708 | 0 | 0 | 0 | 32.1085
10 | 4.5 | 46.6337 | 31.6683 | 33.6113 | 19.047 | 3.472 | 15.575 | 31.6683 | 14.9654 | 0 | 0 | 33.6113
11 | 5 | 92.495 | 31.109 | 31.6131 | 61.641 | 0.156 | 61.485 | 31.109 | 61.386 | 0 | 0 | 31.6131
12 | 5.5 | 148.7466 | 32.4932 | 33.1521 | 117.26 | 1.017 | 116.243 | 32.4932 | 116.243 | 0.0104 | 0 | 33.1417
13 | 6 | 210.1039 | 37.8365 | 32.8683 | 173.313 | 1.031 | 172.282 | 37.8365 | 172.2674 | 0 | 0 | 32.8683
14 | 6.5 | 272.2248 | 38.2355 | 45.8151 | 235.825 | 1.825 | 234 | 38.2355 | 233.9893 | 0 | 0 | 45.8151
15 | 7 | 334.029 | 47.7215 | 53.3642 | 287.915 | 1.614 | 286.301 | 47.7215 | 286.301 | 0.0065 | 0 | 53.3577
16 | 7.5 | 395.9099 | 59.6095 | 62.2978 | 314.715 | 3.268 | 311.447 | 59.6095 | 311.447 | 24.8534 | 0 | 37.4444
17 | 8 | 453.9941 | 73.3317 | 82.3893 | 209.761 | 4.874 | 204.887 | 73.3317 | 204.887 | 82.3893 | 93.3861 | 0
18 | 8.5 | 508.6024 | 87.7537 | 90.4962 | 129.311 | 4.867 | 124.444 | 87.7537 | 124.444 | 90.4962 | 205.9085 | 0
19 | 9 | 555.1017 | 94.2237 | 96.7693 | 80.213 | 3.802 | 76.411 | 94.2237 | 76.411 | 96.7693 | 287.6977 | 0
20 | 9.5 | 594.7632 | 101.1567 | 101.8928 | 58.076 | 5.658 | 52.418 | 101.1567 | 52.418 | 101.8928 | 339.2957 | 0
21 | 10 | 629.57 | 82.3651 | 114.194 | 38.4223 | 1.749 | 36.6733 | 82.3651 | 36.6733 | 114.194 | 396.3376 | 0
22 | 10.5 | 658.3056 | 97.1633 | 106.8198 | 21.439 | 5.971 | 15.468 | 97.1633 | 15.468 | 106.8198 | 438.8545 | 0
23 | 11 | 678.6903 | 90.1161 | 105.0552 | 15.167 | 7.714 | 7.453 | 90.1161 | 7.453 | 105.0552 | 476.066 | 0
24 | 11.5 | 687.6348 | 94.0169 | 113.3247 | 13.975 | 4.438 | 9.537 | 94.0169 | 9.537 | 113.3247 | 470.7562 | 0
25 | 12 | 690.2213 | 97.2896 | 105.9461 | 10.811 | 3.412 | 7.399 | 97.2896 | 7.399 | 105.9461 | 479.5866 | 0
26 | 12.5 | 685.3727 | 89.8286 | 95.3539 | 8.768 | 1.187 | 7.581 | 89.8286 | 7.581 | 95.3539 | 492.6092 | 0
27 | 13 | 669.1046 | 88.473 | 95.2358 | 9.004 | 2.106 | 6.898 | 88.473 | 6.898 | 95.2358 | 478.4978 | 0
28 | 13.5 | 644.271 | 87.7507 | 80.5411 | 3.947 | 1.598 | 2.349 | 87.7507 | 2.349 | 80.5411 | 473.6302 | 0
29 | 14 | 614.6327 | 89.1062 | 80.8716 | 5.04 | 1.813 | 3.227 | 89.1062 | 3.227 | 80.8716 | 441.4279 | 0
30 | 14.5 | 577.0765 | 82.9663 | 89.0334 | 2.177 | 2.31 | -0.133 | 82.9663 | 0 | 89.0334 | 405.0768 | 0
31 | 15 | 537.1631 | 85.7534 | 86.8858 | 0.754 | 8.125 | -7.371 | 85.7534 | 0 | 86.8858 | 364.5239 | 0
32 | 15.5 | 489.1358 | 82.7183 | 79.4787 | 3.626 | 4.725 | -1.099 | 82.7183 | 0 | 79.4787 | 326.9388 | 0
33 | 16 | 435.0475 | 81.6394 | 88.7221 | 4.217 | 6.521 | -2.304 | 81.6394 | 0 | 88.7221 | 264.686 | 0
34 | 16.5 | 369.7385 | 91.7647 | 85.899 | 5.002 | 9.283 | -4.281 | 91.7647 | 0 | 85.899 | 192.0748 | 0
35 | 17 | 308.6096 | 99.738 | 91.0966 | 7.148 | 11.815 | -4.667 | 99.738 | 0 | 91.0966 | 117.775 | 0
36 | 17.5 | 245.7995 | 111.1502 | 109.1354 | 6.099 | 27.556 | -21.457 | 111.1502 | 0 | 109.1354 | 25.5139 | 0
37 | 18 | 185.0458 | 104.5699 | 115.1052 | 7.053 | 30.668 | -23.615 | 104.5699 | 0 | 80.4759 | 0 | 34.6293
38 | 18.5 | 126.4714 | 111.2248 | 99.2655 | 5.572 | 42.251 | -36.679 | 111.2248 | 0 | 15.2466 | 0 | 84.0189
39 | 19 | 73.8461 | 105.5379 | 107.9193 | 3.196 | 50.096 | -46.9 | 73.8461 | 0 | 0 | 0 | 107.9193
40 | 19.5 | 21.4936 | 116.513 | 126.2189 | 0.1825 | 93.991 | -93.8085 | 21.4936 | 0 | 0 | 0 | 126.2189
41 | 20 | 3.9673 | 132.6328 | 129.7305 | 0 | 126.362 | -126.362 | 3.9673 | 0 | 0 | 0 | 129.7305
42 | 20.5 | 0 | 139.3129 | 131.925 | 0 | 127.361 | -127.361 | 0 | 0 | 0 | 0 | 131.925
43 | 21 | 0 | 134.7812 | 135.0555 | 0 | 126.249 | -126.249 | 0 | 0 | 0 | 0 | 135.0555
44 | 21.5 | 0 | 119.3487 | 133.2186 | 0 | 110.453 | -110.453 | 0 | 0 | 0 | 0 | 133.2186
45 | 22 | 0 | 118.9366 | 134.1548 | 0 | 109.032 | -109.032 | 0 | 0 | 0 | 0 | 134.1548
46 | 22.5 | 0 | 105.9755 | 125.1535 | 0 | 89.609 | -89.609 | 0 | 0 | 0 | 0 | 125.1535
47 | 23 | 0 | 84.9062 | 95.6281 | 0 | 68.992 | -68.992 | 0 | 0 | 0 | 0 | 95.6281
48 | 23.5 | 0 | 63.3695 | 74.256 | 0 | 49.181 | -49.181 | 0 | 0 | 0 | 0 | 74.256
TOTAL | kWh/day | 6477.2304 | 1888.8498 | 1977.3099 | 929.3834 | 740.1433 | 189.2401 | 1206.3698 | 875.6722 | 1009.8668 | 3385.3216 | 967.4431
Each half-hour is 0.5 h, so daily energy (kWh) = Σ(power in kW) × 0.5.
Trace any input: e.g. cell C5 = SUM of column C on sheet 3 (PV of all 534 connections at 00:00). Click it to see the formula.

## 8. Results & charts
TR6 PV allocation — results
Where the day's PV goes |  |  | How the customers (272) are supplied
Destination | kWh/day | % of PV | Source | kWh/day | % of cust. load
PV → prosumers' own load | 1206.3698 | 18.62% | From prosumer PV (day) | 1009.8668 | 51.07%
PV → battery storage | 875.6722 | 13.52% | From grid import (night) | 967.4431 | 48.93%
PV → customers | 1009.8668 | 15.59% | TOTAL customer load | 1977.3099 | 100%
PV → export to grid | 3385.3216 | 52.26%
TOTAL (= PV) | 6477.2304 | 100%
Charts read live from sheet 7, which reads live from raw sheets 3–6.