## 1. Overview
TR9 — Where does the PV energy go?
Prosumers vs. pure customers — every kWh traced from the raw model inputs
Purpose
This workbook accounts for every kWh of PV generated on transformer TR9 over one representative day, and it is fully auditable: nothing is hand-typed except the raw model outputs. Follow the data chain below — each step is a live formula, so changing any raw number updates everything.
The data chain (how each number is built)
Sheet 3 · Raw PV per load | The PV profile of every connection, 48 half-hours. Copied verbatim from TR9_load_PV_48periods.xlsx (sheet PV_generation_kW). Customers = 0.
Sheet 4 · Raw load per load | The load profile of every connection, 48 half-hours, tagged prosumer / customer. Copied from TR9_load_PV_48periods.xlsx (sheet Load_P_kW).
Sheet 5 · Raw batt charge | Charging power of every battery, 48 half-hours. Copied from the rolling dispatch TR9_analysis_data.xlsx (sheet Charge_kW).
Sheet 6 · Raw batt discharge | Discharging power of every battery. Copied from the same run (Discharge_kW).
Sheet 7 · PV allocation | Per half-hour: the five blue inputs are AGGREGATED from sheets 3–6 by SUM / SUMIF; the amber columns then split the PV by the priority rule.
Sheets 1 & 8 · Results | Daily totals (Σ×0.5 h) and shares. Every headline cell links to sheet 7.
The aggregation formulas (sheet 7, per half-hour)
PV (all)
prosumer load
customer load
battery charge
battery discharge
Headline results (all linked live to sheet 7)
Quantity | Value | Unit
Prosumers (PV + battery) | 90 | connections
Pure customers (load only) | 82 | connections
PV generated | 2241.1862 | kWh/day
PV → prosumers' own load (direct) | 399.9009 | kWh/day
PV → battery storage | 306.736 | kWh/day
PV → customers | 319.0854 | kWh/day
PV → export to grid | 1215.4639 | kWh/day
PV share reaching customers | 14.24% | % of PV
Customer load covered by PV | 52.73% | % of customer load
Customer load covered by grid | 47.27% | % of customer load
Colour key & provenance
• LIGHT-BLUE cell = data belonging to a prosumer (its rooftop PV, load, or battery). WHITE = a pure customer (load only). On sheet 7: VIOLET = value aggregated live from the raw sheets (SUM/SUMIF); AMBER = allocation formula; GREEN = daily total (Σ × 0.5 h).
• Per-load PV & load profiles: results/tables/TR9_load_PV_48periods.xlsx (built from OpData.xls).
• Per-battery charge/discharge: TR9_analysis/01_DAILY_ROLLING_DISPATCH/TR9_analysis_data.xlsx (exact-QCP rolling dispatch, RunFOR_Rolling, CPLEX).
• Load classification (PV size > 0 = prosumer): sheet 'Customers' of the load/PV workbook.
• Method note: priority energy allocation per half-hour; downstream network + battery round-trip losses (~3–4% of PV) are not separated out in the per-period disposition.

## 2. Load classification
TR9 load classification — 172 connections
90 prosumers (PV + battery) · 82 pure customers (load only)
ID | Load name | Bus | Phase | PV size (kW) | Type
2259 | Load_TR9_F2_1 | TR9_two130 | 3 | 0 | customer
2260 | Load_TR9_F2_10 | TR9_two249 | 1 | 0 | customer
2263 | Load_TR9_F2_13 | TR9_two283 | 2 | 0 | customer
2270 | Load_TR9_F2_2 | TR9_two137 | 2 | 0 | customer
2273 | Load_TR9_F2_3 | TR9_two149 | 2 | 0 | customer
2274 | Load_TR9_F2_4 | TR9_two217 | 1 | 0 | customer
2276 | Load_TR9_F2_6 | TR9_two229 | 1 | 0 | customer
2278 | Load_TR9_F2_8 | TR9_two238 | 3 | 0 | customer
2279 | Load_TR9_F2_9 | TR9_two242 | 2 | 0 | customer
2280 | Load_TR9_F5_1 | TR9_five58 | 3 | 0 | customer
2284 | Load_TR9_F5_13 | TR9_five168 | 1 | 0 | customer
2287 | Load_TR9_F5_16 | TR9_five186 | 3 | 0 | customer
2288 | Load_TR9_F5_17 | TR9_five194 | 3 | 0 | customer
2289 | Load_TR9_F5_18 | TR9_five199 | 3 | 0 | customer
2292 | Load_TR9_F5_20 | TR9_five223 | 1 | 0 | customer
2293 | Load_TR9_F5_21 | TR9_five242 | 1 | 0 | customer
2294 | Load_TR9_F5_22 | TR9_five243 | 2 | 0 | customer
2296 | Load_TR9_F5_24 | TR9_five285 | 2 | 0 | customer
2297 | Load_TR9_F5_25 | TR9_five303 | 2 | 0 | customer
2298 | Load_TR9_F5_26 | TR9_five309 | 3 | 0 | customer
2299 | Load_TR9_F5_27 | TR9_five324 | 2 | 0 | customer
2304 | Load_TR9_F5_31 | TR9_five421 | 1 | 0 | customer
2306 | Load_TR9_F5_33 | TR9_five451 | 1 | 0 | customer
2307 | Load_TR9_F5_34 | TR9_five457 | 2 | 0 | customer
2308 | Load_TR9_F5_35 | TR9_five466 | 1 | 0 | customer
2309 | Load_TR9_F5_36 | TR9_five472 | 1 | 0 | customer
2310 | Load_TR9_F5_37 | TR9_five488 | 2 | 0 | customer
2311 | Load_TR9_F5_38 | TR9_five494 | 2 | 0 | customer
2314 | Load_TR9_F5_40 | TR9_five512 | 1 | 0 | customer
2315 | Load_TR9_F5_41 | TR9_five513 | 2 | 0 | customer
2317 | Load_TR9_F5_43 | TR9_five537 | 3 | 0 | customer
2318 | Load_TR9_F5_44 | TR9_five540 | 1 | 0 | customer
2320 | Load_TR9_F5_46 | TR9_five551 | 3 | 0 | customer
2321 | Load_TR9_F5_47 | TR9_five585 | 1 | 0 | customer
2323 | Load_TR9_F5_49 | TR9_five631 | 2 | 0 | customer
2324 | Load_TR9_F5_5 | TR9_five108 | 2 | 0 | customer
2325 | Load_TR9_F5_50 | TR9_five649 | 1 | 0 | customer
2326 | Load_TR9_F5_51 | TR9_five663 | 3 | 0 | customer
2329 | Load_TR9_F5_54 | TR9_five695 | 1 | 0 | customer
2332 | Load_TR9_F5_57 | TR9_five733 | 3 | 0 | customer
2333 | Load_TR9_F5_58 | TR9_five735 | 1 | 0 | customer
2336 | Load_TR9_F5_60 | TR9_five750 | 2 | 0 | customer
2338 | Load_TR9_F5_62 | TR9_five793 | 1 | 0 | customer
2341 | Load_TR9_F5_65 | TR9_five809 | 2 | 0 | customer
2342 | Load_TR9_F5_66 | TR9_five831 | 3 | 0 | customer
2344 | Load_TR9_F5_68 | TR9_five905 | 2 | 0 | customer
2345 | Load_TR9_F5_7 | TR9_five118 | 2 | 0 | customer
2347 | Load_TR9_F5_9 | TR9_five129 | 3 | 0 | customer
2348 | Load_TR9_F6_1 | TR9_six64 | 1 | 0 | customer
2349 | Load_TR9_F6_10 | TR9_six154 | 3 | 0 | customer
2350 | Load_TR9_F6_11 | TR9_six173 | 3 | 0 | customer
2357 | Load_TR9_F6_18 | TR9_six254 | 2 | 0 | customer
2359 | Load_TR9_F6_2 | TR9_six68 | 3 | 0 | customer
2361 | Load_TR9_F6_21 | TR9_six317 | 3 | 0 | customer
2363 | Load_TR9_F6_23 | TR9_six329 | 1 | 0 | customer
2364 | Load_TR9_F6_24 | TR9_six342 | 1 | 0 | customer
2366 | Load_TR9_F6_26 | TR9_six350 | 2 | 0 | customer
2369 | Load_TR9_F6_29 | TR9_six378 | 1 | 0 | customer
2370 | Load_TR9_F6_3 | TR9_six75 | 1 | 0 | customer
2373 | Load_TR9_F6_32 | TR9_six392 | 3 | 0 | customer
2374 | Load_TR9_F6_33 | TR9_six410 | 1 | 0 | customer
2377 | Load_TR9_F6_36 | TR9_six484 | 2 | 0 | customer
2380 | Load_TR9_F6_39 | TR9_six518 | 2 | 0 | customer
2384 | Load_TR9_F6_42 | TR9_six571 | 3 | 0 | customer
2386 | Load_TR9_F6_44 | TR9_six591 | 3 | 0 | customer
2387 | Load_TR9_F6_45 | TR9_six595 | 2 | 0 | customer
2389 | Load_TR9_F6_47 | TR9_six643 | 1 | 0 | customer
2392 | Load_TR9_F6_5 | TR9_six87 | 1 | 0 | customer
2393 | Load_TR9_F6_50 | TR9_six652 | 1 | 0 | customer
2394 | Load_TR9_F6_51 | TR9_six665 | 2 | 0 | customer
2395 | Load_TR9_F6_52 | TR9_six667 | 1 | 0 | customer
2396 | Load_TR9_F6_53 | TR9_six699 | 3 | 0 | customer
2399 | Load_TR9_F6_56 | TR9_six723 | 2 | 0 | customer
2410 | Load_TR9_F6_66 | TR9_six869 | 3 | 0 | customer
2412 | Load_TR9_F6_68 | TR9_six894 | 2 | 0 | customer
2413 | Load_TR9_F6_69 | TR9_six909 | 3 | 0 | customer
2414 | Load_TR9_F6_7 | TR9_six105 | 1 | 0 | customer
2417 | Load_TR9_F6_72 | TR9_six929 | 1 | 0 | customer
2419 | Load_TR9_F6_74 | TR9_six945 | 3 | 0 | customer
2420 | Load_TR9_F6_75 | TR9_six952 | 1 | 0 | customer
2423 | Load_TR9_F6_78 | TR9_six979 | 1 | 0 | customer
2427 | Load_TR9_F6_81 | TR9_six1020 | 1 | 0 | customer
2261 | Load_TR9_F2_11 | TR9_two267 | 3 | 3 | prosumer
2262 | Load_TR9_F2_12 | TR9_two275 | 3 | 4 | prosumer
2264 | Load_TR9_F2_14 | TR9_two292 | 2 | 4 | prosumer
2265 | Load_TR9_F2_15 | TR9_two306 | 1 | 4 | prosumer
2266 | Load_TR9_F2_16 | TR9_two308 | 1 | 4 | prosumer
2267 | Load_TR9_F2_17 | TR9_two312 | 3 | 3.5 | prosumer
2268 | Load_TR9_F2_18 | TR9_two313 | 3 | 4 | prosumer
2269 | Load_TR9_F2_19 | TR9_two315 | 1 | 3.5 | prosumer
2271 | Load_TR9_F2_20 | TR9_two316 | 1 | 3.5 | prosumer
2272 | Load_TR9_F2_21 | TR9_two339 | 1 | 2 | prosumer
2275 | Load_TR9_F2_5 | TR9_two225 | 3 | 3 | prosumer
2277 | Load_TR9_F2_7 | TR9_two233 | 1 | 4 | prosumer
2281 | Load_TR9_F5_10 | TR9_five147 | 3 | 3 | prosumer
2282 | Load_TR9_F5_11 | TR9_five149 | 1 | 2 | prosumer
2283 | Load_TR9_F5_12 | TR9_five160 | 3 | 3 | prosumer
2285 | Load_TR9_F5_14 | TR9_five170 | 1 | 4 | prosumer
2286 | Load_TR9_F5_15 | TR9_five177 | 1 | 1.5 | prosumer
2290 | Load_TR9_F5_19 | TR9_five220 | 3 | 3.5 | prosumer
2291 | Load_TR9_F5_2 | TR9_five67 | 3 | 2 | prosumer
2295 | Load_TR9_F5_23 | TR9_five284 | 3 | 3.5 | prosumer
2300 | Load_TR9_F5_28 | TR9_five345 | 1 | 3.5 | prosumer
2301 | Load_TR9_F5_29 | TR9_five355 | 1 | 3 | prosumer
2302 | Load_TR9_F5_3 | TR9_five78 | 1 | 4 | prosumer
2303 | Load_TR9_F5_30 | TR9_five394 | 3 | 2.5 | prosumer
2305 | Load_TR9_F5_32 | TR9_five445 | 3 | 4 | prosumer
2312 | Load_TR9_F5_39 | TR9_five499 | 2 | 4 | prosumer
2313 | Load_TR9_F5_4 | TR9_five92 | 1 | 4 | prosumer
2316 | Load_TR9_F5_42 | TR9_five520 | 3 | 4 | prosumer
2319 | Load_TR9_F5_45 | TR9_five545 | 2 | 2 | prosumer
2322 | Load_TR9_F5_48 | TR9_five588 | 1 | 4 | prosumer
2327 | Load_TR9_F5_52 | TR9_five670 | 3 | 2.5 | prosumer
2328 | Load_TR9_F5_53 | TR9_five685 | 2 | 2.5 | prosumer
2330 | Load_TR9_F5_55 | TR9_five704 | 1 | 4 | prosumer
2331 | Load_TR9_F5_56 | TR9_five719 | 1 | 1.5 | prosumer
2334 | Load_TR9_F5_59 | TR9_five748 | 2 | 2 | prosumer
2335 | Load_TR9_F5_6 | TR9_five117 | 2 | 3 | prosumer
2337 | Load_TR9_F5_61 | TR9_five778 | 2 | 4 | prosumer
2339 | Load_TR9_F5_63 | TR9_five799 | 3 | 3.5 | prosumer
2340 | Load_TR9_F5_64 | TR9_five801 | 3 | 3.5 | prosumer
2343 | Load_TR9_F5_67 | TR9_five881 | 3 | 4 | prosumer
2346 | Load_TR9_F5_8 | TR9_five123 | 2 | 3 | prosumer
2351 | Load_TR9_F6_12 | TR9_six186 | 1 | 2 | prosumer
2352 | Load_TR9_F6_13 | TR9_six191 | 2 | 3.5 | prosumer
2353 | Load_TR9_F6_14 | TR9_six203 | 1 | 2.5 | prosumer
2354 | Load_TR9_F6_15 | TR9_six232 | 3 | 4 | prosumer
2355 | Load_TR9_F6_16 | TR9_six238 | 1 | 2 | prosumer
2356 | Load_TR9_F6_17 | TR9_six249 | 2 | 3 | prosumer
2358 | Load_TR9_F6_19 | TR9_six269 | 3 | 1.5 | prosumer
2360 | Load_TR9_F6_20 | TR9_six289 | 3 | 2.5 | prosumer
2362 | Load_TR9_F6_22 | TR9_six326 | 1 | 4 | prosumer
2365 | Load_TR9_F6_25 | TR9_six349 | 1 | 2.5 | prosumer
2367 | Load_TR9_F6_27 | TR9_six362 | 3 | 2.5 | prosumer
2368 | Load_TR9_F6_28 | TR9_six365 | 3 | 2.5 | prosumer
2371 | Load_TR9_F6_30 | TR9_six385 | 2 | 3 | prosumer
2372 | Load_TR9_F6_31 | TR9_six387 | 1 | 2 | prosumer
2375 | Load_TR9_F6_34 | TR9_six431 | 3 | 2.5 | prosumer
2376 | Load_TR9_F6_35 | TR9_six441 | 1 | 1.5 | prosumer
2378 | Load_TR9_F6_37 | TR9_six501 | 1 | 4 | prosumer
2379 | Load_TR9_F6_38 | TR9_six512 | 2 | 3 | prosumer
2381 | Load_TR9_F6_4 | TR9_six82 | 1 | 4 | prosumer
2382 | Load_TR9_F6_40 | TR9_six523 | 3 | 3.5 | prosumer
2383 | Load_TR9_F6_41 | TR9_six534 | 2 | 1.5 | prosumer
2385 | Load_TR9_F6_43 | TR9_six583 | 1 | 4 | prosumer
2388 | Load_TR9_F6_46 | TR9_six625 | 1 | 4 | prosumer
2390 | Load_TR9_F6_48 | TR9_six646 | 2 | 4 | prosumer
2391 | Load_TR9_F6_49 | TR9_six651 | 3 | 3 | prosumer
2397 | Load_TR9_F6_54 | TR9_six718 | 3 | 4 | prosumer
2398 | Load_TR9_F6_55 | TR9_six721 | 1 | 3.5 | prosumer
2400 | Load_TR9_F6_57 | TR9_six740 | 1 | 1.5 | prosumer
2401 | Load_TR9_F6_58 | TR9_six758 | 2 | 2 | prosumer
2402 | Load_TR9_F6_59 | TR9_six784 | 2 | 4 | prosumer
2403 | Load_TR9_F6_6 | TR9_six90 | 2 | 2 | prosumer
2404 | Load_TR9_F6_60 | TR9_six799 | 2 | 3 | prosumer
2405 | Load_TR9_F6_61 | TR9_six801 | 3 | 2 | prosumer
2406 | Load_TR9_F6_62 | TR9_six807 | 1 | 4 | prosumer
2407 | Load_TR9_F6_63 | TR9_six844 | 3 | 2 | prosumer
2408 | Load_TR9_F6_64 | TR9_six852 | 2 | 3 | prosumer
2409 | Load_TR9_F6_65 | TR9_six860 | 3 | 4 | prosumer
2411 | Load_TR9_F6_67 | TR9_six885 | 1 | 4 | prosumer
2415 | Load_TR9_F6_70 | TR9_six914 | 1 | 2.5 | prosumer
2416 | Load_TR9_F6_71 | TR9_six921 | 2 | 2.5 | prosumer
2418 | Load_TR9_F6_73 | TR9_six938 | 1 | 2 | prosumer
2421 | Load_TR9_F6_76 | TR9_six967 | 2 | 1.5 | prosumer
2422 | Load_TR9_F6_77 | TR9_six974 | 3 | 1.5 | prosumer
2424 | Load_TR9_F6_79 | TR9_six990 | 2 | 4 | prosumer
2425 | Load_TR9_F6_8 | TR9_six111 | 3 | 3 | prosumer
2426 | Load_TR9_F6_80 | TR9_six1006 | 3 | 3.5 | prosumer
2428 | Load_TR9_F6_82 | TR9_six1025 | 2 | 4 | prosumer
2429 | Load_TR9_F6_83 | TR9_six1064 | 3 | 4 | prosumer
2430 | Load_TR9_F6_9 | TR9_six128 | 2 | 4 | prosumer

## 3. Raw PV per load
Raw PV per load
Verbatim copy of PV_generation_kW (TR9_load_PV_48periods.xlsx). One row per connection, 48 half-hours (kW).
Load name | Type | p1 | p2 | p3 | p4 | p5 | p6 | p7 | p8 | p9 | p10 | p11 | p12 | p13 | p14 | p15 | p16 | p17 | p18 | p19 | p20 | p21 | p22 | p23 | p24 | p25 | p26 | p27 | p28 | p29 | p30 | p31 | p32 | p33 | p34 | p35 | p36 | p37 | p38 | p39 | p40 | p41 | p42 | p43 | p44 | p45 | p46 | p47 | p48
Load_TR9_F2_1 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F2_10 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F2_11 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F2_12 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F2_13 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F2_14 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F2_15 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F2_16 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F2_17 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F2_18 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F2_19 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F2_2 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F2_20 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F2_21 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F2_3 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F2_4 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F2_5 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F2_6 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F2_7 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F2_8 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F2_9 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_1 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_10 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_11 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_12 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_13 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_14 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_15 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_16 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_17 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_18 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_19 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_2 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_20 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_21 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_22 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_23 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_24 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_25 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_26 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_27 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_28 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_29 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_3 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_30 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_31 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_32 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_33 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_34 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_35 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_36 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_37 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_38 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_39 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_4 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_40 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_41 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_42 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_43 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_44 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_45 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_46 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_47 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_48 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_49 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_5 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_50 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_51 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_52 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_53 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_54 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_55 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_56 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_57 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_58 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_59 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_6 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_60 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_61 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_62 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_63 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_64 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_65 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_66 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_67 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_68 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_7 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_8 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F5_9 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_1 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_10 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_11 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_12 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_13 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_14 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_15 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_16 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_17 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_18 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_19 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_2 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_20 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_21 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_22 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_23 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_24 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_25 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_26 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_27 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_28 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_29 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_3 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_30 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_31 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_32 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_33 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_34 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_35 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_36 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_37 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_38 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_39 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_4 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_40 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_41 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_42 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_43 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_44 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_45 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_46 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_47 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_48 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_49 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_5 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_50 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_51 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_52 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_53 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_54 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_55 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_56 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_57 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_58 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_59 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_6 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_60 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_61 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_62 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_63 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_64 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_65 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_66 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_67 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_68 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_69 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_7 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_70 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_71 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_72 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_73 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_74 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_75 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_76 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_77 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_78 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_79 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_8 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_80 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_81 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_82 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_83 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR9_F6_9 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 4. Raw load per load
Raw load per load
Verbatim copy of Load_P_kW (TR9_load_PV_48periods.xlsx), tagged by type. One row per connection, 48 half-hours (kW).
Load name | Type | p1 | p2 | p3 | p4 | p5 | p6 | p7 | p8 | p9 | p10 | p11 | p12 | p13 | p14 | p15 | p16 | p17 | p18 | p19 | p20 | p21 | p22 | p23 | p24 | p25 | p26 | p27 | p28 | p29 | p30 | p31 | p32 | p33 | p34 | p35 | p36 | p37 | p38 | p39 | p40 | p41 | p42 | p43 | p44 | p45 | p46 | p47 | p48
Load_TR9_F2_1 | customer | 0.116 | 0.1435 | 0.054 | 0.1573 | 0.1022 | 0.054 | 0.054 | 0.116 | 0.1435 | 0.054 | 0.0747 | 0.1848 | 0.054 | 0.1917 | 0.0678 | 0.054 | 0.054 | 0.1435 | 2.0585 | 0.6477 | 0.101 | 0.2546 | 0.188 | 0.3354 | 0.413 | 0.054 | 0.1642 | 0.0953 | 0.054 | 0.2055 | 0.054 | 0.054 | 0.216 | 0.1039 | 0.3041 | 0.054 | 0.1229 | 0.4397 | 0.3222 | 0.5606 | 0.4578 | 1.3998 | 0.4976 | 0.3628 | 0.5337 | 0.284 | 0.4844 | 0.1515
Load_TR9_F2_10 | customer | 0.1295 | 0.0823 | 0.1106 | 0.1012 | 0.0917 | 0.054 | 0.087 | 0.1059 | 0.054 | 0.054 | 0.054 | 0.0634 | 0.1295 | 0.054 | 0.1698 | 2.0509 | 1.8305 | 1.1694 | 0.4114 | 1.3354 | 0.054 | 0.054 | 0.054 | 0.1579 | 0.054 | 0.1389 | 0.054 | 0.1389 | 0.054 | 0.1648 | 0.376 | 0.1453 | 0.0864 | 0.4269 | 0.4964 | 0.0666 | 0.2591 | 0.2307 | 0.2955 | 0.054 | 0.054 | 0.054 | 0.3601 | 0.4062 | 0.4366 | 0.445 | 0.2895 | 0.1248
Load_TR9_F2_11 | prosumer | 0.048 | 0.1005 | 0.3037 | 0.0769 | 0.1203 | 0.269 | 0.1062 | 0.2394 | 0.1792 | 0.048 | 0.2621 | 0.3604 | 0.2161 | 1.5606 | 0.2934 | 1.4221 | 0.5454 | 0.3273 | 0.5762 | 0.5385 | 0.2503 | 0.3974 | 0.0572 | 0.048 | 0.3147 | 0.5124 | 0.048 | 0.2838 | 0.1493 | 0.048 | 0.3634 | 0.0697 | 0.048 | 0.1615 | 0.3194 | 0.0943 | 1.3534 | 0.2009 | 0.3023 | 0.5735 | 0.2367 | 0.4093 | 0.5228 | 1.2307 | 0.6806 | 0.7499 | 0.5675 | 0.5005
Load_TR9_F2_12 | prosumer | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.1063 | 0.1116 | 0.1449 | 1.0046 | 0.1016 | 0.0924 | 0.0736 | 0.049 | 0.0716 | 0.1202 | 0.1803 | 0.1701 | 0.9349 | 0.2773 | 0.4947 | 0.133 | 0.049 | 0.5026 | 1.3947 | 0.4174 | 0.1025 | 0.4385 | 0.2115 | 0.3798 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.3964 | 0.1651
Load_TR9_F2_13 | customer | 0.384 | 0.054 | 0.3461 | 0.0739 | 0.3415 | 0.1144 | 0.3091 | 0.1827 | 0.1592 | 0.1598 | 0.2388 | 0.1618 | 0.2782 | 0.1879 | 0.26 | 0.1622 | 0.1635 | 0.2891 | 0.3101 | 0.3613 | 0.447 | 2.2095 | 2.5968 | 1.951 | 0.209 | 0.2639 | 0.2398 | 1.1335 | 0.6056 | 0.3996 | 0.246 | 0.1427 | 0.1418 | 0.7082 | 0.706 | 0.7192 | 0.8493 | 0.4953 | 0.7129 | 0.3661 | 0.2241 | 0.1353 | 0.2887 | 0.0849 | 0.2096 | 0.054 | 0.4059 | 0.066
Load_TR9_F2_14 | prosumer | 0.054 | 0.2155 | 0.0583 | 0.054 | 0.1315 | 0.1423 | 0.054 | 0.054 | 0.1423 | 0.1185 | 0.0985 | 0.1323 | 0.1099 | 0.054 | 0.1423 | 0.054 | 0.1315 | 0.1942 | 1.6659 | 1.4541 | 1.1433 | 0.1974 | 0.2347 | 0.6195 | 0.5548 | 0.7274 | 0.4009 | 0.1089 | 0.1653 | 0.1021 | 0.302 | 0.7193 | 0.1569 | 0.144 | 0.2498 | 0.054 | 0.2855 | 0.054 | 0.1423 | 0.1315 | 0.0729 | 0.2008 | 0.0583 | 0.3604 | 0.4995 | 0.436 | 0.5956 | 0.7427
Load_TR9_F2_15 | prosumer | 0.1166 | 0.0852 | 0.0544 | 0.2229 | 0.067 | 0.1005 | 0.046 | 0.1558 | 0.1214 | 0.046 | 0.1558 | 0.046 | 0.2312 | 0.046 | 0.1763 | 0.1009 | 0.046 | 0.1214 | 0.046 | 0.2312 | 0.0604 | 0.1989 | 0.0623 | 0.124 | 0.1558 | 0.046 | 0.046 | 0.2312 | 1.849 | 0.191 | 0.4265 | 0.1383 | 0.2033 | 0.1474 | 0.4352 | 0.1387 | 0.1366 | 0.0931 | 0.0921 | 0.1851 | 0.1005 | 0.1781 | 0.1206 | 0.2679 | 0.4704 | 0.107 | 0.1692 | 0.601
Load_TR9_F2_16 | prosumer | 0.5774 | 0.4897 | 0.2732 | 0.0848 | 0.2881 | 0.1433 | 0.1995 | 0.2392 | 0.042 | 0.2687 | 0.17 | 0.042 | 0.1823 | 0.2564 | 0.2729 | 0.2576 | 0.3535 | 0.489 | 0.0572 | 0.2406 | 0.3179 | 0.4507 | 0.4016 | 1.0075 | 3.0598 | 1.9052 | 0.4365 | 0.335 | 0.1935 | 0.3789 | 0.1551 | 0.302 | 0.3234 | 1.2339 | 1.1878 | 1.8042 | 0.3548 | 0.5796 | 0.5944 | 0.7312 | 0.9048 | 1.0234 | 0.6867 | 0.6497 | 0.1805 | 0.1955 | 0.2362 | 0.413
Load_TR9_F2_17 | prosumer | 0.5937 | 0.5725 | 0.5629 | 0.058 | 0.2905 | 0.13 | 0.1013 | 0.3193 | 0.058 | 0.21 | 0.2105 | 0.146 | 0.1781 | 0.1544 | 0.058 | 0.3626 | 1.9124 | 0.3362 | 0.2499 | 0.295 | 0.066 | 0.3546 | 0.058 | 0.135 | 0.2856 | 0.058 | 0.3417 | 0.1236 | 0.2912 | 0.3686 | 0.1963 | 0.4052 | 0.2604 | 0.3942 | 0.2771 | 0.2002 | 0.138 | 0.6411 | 1.6412 | 0.4917 | 0.5626 | 0.6514 | 0.4957 | 0.17 | 0.058 | 0.2726 | 0.148 | 0.058
Load_TR9_F2_18 | prosumer | 0.045 | 0.1388 | 0.045 | 0.1388 | 0.045 | 0.1388 | 0.045 | 0.045 | 0.1388 | 0.045 | 0.1388 | 0.045 | 0.1013 | 0.0825 | 0.045 | 0.0563 | 0.1013 | 0.2916 | 2.0625 | 0.8015 | 1.0392 | 0.5931 | 0.1832 | 1.1805 | 0.4183 | 0.1354 | 0.202 | 0.0892 | 0.0988 | 0.1668 | 0.0591 | 0.1247 | 0.045 | 0.0825 | 0.1013 | 0.1005 | 0.1478 | 0.0753 | 0.2416 | 0.2031 | 0.3022 | 0.3942 | 0.5067 | 0.4655 | 0.4839 | 0.5486 | 0.4088 | 1.1005
Load_TR9_F2_19 | prosumer | 0.211 | 0.046 | 0.3164 | 0.0894 | 0.0894 | 0.3041 | 0.0583 | 0.1415 | 0.1415 | 0.046 | 0.1564 | 0.2493 | 0.046 | 0.2493 | 0.1564 | 0.1502 | 0.2003 | 0.1167 | 0.2446 | 0.2148 | 1.1337 | 0.9164 | 0.2137 | 1.0145 | 1.3613 | 0.4072 | 0.3297 | 0.5557 | 0.1819 | 0.1962 | 0.3147 | 1.2989 | 0.4413 | 0.24 | 0.4094 | 0.2716 | 1.4863 | 0.4278 | 0.0828 | 0.046 | 0.2371 | 0.0644 | 0.2024 | 0.2034 | 0.1503 | 0.0721 | 0.3337 | 0.046
Load_TR9_F2_2 | customer | 0.1157 | 0.053 | 0.053 | 0.1336 | 0.053 | 0.1023 | 0.0843 | 0.053 | 0.053 | 0.1202 | 0.0664 | 0.1291 | 0.0575 | 0.1247 | 0.062 | 0.1336 | 0.1672 | 0.1479 | 0.0936 | 0.1381 | 0.0897 | 0.907 | 0.1905 | 0.1347 | 0.0575 | 0.2927 | 0.053 | 0.3139 | 0.053 | 0.1336 | 0.053 | 0.1336 | 0.053 | 0.0754 | 0.1112 | 0.053 | 0.1336 | 0.053 | 0.0799 | 0.1771 | 0.437 | 0.4265 | 0.8826 | 1.131 | 0.298 | 0.2241 | 0.053 | 0.0799
Load_TR9_F2_20 | prosumer | 0.145 | 0.1983 | 0.171 | 0.3482 | 0.1543 | 0.1841 | 0.2348 | 0.171 | 0.212 | 0.1902 | 0.283 | 0.0599 | 0.3518 | 0.1674 | 0.269 | 2.7175 | 0.4602 | 0.3566 | 0.1354 | 0.307 | 0.244 | 0.1013 | 0.3665 | 0.1818 | 0.3585 | 1.3912 | 0.086 | 1.1253 | 1.1774 | 1.6846 | 0.473 | 0.3574 | 2.3893 | 0.1671 | 0.6025 | 1.4326 | 1.136 | 1.2193 | 2.2385 | 0.5609 | 0.4093 | 0.7159 | 0.8341 | 0.8049 | 1.0649 | 0.9336 | 0.224 | 0.2953
Load_TR9_F2_21 | prosumer | 0.156 | 0.2934 | 0.1212 | 0.2222 | 0.0828 | 0.2867 | 0.1672 | 0.2298 | 0.2206 | 0.1212 | 0.2622 | 0.1452 | 0.0582 | 0.1329 | 0.2817 | 0.2319 | 0.0727 | 0.3443 | 0.097 | 0.1524 | 0.3199 | 0.1493 | 0.0945 | 0.0672 | 0.3549 | 0.0919 | 0.2217 | 0.1906 | 0.1017 | 1.5333 | 0.9708 | 1.6557 | 0.326 | 0.1343 | 0.4083 | 0.3734 | 0.3257 | 0.2777 | 0.6969 | 0.3692 | 0.3002 | 0.5996 | 0.2333 | 0.0919 | 0.1379 | 0.1705 | 0.2056 | 0.1928
Load_TR9_F2_3 | customer | 0.053 | 0.0612 | 0.1186 | 0.0612 | 0.1186 | 0.053 | 0.0858 | 0.094 | 0.053 | 0.1268 | 0.053 | 0.1268 | 0.053 | 0.1268 | 0.053 | 0.1104 | 0.6195 | 0.7395 | 0.3155 | 0.2845 | 0.0858 | 0.0694 | 0.1104 | 0.053 | 0.053 | 0.1268 | 0.1023 | 0.2133 | 1.4197 | 2.4125 | 0.2908 | 1.316 | 0.053 | 0.1442 | 0.3457 | 0.6691 | 0.1072 | 0.0806 | 0.1199 | 0.4366 | 0.5327 | 0.8407 | 0.4541 | 0.3889 | 0.3958 | 0.4617 | 0.053 | 0.053
Load_TR9_F2_4 | customer | 0.056 | 0.2407 | 0.056 | 0.1315 | 0.1651 | 0.056 | 0.1567 | 0.1399 | 0.056 | 0.2155 | 0.0812 | 0.056 | 0.2854 | 0.1837 | 0.2922 | 0.056 | 0.4031 | 0.4872 | 0.2993 | 0.191 | 0.6644 | 0.523 | 0.4831 | 0.8183 | 0.4127 | 0.4051 | 0.1674 | 0.5903 | 1.1843 | 0.6869 | 0.3927 | 0.2435 | 0.2455 | 0.662 | 0.5541 | 0.3378 | 0.3336 | 0.2648 | 2.6447 | 1.4062 | 0.4996 | 0.6059 | 2.2033 | 0.6148 | 0.7053 | 0.8135 | 0.5569 | 0.056
Load_TR9_F2_5 | prosumer | 0.052 | 0.1135 | 0.1182 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.1086 | 0.1873 | 0.1898 | 1.5669 | 2.6428 | 1.2797 | 0.2398 | 1.8927 | 3.3393 | 1.3787 | 0.2202 | 0.085 | 0.0674 | 0.0599 | 0.1266 | 0.142 | 0.0931 | 0.1347 | 0.1783 | 0.2047 | 0.2487 | 0.3186 | 0.1056 | 0.1147 | 0.3431 | 0.4766 | 0.3741 | 0.5872 | 0.8089 | 0.5527 | 0.4066 | 0.411 | 0.3946
Load_TR9_F2_6 | customer | 0.3544 | 0.295 | 0.2138 | 0.047 | 0.1241 | 0.1855 | 0.0787 | 0.0969 | 0.1018 | 0.2077 | 0.047 | 0.2016 | 0.1079 | 0.047 | 0.2534 | 0.0561 | 0.0602 | 0.3511 | 0.1479 | 0.2361 | 0.122 | 0.3176 | 0.3743 | 0.1761 | 0.1949 | 0.1341 | 0.2958 | 0.047 | 0.1555 | 0.3173 | 0.1118 | 0.0882 | 0.2499 | 0.2107 | 0.2014 | 0.4992 | 0.2862 | 0.3392 | 0.6267 | 0.3878 | 0.4121 | 0.5355 | 0.5621 | 0.4247 | 0.6046 | 0.5129 | 0.1286 | 0.047
Load_TR9_F2_7 | prosumer | 0.7056 | 0.1358 | 0.1486 | 0.1865 | 0.174 | 0.047 | 0.1801 | 0.1232 | 0.1929 | 0.1295 | 0.1422 | 0.1928 | 0.1676 | 0.047 | 0.085 | 0.288 | 0.2227 | 0.2119 | 0.1612 | 0.1422 | 0.2182 | 0.047 | 0.1041 | 0.2909 | 0.2622 | 0.5041 | 0.047 | 0.0641 | 0.4977 | 0.7051 | 0.2709 | 0.0955 | 0.3135 | 0.047 | 0.0724 | 0.2183 | 0.1167 | 0.0914 | 0.2437 | 0.0724 | 0.174 | 0.1865 | 0.174 | 0.1294 | 0.1358 | 0.1422 | 0.1421 | 0.2184
Load_TR9_F2_8 | customer | 0.0629 | 0.1583 | 0.1881 | 0.0824 | 0.264 | 0.0629 | 0.1588 | 0.136 | 0.2456 | 0.3331 | 0.2634 | 0.2617 | 0.1876 | 0.2025 | 0.0708 | 0.096 | 0.1988 | 0.1145 | 0.1241 | 0.1707 | 0.1145 | 1.2369 | 0.5034 | 0.1153 | 0.2113 | 0.2006 | 0.9709 | 0.8789 | 0.3988 | 0.2497 | 0.2121 | 0.3354 | 0.1515 | 0.2108 | 0.0576 | 0.1351 | 0.153 | 0.136 | 0.1868 | 0.1881 | 0.5016 | 0.4003 | 0.7206 | 0.8284 | 0.1577 | 0.158 | 0.1588 | 0.1373
Load_TR9_F2_9 | customer | 0.1351 | 0.1324 | 0.0536 | 0.088 | 0.0721 | 0.1869 | 0.0406 | 0.1709 | 0.0967 | 0.032 | 0.0893 | 0.1395 | 0.0708 | 0.032 | 0.184 | 0.0949 | 0.2233 | 0.3517 | 0.2105 | 0.2081 | 0.0701 | 0.2112 | 2.8267 | 0.241 | 1.5182 | 0.6308 | 0.1719 | 0.118 | 0.1387 | 0.2428 | 0.4549 | 0.1255 | 0.1109 | 0.5096 | 0.2711 | 0.2615 | 0.1635 | 0.2052 | 0.1303 | 0.2463 | 0.403 | 0.7206 | 1.4928 | 0.4927 | 0.3013 | 0.0851 | 0.0794 | 0.1365
Load_TR9_F5_1 | customer | 0.05 | 0.2224 | 0.05 | 0.1597 | 0.1127 | 0.0735 | 0.1989 | 0.05 | 0.05 | 0.191 | 0.0813 | 0.0578 | 0.2145 | 0.05 | 0.1205 | 0.1518 | 0.05 | 0.2224 | 0.05 | 0.1518 | 0.1205 | 0.3633 | 1.8014 | 0.0657 | 0.1283 | 0.144 | 0.05 | 0.0549 | 0.4977 | 1.0113 | 0.2696 | 0.1124 | 0.1046 | 0.2491 | 0.4523 | 0.7791 | 0.2391 | 0.2838 | 0.2563 | 0.4673 | 0.6659 | 0.8524 | 0.5596 | 0.4882 | 0.473 | 0.0735 | 0.1989 | 0.05
Load_TR9_F5_10 | prosumer | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.0651 | 0.067 | 0.067 | 0.2747 | 0.067 | 0.1645 | 0.067 | 0.067 | 1.0833 | 0.7592 | 1.3499 | 0.0532 | 0.049 | 0.0643 | 0.0836 | 0.3725 | 0.254 | 0.3183 | 0.049 | 0.049 | 0.049 | 0.202 | 0.2448 | 0.5062 | 1.9547 | 0.2224 | 0.326 | 1.5915 | 1.3369 | 0.9718 | 0.3877 | 0.4636 | 0.576 | 0.4538 | 0.1738 | 0.3233 | 0.049
Load_TR9_F5_11 | prosumer | 1.0471 | 0.5736 | 0.9302 | 0.0783 | 0.1046 | 0.1889 | 0.052 | 0.2243 | 0.0955 | 0.052 | 0.1683 | 0.1515 | 0.052 | 0.1453 | 0.1701 | 0.0564 | 0.1889 | 0.157 | 0.1092 | 0.2151 | 0.7098 | 0.6339 | 0.2616 | 0.0564 | 0.1702 | 0.0707 | 0.1932 | 0.1267 | 0.1284 | 0.2074 | 0.1408 | 0.2785 | 0.2671 | 0.1981 | 0.2468 | 0.1377 | 1.0737 | 1.4547 | 0.086 | 0.4534 | 0.5414 | 0.5363 | 0.7395 | 1.513 | 2.0652 | 0.9141 | 1.2317 | 0.7
Load_TR9_F5_12 | prosumer | 1.0705 | 1.043 | 0.0584 | 0.2291 | 0.1171 | 0.1414 | 0.2112 | 0.052 | 0.2716 | 0.0809 | 0.052 | 0.3006 | 0.052 | 0.2027 | 0.386 | 0.052 | 0.2044 | 1.1387 | 0.088 | 1.2314 | 1.2423 | 0.3924 | 0.3257 | 1.3252 | 0.5289 | 0.3799 | 0.1959 | 0.1853 | 0.3583 | 0.0839 | 0.2832 | 0.261 | 0.2211 | 0.3305 | 0.668 | 1.3922 | 0.6655 | 1.4904 | 0.5037 | 0.0584 | 1.4034 | 0.617 | 1.2445 | 0.6336 | 1.0957 | 0.7882 | 0.811 | 0.2282
Load_TR9_F5_13 | customer | 0.1516 | 0.4037 | 0.647 | 0.6764 | 0.5587 | 0.055 | 0.0614 | 0.1902 | 0.055 | 0.1967 | 0.055 | 0.1001 | 0.1516 | 0.055 | 0.1967 | 0.055 | 0.1967 | 0.2325 | 0.2009 | 0.31 | 0.4421 | 0.4893 | 0.2761 | 0.6445 | 3.9178 | 2.9216 | 0.6122 | 0.1461 | 2.024 | 0.2306 | 0.2635 | 0.2568 | 0.2774 | 0.1136 | 1.5768 | 0.9287 | 0.1847 | 0.3144 | 0.1821 | 0.3357 | 0.6648 | 0.6004 | 0.5574 | 0.7187 | 0.8912 | 0.8731 | 0.8478 | 0.055
Load_TR9_F5_14 | prosumer | 0.5703 | 0.7125 | 0.0927 | 0.171 | 0.1423 | 0.048 | 0.2653 | 0.048 | 0.2076 | 0.1057 | 0.048 | 0.1368 | 0.1095 | 0.0753 | 0.2231 | 0.0629 | 0.2225 | 0.0908 | 0.048 | 0.2653 | 0.048 | 0.1648 | 0.1486 | 0.0902 | 0.2729 | 0.2268 | 0.1461 | 0.1523 | 0.0927 | 0.2743 | 0.2639 | 0.3577 | 2.5429 | 0.2717 | 0.4078 | 0.1904 | 0.3325 | 0.2265 | 0.1902 | 0.1232 | 0.115 | 0.1983 | 0.1515 | 0.3036 | 0.6972 | 0.5686 | 0.5099 | 0.0753
Load_TR9_F5_15 | prosumer | 0.1002 | 0.1218 | 0.1161 | 0.1604 | 0.057 | 0.0786 | 0.2763 | 0.0865 | 0.0939 | 0.1825 | 0.057 | 0.165 | 0.1308 | 0.2104 | 0.1002 | 0.2194 | 0.1056 | 0.1164 | 0.2302 | 0.1542 | 0.1308 | 0.1456 | 0.165 | 0.2194 | 0.057 | 0.165 | 0.1235 | 0.153 | 0.165 | 0.1308 | 0.1456 | 0.165 | 0.2121 | 0.0644 | 0.1678 | 0.1951 | 0.0786 | 0.2194 | 0.057 | 0.1678 | 0.2177 | 0.3824 | 0.6582 | 0.4316 | 0.4859 | 0.2616 | 0.0624 | 0.322
Load_TR9_F5_16 | customer | 1.0279 | 1.1744 | 0.057 | 0.2101 | 0.0812 | 0.057 | 0.2343 | 0.057 | 0.1376 | 0.1537 | 0.057 | 0.2343 | 0.057 | 0.0628 | 0.3006 | 0.1264 | 0.7451 | 0.5513 | 0.2545 | 0.2612 | 0.5135 | 0.4785 | 0.2163 | 0.1779 | 0.1134 | 0.0731 | 0.2181 | 0.057 | 0.2343 | 0.3831 | 1.5327 | 0.3639 | 0.4432 | 0.4964 | 0.3003 | 0.1113 | 0.1315 | 0.6857 | 0.3886 | 0.4098 | 2.0248 | 0.9014 | 0.9683 | 0.8729 | 0.6088 | 0.886 | 0.6484 | 0.7532
Load_TR9_F5_17 | customer | 0.2728 | 0.049 | 0.2973 | 0.0988 | 0.049 | 0.2226 | 0.0573 | 0.1901 | 0.2061 | 0.1653 | 0.2309 | 0.049 | 0.2397 | 0.1565 | 0.1818 | 0.2143 | 0.2696 | 0.4273 | 0.2109 | 0.1071 | 0.3369 | 0.049 | 0.1813 | 0.2149 | 0.049 | 0.0821 | 0.3058 | 0.1052 | 0.1151 | 0.281 | 0.049 | 0.2309 | 0.1653 | 0.049 | 0.289 | 0.1071 | 0.0986 | 0.2976 | 0.049 | 0.1071 | 0.3892 | 0.5159 | 0.4539 | 0.4355 | 0.9275 | 0.8141 | 0.6107 | 0.8299
Load_TR9_F5_18 | customer | 0.2803 | 0.048 | 0.2473 | 0.1221 | 0.048 | 0.2023 | 0.1592 | 0.0633 | 0.2023 | 0.1598 | 0.048 | 0.2687 | 0.4324 | 0.0545 | 1.0979 | 2.67 | 4.2192 | 1.1146 | 0.3164 | 0.9567 | 0.1892 | 0.1172 | 1.52 | 0.6907 | 0.1834 | 0.3567 | 0.1892 | 0.1803 | 0.1537 | 0.3532 | 0.3435 | 0.158 | 0.627 | 0.1458 | 1.3716 | 3.4335 | 2.2435 | 1.288 | 0.9384 | 1.5028 | 0.8328 | 0.74 | 0.472 | 0.8222 | 1.2449 | 0.7025 | 0.5239 | 0.7033
Load_TR9_F5_19 | prosumer | 0.046 | 0.1588 | 0.1193 | 0.2879 | 0.0573 | 0.046 | 0.2306 | 0.1879 | 0.1575 | 0.0901 | 0.2092 | 0.2327 | 0.1458 | 0.2465 | 0.1174 | 0.1137 | 0.046 | 0.1971 | 0.2214 | 0.0801 | 0.3318 | 0.0526 | 0.2675 | 0.151 | 0.2282 | 0.1903 | 0.0799 | 0.2538 | 0.1409 | 0.385 | 0.2854 | 0.1115 | 0.0499 | 0.0976 | 0.2802 | 0.2434 | 0.3925 | 0.2389 | 0.1841 | 0.4586 | 0.7928 | 0.4193 | 0.2906 | 0.4634 | 0.533 | 0.5935 | 0.5455 | 0.2354
Load_TR9_F5_2 | prosumer | 0.061 | 0.0523 | 0.1214 | 0.048 | 0.1258 | 0.0523 | 0.1214 | 0.0523 | 0.1214 | 0.048 | 0.1258 | 0.048 | 0.061 | 0.1128 | 0.0869 | 0.0869 | 0.0566 | 0.1171 | 0.048 | 0.048 | 0.048 | 0.1085 | 0.0653 | 0.061 | 0.1128 | 0.048 | 0.061 | 0.1128 | 0.0782 | 0.1408 | 0.048 | 0.149 | 0.0974 | 0.1723 | 0.0623 | 0.048 | 0.1008 | 0.1258 | 0.0572 | 0.1745 | 0.3424 | 0.3084 | 0.3381 | 0.1042 | 0.048 | 0.0653 | 0.1085 | 0.0782
Load_TR9_F5_20 | customer | 0.044 | 0.2644 | 0.0762 | 0.1218 | 0.2189 | 0.044 | 0.044 | 0.1549 | 0.1663 | 0.1663 | 0.0519 | 0.1728 | 0.1678 | 0.0569 | 0.1886 | 0.1391 | 0.044 | 0.2491 | 0.0915 | 0.147 | 0.1936 | 0.1021 | 0.1731 | 0.0765 | 0.4802 | 0.0569 | 0.3152 | 0.1223 | 0.1608 | 0.1463 | 0.1359 | 0.1864 | 0.2042 | 0.1182 | 0.274 | 0.0689 | 0.148 | 0.2122 | 0.0483 | 0.4943 | 0.2042 | 0.216 | 0.3618 | 0.196 | 1.285 | 0.7678 | 0.1845 | 0.1263
Load_TR9_F5_21 | customer | 0.061 | 0.061 | 0.1339 | 0.061 | 0.3561 | 0.6324 | 0.0813 | 0.1299 | 0.0651 | 0.061 | 0.061 | 0.1096 | 0.0853 | 0.061 | 0.061 | 0.1339 | 0.061 | 0.1188 | 0.2201 | 0.3247 | 0.1871 | 1.3831 | 0.1079 | 0.0896 | 0.1693 | 0.3867 | 0.264 | 0.3867 | 0.3459 | 1.4724 | 0.208 | 0.208 | 0.2699 | 0.293 | 0.1422 | 0.1538 | 1.4642 | 0.2892 | 0.1584 | 0.309 | 0.4316 | 0.3347 | 0.1339 | 0.061 | 0.0934 | 0.1015 | 0.1177 | 0.0772
Load_TR9_F5_22 | customer | 0.086 | 0.1561 | 0.044 | 0.1981 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.1561 | 0.086 | 0.044 | 0.1911 | 0.051 | 0.4402 | 0.0927 | 0.1981 | 0.044 | 0.1055 | 0.2984 | 0.1339 | 0.2027 | 0.058 | 0.044 | 0.2212 | 0.2921 | 0.044 | 0.0668 | 0.0836 | 0.1204 | 0.5243 | 0.2721 | 0.3065 | 0.3684 | 0.1177 | 1.269 | 0.132 | 0.1694 | 0.3566 | 0.2272 | 0.6312 | 0.5479 | 0.3848 | 0.8235 | 0.4159 | 0.7879 | 0.2735 | 0.072
Load_TR9_F5_23 | prosumer | 0.0822 | 0.1252 | 0.0554 | 0.1521 | 0.05 | 0.1467 | 0.0607 | 0.05 | 0.1574 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1037 | 0.1037 | 0.05 | 0.2171 | 0.2611 | 0.3553 | 0.2986 | 0.2788 | 0.4645 | 0.3231 | 0.4142 | 0.3662 | 0.1143 | 0.2461 | 0.0708 | 0.4268 | 0.4816 | 0.3386 | 0.264 | 0.6762 | 0.2947 | 0.2469 | 0.5616 | 0.5158 | 0.2936 | 0.7212 | 0.6563 | 0.3926 | 0.5737 | 0.5577 | 0.6015 | 0.5304 | 0.05 | 0.0876
Load_TR9_F5_24 | customer | 0.7776 | 0.6679 | 0.1696 | 0.037 | 0.2765 | 0.037 | 0.037 | 0.2383 | 0.0752 | 0.1358 | 0.1777 | 0.037 | 0.1994 | 0.1141 | 0.037 | 0.5972 | 0.095 | 0.1376 | 0.1636 | 1.2082 | 0.1811 | 0.4677 | 0.302 | 1.1612 | 1.8629 | 2.1233 | 0.3141 | 0.2165 | 0.0896 | 0.0705 | 0.2001 | 0.1135 | 0.2964 | 0.331 | 0.1934 | 0.0647 | 1.3583 | 0.1295 | 0.2194 | 0.4224 | 0.4244 | 0.631 | 0.6798 | 0.4959 | 0.4968 | 0.6069 | 0.2655 | 0.142
Load_TR9_F5_25 | customer | 0.2015 | 0.051 | 0.2076 | 0.0757 | 0.051 | 0.1169 | 0.1664 | 0.051 | 0.051 | 0.051 | 0.2324 | 0.051 | 0.051 | 0.1747 | 0.1087 | 0.051 | 0.1334 | 0.1499 | 0.1606 | 0.2282 | 1.1752 | 0.8687 | 1.2004 | 1.0711 | 0.9242 | 3.7226 | 2.6225 | 0.4692 | 0.2324 | 0.051 | 0.0675 | 0.2159 | 0.051 | 0.1582 | 0.1252 | 0.0922 | 0.1911 | 0.051 | 0.2324 | 0.051 | 0.1417 | 0.1417 | 0.051 | 0.1911 | 0.0922 | 0.051 | 0.1664 | 0.1169
Load_TR9_F5_26 | customer | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.0929 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.0665 | 0.2355 | 0.0599 | 0.0552 | 0.049 | 0.2089 | 0.0539 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.1253 | 0.1814 | 0.0652 | 0.0757 | 0.1003 | 0.1805 | 0.1099 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049
Load_TR9_F5_27 | customer | 0.053 | 0.053 | 0.2313 | 0.053 | 0.1016 | 0.1827 | 0.053 | 0.0935 | 0.1908 | 0.053 | 0.2313 | 0.053 | 0.1908 | 0.0935 | 0.2883 | 0.3007 | 0.2267 | 0.3962 | 0.1194 | 0.0856 | 0.408 | 0.2027 | 0.053 | 0.2313 | 0.053 | 0.0854 | 0.1989 | 0.1445 | 0.3828 | 0.4351 | 0.4133 | 0.3 | 0.3538 | 0.4953 | 0.3045 | 1.1066 | 0.1624 | 0.059 | 0.2493 | 0.234 | 0.3789 | 0.2963 | 0.4147 | 0.2993 | 0.5999 | 0.6317 | 0.053 | 0.053
Load_TR9_F5_28 | prosumer | 0.2877 | 0.375 | 0.2157 | 0.056 | 0.056 | 0.142 | 0.1977 | 0.056 | 0.2692 | 0.0705 | 0.056 | 0.2271 | 0.1127 | 0.056 | 0.2128 | 0.1269 | 0.1359 | 0.2039 | 0.0778 | 0.194 | 0.056 | 0.2157 | 0.124 | 0.056 | 0.3002 | 0.1749 | 0.1127 | 0.3442 | 0.6062 | 0.5005 | 0.4543 | 0.0923 | 0.0975 | 0.2277 | 0.1045 | 0.2761 | 0.5675 | 0.495 | 0.3904 | 0.4816 | 0.5535 | 0.758 | 0.6344 | 0.2815 | 0.0787 | 0.1617 | 0.178 | 0.056
Load_TR9_F5_29 | prosumer | 0.045 | 0.3047 | 0.0879 | 0.051 | 0.3416 | 0.051 | 0.1595 | 0.045 | 0.2392 | 0.1535 | 0.1085 | 1.6839 | 1.3392 | 0.6422 | 0.1026 | 0.0857 | 0.3527 | 0.045 | 0.4795 | 1.0517 | 0.664 | 0.3311 | 0.0616 | 0.1609 | 0.1112 | 0.1655 | 0.2744 | 0.3035 | 0.2677 | 0.5255 | 0.3854 | 0.562 | 0.4345 | 0.1896 | 0.5622 | 0.1939 | 0.2977 | 0.3885 | 0.2918 | 0.1873 | 0.1692 | 0.2306 | 0.5601 | 0.376 | 0.5474 | 0.5203 | 0.3439 | 0.2445
Load_TR9_F5_3 | prosumer | 0.055 | 0.1269 | 0.2176 | 0.055 | 0.1774 | 0.1672 | 0.1054 | 0.2392 | 0.055 | 0.1312 | 0.2134 | 0.1185 | 0.1397 | 0.1668 | 0.1058 | 0.2134 | 0.055 | 0.055 | 0.2134 | 0.055 | 0.127 | 0.1414 | 0.0592 | 0.2277 | 0.1168 | 0.1773 | 0.163 | 0.1312 | 0.1429 | 0.6906 | 0.337 | 0.5922 | 0.4957 | 0.055 | 0.2557 | 0.0888 | 0.055 | 0.2895 | 0.2293 | 1.4752 | 0.4166 | 0.3136 | 0.3486 | 0.7944 | 0.0931 | 0.2036 | 0.141 | 0.0694
Load_TR9_F5_30 | prosumer | 0.1642 | 0.048 | 0.3088 | 0.0685 | 0.048 | 0.2473 | 0.13 | 0.048 | 0.3157 | 0.0617 | 0.0742 | 0.2895 | 0.0617 | 0.1369 | 0.1292 | 0.1593 | 0.1984 | 0.048 | 0.1642 | 0.2131 | 0.048 | 0.1801 | 0.1972 | 0.0545 | 0.3091 | 0.0617 | 0.2747 | 0.1168 | 0.3311 | 0.27 | 0.0851 | 0.1553 | 0.2561 | 0.4423 | 0.4568 | 0.0901 | 0.2999 | 0.3266 | 0.156 | 0.2982 | 0.1154 | 0.1946 | 0.3657 | 0.9993 | 0.3915 | 0.3086 | 0.1681 | 0.2246
Load_TR9_F5_31 | customer | 0.2049 | 0.0673 | 0.1072 | 0.1372 | 0.1937 | 0.0936 | 0.053 | 0.2102 | 0.053 | 0.2057 | 0.1387 | 0.1343 | 0.053 | 0.0673 | 0.2771 | 0.053 | 0.2565 | 0.088 | 0.1162 | 0.4177 | 0.3135 | 0.2419 | 0.5377 | 0.2338 | 0.1749 | 0.9945 | 1.7531 | 0.7077 | 0.053 | 0.2102 | 0.053 | 0.1102 | 0.153 | 0.053 | 0.103 | 0.1602 | 0.1343 | 0.0959 | 0.1673 | 0.053 | 0.2102 | 0.1343 | 0.053 | 0.053 | 0.1974 | 0.147 | 0.0887 | 0.2557
Load_TR9_F5_32 | prosumer | 0.7503 | 0.2568 | 0.054 | 0.2598 | 0.054 | 0.0801 | 0.2061 | 0.0816 | 0.054 | 0.2657 | 0.251 | 0.208 | 0.1565 | 0.054 | 0.2995 | 0.1329 | 0.0781 | 0.3967 | 0.2225 | 0.2209 | 1.5191 | 0.1092 | 0.1389 | 0.1128 | 0.1092 | 0.2046 | 0.1092 | 0.1197 | 0.1389 | 0.8332 | 0.2715 | 0.2846 | 0.3657 | 0.2556 | 0.3344 | 0.3876 | 0.4378 | 0.3632 | 0.5226 | 0.323 | 0.5758 | 0.5674 | 0.684 | 1.0293 | 0.4407 | 0.1683 | 0.1455 | 0.054
Load_TR9_F5_33 | customer | 0.475 | 0.3973 | 0.1698 | 0.0497 | 0.3182 | 0.063 | 0.0904 | 0.2908 | 0.043 | 0.1974 | 0.1371 | 0.1485 | 0.1459 | 0.043 | 0.1498 | 0.2314 | 0.1031 | 0.2194 | 0.1018 | 0.1228 | 1.0358 | 0.0829 | 0.1526 | 0.1813 | 1.56 | 0.883 | 1.923 | 0.3972 | 2.5188 | 2.5954 | 0.9561 | 0.2047 | 0.4224 | 0.043 | 0.1765 | 0.2708 | 0.075 | 0.2058 | 0.1845 | 0.7112 | 0.3785 | 0.3525 | 0.366 | 0.5935 | 0.3908 | 0.168 | 0.1632 | 0.2181
Load_TR9_F5_34 | customer | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.0921 | 0.4468 | 0.056 | 0.0778 | 0.882 | 0.7728 | 0.938 | 1.6545 | 0.071 | 1.0215 | 0.779 | 1.2854 | 1.1663 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.4931 | 1.3482 | 1.1422 | 0.1874 | 0.339 | 1.5287 | 0.1346 | 0.2976 | 0.3638 | 0.3457 | 0.2681 | 0.2726 | 0.3406
Load_TR9_F5_35 | customer | 0.1645 | 0.0923 | 0.114 | 0.1429 | 0.0707 | 0.1862 | 0.049 | 0.2538 | 0.049 | 0.049 | 0.1934 | 0.0634 | 0.049 | 0.1645 | 0.0923 | 0.049 | 0.1862 | 0.0707 | 0.0634 | 0.2019 | 0.0808 | 0.2396 | 0.0543 | 0.1429 | 0.1229 | 0.1827 | 0.224 | 0.2073 | 0.1702 | 0.2155 | 0.0863 | 0.2078 | 0.0584 | 0.0721 | 0.1827 | 0.0923 | 0.114 | 0.1429 | 0.049 | 0.2078 | 0.049 | 0.1637 | 0.3009 | 0.254 | 0.2513 | 0.3431 | 0.3098 | 0.2219
Load_TR9_F5_36 | customer | 0.049 | 0.2777 | 0.0925 | 0.0997 | 0.2084 | 0.1111 | 0.2083 | 0.1619 | 0.049 | 0.1078 | 0.2624 | 0.049 | 0.2535 | 0.1167 | 0.0997 | 0.1576 | 0.1054 | 0.1706 | 0.1488 | 0.1562 | 0.1576 | 0.2126 | 0.049 | 0.1975 | 0.223 | 0.2025 | 0.1794 | 0.078 | 0.049 | 0.0772 | 0.293 | 0.049 | 0.3212 | 0.049 | 0.1651 | 0.3932 | 0.0772 | 0.1337 | 0.2586 | 0.6139 | 0.5827 | 0.7466 | 0.6861 | 0.8749 | 1.2018 | 0.3003 | 0.1167 | 0.2535
Load_TR9_F5_37 | customer | 0.9617 | 0.5561 | 0.8354 | 0.7362 | 0.1576 | 0.137 | 0.2422 | 0.2307 | 0.0639 | 0.2913 | 0.1906 | 0.4184 | 0.6373 | 0.3183 | 0.4199 | 0.1819 | 0.2082 | 0.4571 | 1.5202 | 0.2489 | 0.1637 | 0.2213 | 0.3085 | 0.3175 | 0.1993 | 0.4181 | 0.1968 | 0.5473 | 0.7599 | 0.4932 | 0.2217 | 0.7588 | 0.1884 | 0.2482 | 0.3904 | 0.5471 | 1.3444 | 0.7669 | 1.3423 | 0.2905 | 0.3876 | 0.766 | 0.264 | 0.8794 | 1.2691 | 0.4119 | 0.6214 | 0.1681
Load_TR9_F5_38 | customer | 0.1897 | 0.2611 | 0.0791 | 0.2595 | 0.1702 | 0.1543 | 0.2043 | 0.1818 | 0.1425 | 0.1147 | 0.2849 | 0.1092 | 0.2156 | 0.1754 | 0.1177 | 0.2523 | 3.5086 | 1.2015 | 0.9525 | 0.316 | 1.4874 | 1.4209 | 1.0839 | 0.4138 | 0.2612 | 0.0993 | 0.4685 | 0.1098 | 0.2649 | 0.1957 | 0.4001 | 0.2838 | 0.1625 | 0.2981 | 0.2266 | 0.3572 | 0.2695 | 0.4171 | 0.3557 | 0.6853 | 0.7839 | 0.6368 | 0.969 | 0.695 | 1.1144 | 0.9802 | 0.1801 | 0.9379
Load_TR9_F5_39 | prosumer | 0.1034 | 0.089 | 0.2085 | 0.2412 | 0.2768 | 0.046 | 0.1751 | 0.0747 | 0.1177 | 0.1321 | 0.046 | 0.2038 | 0.046 | 0.1894 | 0.0603 | 0.046 | 0.0494 | 0.0692 | 0.1751 | 0.0747 | 0.046 | 0.0747 | 0.1751 | 0.046 | 0.3215 | 0.1177 | 0.046 | 0.2106 | 0.0601 | 0.1308 | 0.4847 | 0.245 | 0.1679 | 0.0921 | 2.1325 | 2.5812 | 1.7829 | 0.052 | 0.1044 | 0.6324 | 0.0603 | 0.0532 | 0.6161 | 0.4601 | 0.6164 | 0.7547 | 0.5523 | 1.4402
Load_TR9_F5_4 | prosumer | 0.046 | 0.1072 | 0.1908 | 0.0725 | 0.1989 | 0.046 | 0.2431 | 0.0814 | 0.0858 | 0.2387 | 0.0681 | 0.2563 | 0.046 | 0.1123 | 0.2121 | 0.046 | 0.196 | 0.1534 | 0.0898 | 0.991 | 0.5618 | 0.3996 | 0.1351 | 0.258 | 0.1792 | 0.103 | 0.5726 | 0.0536 | 0.1454 | 0.0995 | 0.046 | 0.1256 | 0.0813 | 1.1341 | 3.1862 | 2.1118 | 0.1759 | 0.1365 | 0.1237 | 0.2102 | 0.2442 | 0.4009 | 0.5292 | 0.3365 | 0.3203 | 0.6663 | 0.046 | 0.1759
Load_TR9_F5_40 | customer | 0.046 | 0.3098 | 0.0573 | 0.1178 | 0.1614 | 0.0629 | 0.236 | 0.1311 | 0.48 | 0.2878 | 0.2131 | 0.2759 | 0.1452 | 0.046 | 0.2084 | 0.046 | 0.1808 | 0.1863 | 0.8571 | 0.7638 | 0.2577 | 0.2316 | 0.1854 | 0.0869 | 0.1549 | 0.1914 | 0.2097 | 0.1813 | 0.1463 | 0.1136 | 0.046 | 0.2935 | 0.1551 | 0.0742 | 0.2312 | 0.1077 | 0.1587 | 0.1454 | 0.32 | 0.3603 | 0.442 | 0.5171 | 0.5757 | 0.3551 | 0.276 | 0.0742 | 0.1632 | 0.1757
Load_TR9_F5_41 | customer | 0.3805 | 0.1247 | 0.048 | 0.166 | 0.048 | 0.166 | 0.048 | 0.0716 | 0.1424 | 0.048 | 0.166 | 0.048 | 0.166 | 0.048 | 1.5799 | 0.0716 | 0.1365 | 0.6076 | 0.644 | 1.8739 | 0.056 | 0.0765 | 0.2355 | 0.1938 | 0.1938 | 0.1423 | 1.3364 | 0.8488 | 0.2237 | 0.1355 | 0.1634 | 0.3957 | 0.0821 | 0.1011 | 0.1129 | 0.2935 | 2.6605 | 2.272 | 0.1542 | 0.0598 | 0.048 | 0.2334 | 0.1269 | 0.4062 | 0.3871 | 0.4897 | 0.2498 | 0.048
Load_TR9_F5_42 | prosumer | 0.048 | 0.2095 | 0.048 | 0.048 | 0.0718 | 0.1434 | 0.048 | 0.048 | 0.048 | 0.1672 | 0.048 | 0.1136 | 0.1016 | 0.048 | 0.0957 | 0.1195 | 0.048 | 0.1672 | 0.096 | 0.1672 | 0.0929 | 0.0581 | 0.171 | 0.9263 | 0.048 | 0.3516 | 0.148 | 0.2672 | 0.0612 | 0.1023 | 0.3294 | 0.2348 | 0.3727 | 0.2383 | 0.0931 | 0.3196 | 0.3716 | 0.4502 | 0.5657 | 0.2976 | 0.1987 | 0.942 | 1.1321 | 0.4801 | 0.4652 | 0.3495 | 0.048 | 0.1672
Load_TR9_F5_43 | customer | 0.052 | 0.052 | 0.052 | 0.052 | 0.0717 | 0.1769 | 0.052 | 0.1769 | 0.0717 | 0.052 | 0.1901 | 0.0586 | 0.0849 | 0.1638 | 0.052 | 0.052 | 0.0798 | 0.1887 | 0.0876 | 0.2011 | 0.9673 | 0.2479 | 0.1966 | 0.052 | 0.1835 | 0.0651 | 0.0651 | 0.1835 | 0.052 | 0.1966 | 0.052 | 0.1572 | 0.0914 | 0.1177 | 0.1309 | 0.0564 | 0.3696 | 1.1587 | 0.2483 | 0.3633 | 0.7898 | 0.4565 | 0.5198 | 0.5305 | 0.4802 | 0.4264 | 0.1608 | 0.1875
Load_TR9_F5_44 | customer | 0.6712 | 0.4177 | 0.05 | 0.05 | 0.1163 | 0.0583 | 0.108 | 0.0666 | 0.0997 | 0.0749 | 0.05 | 0.05 | 0.05 | 0.0956 | 0.079 | 0.05 | 2.8977 | 0.121 | 0.3161 | 0.2878 | 0.3551 | 0.2553 | 0.0989 | 0.1729 | 0.6402 | 2.6501 | 3.4538 | 0.1012 | 0.0523 | 0.1741 | 0.1074 | 0.05 | 0.29 | 0.1555 | 0.3803 | 0.6844 | 0.836 | 0.7187 | 2.0877 | 0.7713 | 1.3992 | 0.593 | 0.6949 | 0.7518 | 0.5373 | 0.3644 | 0.5584 | 0.2376
Load_TR9_F5_45 | prosumer | 0.1036 | 0.1706 | 0.0976 | 0.0586 | 0.2602 | 0.053 | 0.1323 | 0.1865 | 0.053 | 0.174 | 0.1448 | 0.053 | 0.1223 | 0.587 | 1.4668 | 0.2019 | 1.5513 | 0.6897 | 0.3013 | 0.3667 | 0.2005 | 0.1182 | 0.3666 | 0.3576 | 0.1422 | 0.1766 | 0.053 | 0.1422 | 0.1766 | 0.1422 | 0.053 | 0.2658 | 0.053 | 0.1373 | 0.1716 | 0.2485 | 0.4158 | 0.3752 | 0.3559 | 0.4472 | 0.4233 | 0.5942 | 0.442 | 1.4198 | 1.6793 | 0.4103 | 0.2411 | 0.171
Load_TR9_F5_46 | customer | 0.3398 | 0.053 | 0.1617 | 0.2429 | 0.0866 | 0.0866 | 0.1951 | 0.1562 | 0.177 | 0.0908 | 0.2076 | 0.1643 | 0.1646 | 0.2153 | 0.5527 | 0.6306 | 0.4116 | 0.232 | 0.1718 | 0.1016 | 0.202 | 0.2074 | 0.1173 | 0.2429 | 0.1727 | 0.1962 | 0.3358 | 0.1472 | 0.458 | 1.2857 | 0.2749 | 0.4339 | 1.0597 | 0.8525 | 0.4597 | 0.5032 | 0.3017 | 0.1286 | 0.2313 | 0.5028 | 0.5858 | 0.7609 | 0.6387 | 0.7756 | 0.6367 | 0.6774 | 0.6668 | 0.1338
Load_TR9_F5_47 | customer | 0.033 | 0.033 | 0.033 | 0.0689 | 0.0689 | 0.033 | 0.033 | 0.033 | 0.0969 | 0.041 | 0.061 | 0.0769 | 0.0809 | 0.057 | 0.033 | 0.057 | 0.2721 | 0.1381 | 0.21 | 0.0728 | 0.1324 | 0.089 | 3.11 | 2.2321 | 0.6365 | 0.1025 | 0.1166 | 0.0567 | 0.1186 | 0.058 | 0.053 | 0.135 | 0.2414 | 0.069 | 0.0889 | 0.033 | 0.033 | 0.1097 | 0.0815 | 0.042 | 0.0621 | 0.1009 | 0.033 | 0.041 | 0.0969 | 0.033 | 0.1049 | 0.033
Load_TR9_F5_48 | prosumer | 0.046 | 0.1994 | 0.046 | 0.1576 | 0.0878 | 0.046 | 0.1994 | 0.046 | 0.1366 | 0.1088 | 0.046 | 0.046 | 0.1994 | 0.046 | 0.1392 | 0.3114 | 0.1786 | 1.5454 | 1.2938 | 0.6964 | 0.1645 | 0.0809 | 0.046 | 0.1994 | 0.1681 | 0.8241 | 0.4977 | 0.3759 | 0.0502 | 0.106 | 0.1571 | 0.0544 | 0.2113 | 0.165 | 0.1274 | 0.2055 | 0.0753 | 0.1924 | 0.0746 | 0.2884 | 0.1402 | 0.2244 | 0.3742 | 0.2583 | 0.3784 | 0.2107 | 1.2444 | 0.2241
Load_TR9_F5_49 | customer | 0.1577 | 0.1187 | 0.1892 | 0.1377 | 0.1302 | 0.05 | 0.2417 | 0.1196 | 0.1635 | 0.1977 | 0.05 | 0.05 | 0.1645 | 0.0633 | 0.1888 | 1.5059 | 0.3268 | 0.3363 | 0.2011 | 0.268 | 0.053 | 0.2851 | 0.1226 | 0.1292 | 0.9557 | 2.688 | 2.6528 | 0.3785 | 0.0887 | 0.2531 | 0.1081 | 0.1752 | 0.2222 | 0.7812 | 0.5604 | 0.4968 | 0.073 | 0.2243 | 0.1794 | 0.3821 | 0.4503 | 0.6376 | 1.169 | 0.9949 | 0.8171 | 0.8221 | 0.7545 | 0.7299
Load_TR9_F5_5 | customer | 0.1019 | 0.1584 | 0.0898 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.0739 | 0.0742 | 1.0916 | 1.9493 | 0.1718 | 0.1099 | 0.2555 | 0.2679 | 0.0623 | 0.0499 | 0.049 | 2.1216 | 0.5747 | 0.0567 | 0.0684 | 0.2778 | 0.1119 | 0.0671 | 0.2659 | 1.12 | 0.9137 | 0.1035 | 0.0582 | 0.0572 | 1.4034 | 1.0557 | 1.1871 | 0.8472 | 0.2592 | 0.2158 | 0.1981 | 0.4691 | 0.3156 | 0.233 | 0.049
Load_TR9_F5_50 | customer | 0.5914 | 0.5487 | 0.047 | 0.1283 | 0.047 | 0.0644 | 0.1109 | 0.047 | 0.1051 | 0.0702 | 0.047 | 0.144 | 0.047 | 0.0644 | 0.1109 | 0.047 | 0.1283 | 0.047 | 0.0612 | 0.3289 | 0.2523 | 0.0988 | 0.9447 | 0.115 | 1.4616 | 0.1225 | 0.047 | 0.076 | 0.2276 | 0.1126 | 0.1425 | 0.123 | 0.1414 | 0.1353 | 0.0919 | 0.3063 | 0.7747 | 0.461 | 0.2416 | 0.1753 | 0.047 | 0.1283 | 0.2942 | 0.8006 | 0.4576 | 0.4026 | 0.278 | 0.1283
Load_TR9_F5_51 | customer | 0.0976 | 0.0782 | 0.0937 | 0.051 | 0.051 | 0.051 | 0.1209 | 0.051 | 0.051 | 0.051 | 0.0937 | 0.0782 | 0.051 | 0.1209 | 0.051 | 0.0774 | 0.0994 | 0.0939 | 0.9849 | 0.0552 | 0.0667 | 0.3635 | 1.4397 | 0.2315 | 0.4509 | 1.862 | 0.961 | 0.4497 | 0.4021 | 0.5185 | 0.6261 | 0.3146 | 0.2796 | 0.3427 | 0.439 | 0.9075 | 0.5325 | 0.5705 | 0.1838 | 0.5676 | 0.4355 | 0.6852 | 0.702 | 0.6203 | 0.7449 | 0.4691 | 0.5668 | 0.1821
Load_TR9_F5_52 | prosumer | 0.054 | 0.1719 | 0.0786 | 0.0822 | 0.0892 | 0.054 | 0.054 | 0.1173 | 0.054 | 0.054 | 0.1173 | 0.054 | 0.0857 | 0.0857 | 0.054 | 0.1173 | 0.3058 | 0.3028 | 0.0669 | 0.3347 | 0.204 | 0.054 | 0.054 | 0.1138 | 0.0575 | 0.054 | 0.0997 | 0.0716 | 0.1033 | 0.0681 | 0.1173 | 0.1193 | 0.2397 | 2.8577 | 0.434 | 0.2038 | 0.2724 | 0.2786 | 0.4477 | 0.4133 | 0.4717 | 0.9095 | 1.2033 | 0.4327 | 0.4417 | 0.3476 | 0.0822 | 0.0892
Load_TR9_F5_53 | prosumer | 0.5994 | 0.5442 | 0.5475 | 0.6563 | 0.3339 | 0.096 | 0.045 | 0.1867 | 0.1313 | 0.1673 | 0.0643 | 0.0579 | 0.1738 | 0.0977 | 0.2202 | 0.0929 | 0.1606 | 0.1094 | 0.0828 | 0.3248 | 0.1287 | 0.045 | 0.0617 | 1.0719 | 0.2045 | 0.1611 | 0.1518 | 0.2799 | 0.0555 | 0.287 | 0.1089 | 0.1786 | 0.524 | 0.1265 | 0.1867 | 0.1393 | 0.1055 | 0.1713 | 0.1949 | 1.2712 | 0.3241 | 0.4527 | 0.5515 | 0.5493 | 0.3648 | 0.3606 | 0.1025 | 0.0738
Load_TR9_F5_54 | customer | 0.0719 | 0.042 | 0.042 | 0.2062 | 0.042 | 0.0868 | 0.1614 | 0.042 | 0.042 | 0.2062 | 0.042 | 0.0793 | 0.1689 | 0.042 | 0.042 | 0.1212 | 0.2172 | 0.0441 | 0.9284 | 0.2993 | 1.5256 | 2.1318 | 2.6132 | 0.7326 | 0.2395 | 0.5331 | 4.1265 | 2.5312 | 0.3727 | 0.3885 | 3.9087 | 2.8208 | 0.555 | 0.5504 | 1.3131 | 0.6176 | 0.101 | 0.2062 | 0.1007 | 0.3896 | 0.3672 | 0.3629 | 0.1615 | 0.4036 | 0.3691 | 0.3012 | 0.4581 | 0.1092
Load_TR9_F5_55 | prosumer | 0.1444 | 0.2298 | 0.1611 | 0.153 | 0.0963 | 0.3036 | 0.094 | 0.183 | 0.1906 | 0.2472 | 0.1842 | 0.1934 | 0.1515 | 0.2126 | 0.3054 | 0.2342 | 0.3648 | 0.0842 | 0.0958 | 0.2224 | 0.2155 | 0.1476 | 0.2902 | 0.0704 | 0.1315 | 0.253 | 0.1565 | 0.9093 | 0.4148 | 0.7124 | 0.1774 | 0.1669 | 0.63 | 0.1632 | 0.3355 | 0.5556 | 0.124 | 0.2595 | 0.2849 | 0.4331 | 0.5291 | 0.421 | 0.4536 | 0.419 | 0.4381 | 0.2754 | 0.2013 | 0.1494
Load_TR9_F5_56 | prosumer | 0.1651 | 0.047 | 0.2207 | 0.1215 | 0.0825 | 0.0913 | 0.1924 | 0.0833 | 0.2053 | 0.1235 | 0.1268 | 0.2198 | 0.1223 | 0.1006 | 0.2983 | 0.1835 | 0.8476 | 0.138 | 0.1268 | 0.047 | 0.5935 | 0.2266 | 0.2853 | 0.1769 | 0.1268 | 0.2154 | 0.0825 | 0.0913 | 0.2154 | 0.1268 | 0.047 | 0.047 | 0.273 | 0.0692 | 0.1896 | 0.1526 | 0.047 | 0.1268 | 0.1695 | 0.138 | 0.1096 | 0.3694 | 0.2127 | 0.3691 | 0.0592 | 0.1817 | 1.5382 | 1.4055
Load_TR9_F5_57 | customer | 0.1604 | 0.055 | 0.055 | 0.1118 | 0.1766 | 0.055 | 0.2334 | 0.055 | 0.6563 | 0.9147 | 0.4722 | 0.055 | 0.1847 | 0.2353 | 0.055 | 0.2334 | 0.055 | 0.1036 | 0.5109 | 1.4866 | 1.7703 | 2.1891 | 2.5585 | 1.9797 | 0.1361 | 0.055 | 0.055 | 0.168 | 0.8155 | 0.055 | 0.1199 | 1.6688 | 0.4948 | 0.7275 | 0.2765 | 0.2253 | 0.0717 | 0.4107 | 0.6492 | 0.8626 | 0.9268 | 2.4162 | 2.2719 | 1.1693 | 0.9561 | 1.0328 | 0.1604 | 0.128
Load_TR9_F5_58 | customer | 0.5998 | 0.2279 | 0.056 | 0.056 | 0.0794 | 0.2044 | 0.056 | 0.2201 | 0.0638 | 0.0794 | 0.2044 | 0.056 | 0.1263 | 0.1576 | 0.056 | 0.1956 | 0.2547 | 0.181 | 0.2263 | 0.2576 | 0.2134 | 0.4063 | 0.3751 | 0.3846 | 0.6016 | 0.5128 | 0.5043 | 0.2677 | 1.107 | 1.817 | 2.348 | 0.1705 | 0.1825 | 0.4845 | 0.056 | 0.1282 | 0.3764 | 0.1224 | 1.6757 | 1.4086 | 1.375 | 0.4526 | 0.2551 | 0.4675 | 0.2619 | 0.2431 | 0.0873 | 0.1966
Load_TR9_F5_59 | prosumer | 0.1314 | 0.055 | 0.0868 | 0.1633 | 0.055 | 0.055 | 0.1951 | 0.055 | 0.1187 | 0.1314 | 0.0677 | 0.1824 | 0.055 | 0.2395 | 1.9225 | 0.9754 | 1.3233 | 1.8482 | 1.2958 | 0.2631 | 0.2753 | 0.4026 | 0.1484 | 0.2069 | 0.5373 | 0.5677 | 0.5401 | 0.2986 | 0.4586 | 0.2953 | 0.3023 | 0.4501 | 0.2202 | 0.3556 | 1.3429 | 0.1535 | 0.2067 | 0.0968 | 0.2085 | 0.2217 | 0.3476 | 0.528 | 0.3666 | 0.3974 | 1.0337 | 0.3053 | 0.5058 | 0.171
Load_TR9_F5_6 | prosumer | 0.1485 | 0.1704 | 0.2205 | 0.1769 | 0.048 | 0.2205 | 0.1769 | 0.1342 | 0.2502 | 0.0609 | 0.2205 | 0.106 | 0.2443 | 0.095 | 0.1769 | 0.2205 | 0.4403 | 0.2516 | 0.2474 | 0.048 | 0.1769 | 0.2205 | 0.1769 | 0.095 | 0.1734 | 0.0544 | 0.241 | 0.1499 | 0.1382 | 0.2199 | 0.1709 | 0.1793 | 0.3705 | 0.141 | 0.4137 | 0.4205 | 0.4351 | 0.3988 | 0.5446 | 0.599 | 0.5831 | 0.8045 | 0.6223 | 0.8015 | 0.9001 | 0.7618 | 0.58 | 0.9914
Load_TR9_F5_60 | customer | 0.048 | 0.091 | 0.1628 | 0.1259 | 0.2058 | 0.1259 | 0.048 | 0.2664 | 0.0653 | 0.1546 | 0.1771 | 0.1259 | 0.2058 | 0.1259 | 0.1197 | 0.1684 | 0.1076 | 0.1098 | 0.2147 | 0.1671 | 0.2203 | 0.1114 | 0.0913 | 0.0826 | 0.2707 | 0.061 | 0.1259 | 0.2058 | 0.2365 | 0.3792 | 0.3302 | 0.0567 | 0.3386 | 0.2015 | 0.2571 | 0.1848 | 0.3652 | 0.2416 | 0.1521 | 0.546 | 0.3229 | 0.048 | 0.2837 | 0.048 | 0.0956 | 0.2361 | 0.048 | 0.2334
Load_TR9_F5_61 | prosumer | 0.1491 | 0.1391 | 0.083 | 0.034 | 0.1911 | 0.1461 | 0.034 | 0.1881 | 0.103 | 0.08 | 0.1881 | 0.1491 | 0.097 | 0.1251 | 0.2994 | 0.4737 | 0.2383 | 0.5974 | 0.041 | 0.0743 | 0.2068 | 0.09 | 0.0608 | 0.2764 | 0.034 | 0.1491 | 0.1706 | 0.5376 | 0.4566 | 0.3491 | 0.3623 | 0.359 | 0.4337 | 0.1878 | 0.882 | 1.9299 | 0.4614 | 0.2341 | 1.177 | 0.7608 | 0.6809 | 0.7768 | 0.9805 | 0.7012 | 0.7603 | 0.8927 | 0.9862 | 0.6767
Load_TR9_F5_62 | customer | 0.1499 | 0.05 | 0.05 | 0.1049 | 0.095 | 0.05 | 0.1349 | 0.065 | 0.05 | 0.05 | 0.055 | 0.1449 | 0.05 | 0.05 | 0.05 | 0.0616 | 0.0868 | 0.1096 | 0.1595 | 0.0636 | 0.1499 | 0.05 | 0.1499 | 0.05 | 0.095 | 0.1049 | 0.05 | 0.1991 | 0.125 | 0.2259 | 0.328 | 0.1593 | 0.2107 | 0.2746 | 0.1589 | 0.1365 | 0.1903 | 0.2749 | 0.2307 | 1.6831 | 0.2909 | 0.3066 | 0.2822 | 0.3704 | 0.3082 | 0.9488 | 0.8168 | 0.2389
Load_TR9_F5_63 | prosumer | 0.053 | 0.053 | 0.1606 | 0.053 | 0.1452 | 0.0684 | 0.053 | 0.1529 | 0.0607 | 0.053 | 0.1606 | 0.053 | 0.0991 | 0.1145 | 0.053 | 0.1606 | 0.053 | 0.0537 | 0.1634 | 0.2302 | 0.3063 | 0.1736 | 0.5629 | 0.9979 | 0.0675 | 0.1057 | 0.1407 | 0.0878 | 0.972 | 0.1265 | 0.1479 | 0.0761 | 0.1375 | 0.053 | 0.053 | 0.1879 | 0.3499 | 1.1288 | 0.5981 | 0.2402 | 0.053 | 0.053 | 0.1606 | 0.053 | 0.1606 | 0.053 | 0.0607 | 0.1529
Load_TR9_F5_64 | prosumer | 0.1478 | 0.1059 | 0.05 | 0.05 | 0.2037 | 0.05 | 0.1269 | 0.1269 | 0.05 | 0.2037 | 0.05 | 0.2037 | 0.05 | 0.1199 | 0.1338 | 0.0543 | 0.2443 | 0.1614 | 0.223 | 0.3209 | 0.1951 | 0.3382 | 0.229 | 1.3619 | 0.265 | 0.1515 | 0.2037 | 0.05 | 0.1467 | 0.3094 | 1.259 | 0.2287 | 0.0984 | 0.1677 | 0.2486 | 0.1656 | 0.2381 | 0.1488 | 0.162 | 0.3544 | 1.2102 | 0.2354 | 0.7016 | 0.4429 | 0.3211 | 0.1987 | 0.2223 | 0.5724
Load_TR9_F5_65 | customer | 0.1096 | 0.052 | 0.168 | 0.1108 | 0.0958 | 0.1399 | 0.0951 | 0.1197 | 0.048 | 0.1197 | 0.1831 | 0.0998 | 0.1739 | 0.109 | 0.048 | 0.2349 | 0.048 | 0.1213 | 0.1616 | 0.048 | 0.1563 | 0.1265 | 0.1077 | 0.1594 | 0.0637 | 0.1161 | 0.0951 | 0.1157 | 0.2234 | 0.172 | 0.048 | 0.1632 | 0.1197 | 0.1527 | 0.3295 | 0.2339 | 0.4542 | 0.508 | 0.3408 | 0.5425 | 0.5785 | 0.506 | 0.1318 | 0.0759 | 0.2965 | 0.3419 | 0.3942 | 0.1793
Load_TR9_F5_66 | customer | 0.2264 | 0.052 | 0.1512 | 0.052 | 0.0768 | 0.2115 | 0.052 | 0.2316 | 0.0567 | 0.1512 | 0.0709 | 0.1182 | 0.1512 | 0.052 | 0.1958 | 0.2672 | 0.1541 | 0.1591 | 0.1549 | 0.0867 | 0.2699 | 0.1512 | 0.1371 | 0.0768 | 0.1264 | 0.1371 | 0.0619 | 0.1933 | 0.0851 | 0.052 | 0.1264 | 0.0768 | 0.057 | 0.2533 | 0.073 | 0.1064 | 0.2033 | 0.052 | 0.1413 | 0.1045 | 0.2027 | 1.3042 | 0.487 | 0.516 | 0.6302 | 0.6205 | 0.607 | 0.2511
Load_TR9_F5_67 | prosumer | 0.081 | 0.2796 | 0.049 | 0.2026 | 0.1579 | 0.049 | 0.1356 | 0.201 | 0.073 | 0.1979 | 0.1626 | 0.1323 | 0.2282 | 0.049 | 0.225 | 0.049 | 0.049 | 0.2283 | 0.1322 | 0.049 | 0.1259 | 0.2346 | 0.049 | 0.2491 | 0.1114 | 0.1627 | 0.1979 | 0.049 | 0.2779 | 0.0827 | 0.1308 | 0.2298 | 0.049 | 0.049 | 0.1308 | 0.2298 | 0.1521 | 0.209 | 0.065 | 0.0906 | 0.27 | 0.049 | 0.3116 | 0.049 | 0.177 | 0.097 | 0.081 | 0.193
Load_TR9_F5_68 | customer | 0.3348 | 1.2986 | 0.4244 | 0.1076 | 0.1289 | 0.1935 | 0.043 | 0.1836 | 0.1209 | 0.0688 | 0.207 | 0.1076 | 0.2149 | 0.043 | 0.1074 | 0.336 | 0.1331 | 0.3342 | 0.2144 | 0.1326 | 0.1076 | 0.1055 | 0.156 | 0.1159 | 0.4096 | 0.1471 | 0.0597 | 0.197 | 0.2085 | 0.2727 | 0.0821 | 0.1076 | 0.1211 | 0.1367 | 0.1076 | 0.2149 | 0.0574 | 0.2651 | 0.1015 | 0.3181 | 0.5059 | 0.4299 | 0.4875 | 0.3207 | 0.6321 | 0.4502 | 0.4628 | 0.2833
Load_TR9_F5_7 | customer | 0.054 | 0.054 | 0.2292 | 0.054 | 0.2053 | 0.0779 | 0.054 | 0.2292 | 0.054 | 0.1735 | 0.1098 | 0.054 | 0.2292 | 0.054 | 0.2556 | 0.342 | 0.2153 | 0.331 | 0.2925 | 0.2425 | 0.3985 | 0.1117 | 0.1667 | 0.1686 | 0.054 | 0.1416 | 0.1416 | 0.0575 | 0.1894 | 0.0938 | 0.0949 | 0.3019 | 0.147 | 0.298 | 0.1404 | 0.137 | 0.2954 | 0.116 | 0.3385 | 0.3565 | 0.399 | 0.5824 | 0.6396 | 0.5397 | 0.6129 | 0.3975 | 0.4286 | 0.0938
Load_TR9_F5_8 | prosumer | 0.06 | 0.2428 | 0.152 | 0.1902 | 0.1849 | 0.2099 | 0.06 | 0.3348 | 0.06 | 0.1904 | 0.2044 | 0.06 | 0.3348 | 0.06 | 0.2889 | 0.1059 | 0.1386 | 0.2562 | 0.06 | 0.0863 | 0.276 | 0.0925 | 0.152 | 0.1126 | 0.06 | 0.2046 | 0.1902 | 0.4171 | 0.2076 | 0.2398 | 0.1257 | 0.1186 | 0.1908 | 0.178 | 0.1774 | 0.2963 | 0.3515 | 0.2009 | 0.6494 | 0.6687 | 1.3503 | 1.3382 | 0.7974 | 1.0016 | 1.3009 | 1.0223 | 0.875 | 0.5216
Load_TR9_F5_9 | customer | 0.1833 | 0.1591 | 0.037 | 0.1394 | 0.203 | 0.0541 | 0.2076 | 0.037 | 0.1569 | 0.2078 | 0.0617 | 0.1774 | 0.1694 | 0.1132 | 0.2529 | 0.049 | 0.2049 | 0.1613 | 0.1043 | 0.2446 | 0.1608 | 0.2745 | 0.3399 | 0.9871 | 0.2916 | 0.2177 | 0.1819 | 0.1932 | 0.3153 | 1.7103 | 0.8103 | 0.2615 | 1.2081 | 0.832 | 0.3076 | 0.2111 | 0.2316 | 0.4517 | 0.3119 | 0.5211 | 0.8261 | 1.4494 | 0.44 | 0.3287 | 0.1474 | 0.4401 | 0.2688 | 0.296
Load_TR9_F6_1 | customer | 0.041 | 0.112 | 0.041 | 0.112 | 0.041 | 0.112 | 0.041 | 0.041 | 0.041 | 0.041 | 0.0804 | 0.0725 | 1.3923 | 0.2898 | 0.0483 | 0.0923 | 0.0648 | 0.041 | 0.112 | 0.041 | 0.041 | 0.112 | 0.041 | 0.041 | 0.042 | 0.1034 | 0.211 | 0.3642 | 0.2427 | 0.3485 | 0.2646 | 0.3924 | 0.4183 | 0.2181 | 0.2788 | 0.3901 | 1.3275 | 1.8435 | 0.731 | 0.2526 | 0.3799 | 0.37 | 0.3221 | 0.3614 | 0.1936 | 0.041 | 0.112 | 0.041
Load_TR9_F6_10 | customer | 0.052 | 0.1186 | 0.1613 | 0.052 | 0.2279 | 0.052 | 0.1186 | 0.1613 | 0.052 | 0.052 | 0.1121 | 0.1012 | 0.1678 | 0.1121 | 0.2773 | 0.3113 | 0.5342 | 0.3918 | 0.3089 | 0.244 | 0.052 | 0.052 | 0.0668 | 0.1038 | 0.1613 | 0.1186 | 0.1613 | 0.052 | 0.0927 | 0.1325 | 0.114 | 0.1658 | 0.1066 | 0.1186 | 0.1613 | 0.1186 | 0.1558 | 0.0575 | 0.052 | 0.2169 | 0.0629 | 0.3832 | 0.495 | 0.4527 | 0.2498 | 0.2131 | 0.0668 | 0.0705
Load_TR9_F6_11 | customer | 0.041 | 0.1877 | 0.2482 | 0.041 | 0.2542 | 0.1817 | 0.0655 | 0.1529 | 0.1817 | 0.1633 | 0.1178 | 0.3181 | 0.041 | 0.2701 | 0.1658 | 0.0766 | 0.4036 | 0.3181 | 0.1043 | 0.7129 | 1.8022 | 0.8775 | 0.4 | 0.2339 | 0.3309 | 0.041 | 0.1958 | 0.1633 | 0.0973 | 0.1395 | 0.1912 | 0.2447 | 0.041 | 0.2697 | 0.1103 | 0.1349 | 0.3267 | 0.2801 | 0.3054 | 0.2802 | 0.4678 | 0.6157 | 0.3544 | 0.2483 | 0.133 | 0.3226 | 0.1133 | 0.2058
Load_TR9_F6_12 | prosumer | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.0552 | 0.128 | 0.18 | 0.1399 | 0.2018 | 0.1592 | 0.053 | 0.1495 | 0.2362 | 0.1711 | 0.093 | 1.3663 | 0.1785 | 0.247 | 0.0998 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.0938 | 0.1275 | 0.1115 | 0.4656 | 0.2979 | 0.1001 | 0.053 | 0.053 | 0.4857 | 0.4521 | 0.7126 | 0.1609
Load_TR9_F6_13 | prosumer | 0.059 | 0.1475 | 0.1203 | 0.0794 | 0.1884 | 0.059 | 0.059 | 0.2088 | 0.059 | 0.0862 | 0.1816 | 0.059 | 0.059 | 0.2088 | 0.059 | 0.202 | 0.1988 | 0.4981 | 0.2341 | 0.3119 | 0.5542 | 0.4725 | 0.2271 | 0.3887 | 1.5262 | 0.3133 | 0.4614 | 0.4639 | 0.1002 | 0.1913 | 0.5063 | 0.7487 | 0.6873 | 0.8188 | 0.3371 | 0.3087 | 0.4588 | 1.7736 | 0.3947 | 0.4837 | 1.674 | 0.5374 | 0.6608 | 0.9905 | 1.746 | 1.6349 | 0.7602 | 0.0726
Load_TR9_F6_14 | prosumer | 0.1105 | 0.1409 | 0.036 | 0.0658 | 0.1702 | 0.036 | 0.2 | 0.036 | 0.036 | 0.2 | 0.036 | 0.036 | 0.2 | 0.036 | 0.0435 | 0.215 | 0.0435 | 0.0485 | 0.2045 | 0.036 | 0.0509 | 0.1851 | 0.036 | 0.0807 | 0.1552 | 0.036 | 0.036 | 0.2026 | 0.3019 | 1.207 | 0.0909 | 0.1262 | 0.143 | 0.0627 | 0.2383 | 0.0615 | 0.04 | 0.1454 | 0.2401 | 0.271 | 0.4008 | 0.395 | 0.5714 | 0.5932 | 0.4223 | 0.4381 | 0.3057 | 0.305
Load_TR9_F6_15 | prosumer | 0.4989 | 0.6213 | 0.2679 | 0.1765 | 0.1866 | 0.2721 | 0.1794 | 0.255 | 0.1536 | 0.1723 | 0.1689 | 0.2836 | 0.1251 | 0.1437 | 0.2589 | 0.2321 | 0.058 | 0.2118 | 0.2247 | 0.2344 | 0.1437 | 0.2025 | 1.8257 | 2.081 | 0.6405 | 0.4047 | 0.3807 | 0.6716 | 0.1033 | 0.2851 | 0.2021 | 0.0723 | 0.4035 | 0.0694 | 0.2408 | 0.2465 | 0.091 | 0.3428 | 0.5995 | 0.9054 | 0.5255 | 0.9658 | 0.8125 | 0.7217 | 0.8593 | 0.9206 | 0.822 | 0.236
Load_TR9_F6_16 | prosumer | 0.1521 | 0.041 | 0.2431 | 0.041 | 0.041 | 0.2134 | 0.0707 | 0.0528 | 0.1754 | 0.0969 | 0.0904 | 0.1937 | 0.041 | 0.2431 | 0.041 | 0.1188 | 0.1653 | 0.1129 | 1.9727 | 0.4666 | 0.3996 | 0.4737 | 0.1089 | 0.041 | 0.041 | 0.041 | 0.1712 | 0.057 | 0.1264 | 0.2626 | 0.2035 | 0.1306 | 0.0975 | 0.2341 | 0.1441 | 0.1965 | 0.2996 | 0.4575 | 0.2759 | 0.4943 | 0.041 | 0.1357 | 0.4136 | 0.3023 | 0.5755 | 0.6764 | 0.4409 | 0.4726
Load_TR9_F6_17 | prosumer | 0.055 | 0.3199 | 0.0617 | 0.1259 | 0.3515 | 0.2803 | 0.3727 | 1.3461 | 0.0505 | 0.1046 | 0.037 | 0.037 | 0.1181 | 0.037 | 0.1181 | 0.1474 | 0.3387 | 0.1699 | 1.7919 | 0.9711 | 0.3198 | 0.0902 | 0.1181 | 0.037 | 0.082 | 0.1112 | 0.2524 | 0.0828 | 1.4081 | 0.3186 | 0.3844 | 0.037 | 0.4687 | 0.2444 | 0.2364 | 0.1854 | 0.1782 | 0.1437 | 0.2281 | 0.398 | 0.6401 | 0.7186 | 0.4868 | 0.7422 | 1.3567 | 2.1454 | 0.845 | 0.6389
Load_TR9_F6_18 | customer | 0.043 | 0.043 | 0.3915 | 0.2192 | 0.2246 | 0.1182 | 0.043 | 0.043 | 0.1182 | 0.043 | 0.0848 | 0.0764 | 0.043 | 0.1182 | 0.043 | 0.0973 | 0.0639 | 0.1566 | 0.9703 | 0.2427 | 0.1873 | 0.2673 | 0.3341 | 1.0896 | 0.4457 | 0.6726 | 1.4895 | 2.0191 | 3.3654 | 1.9333 | 0.0764 | 0.0485 | 0.2104 | 0.1393 | 0.2109 | 0.7416 | 1.9543 | 0.3796 | 0.1343 | 1.1383 | 0.2346 | 0.2736 | 0.3935 | 0.4165 | 0.3473 | 0.1182 | 0.043 | 0.043
Load_TR9_F6_19 | prosumer | 0.1489 | 0.0821 | 0.042 | 0.189 | 0.042 | 0.042 | 0.1222 | 0.1088 | 0.0687 | 0.1623 | 0.042 | 0.1489 | 0.0821 | 0.1394 | 0.1757 | 0.1111 | 0.1686 | 0.1389 | 0.042 | 0.189 | 0.042 | 0.1088 | 0.1222 | 0.042 | 0.042 | 0.1824 | 0.0554 | 0.1715 | 0.1362 | 0.042 | 1.7143 | 0.0621 | 0.1373 | 0.3129 | 0.4083 | 0.3813 | 0.4322 | 1.658 | 0.1556 | 0.0754 | 0.2226 | 0.5597 | 0.4283 | 0.5077 | 0.6936 | 1.3586 | 0.3208 | 0.169
Load_TR9_F6_2 | customer | 0.049 | 0.2227 | 0.049 | 0.049 | 0.2227 | 0.049 | 0.049 | 0.1911 | 0.0806 | 0.0885 | 0.1832 | 0.049 | 0.1516 | 0.1201 | 0.049 | 0.2227 | 0.049 | 0.0569 | 0.1641 | 0.1847 | 0.6622 | 0.4922 | 1.9595 | 3.0177 | 1.6081 | 0.049 | 0.2762 | 0.1911 | 0.0502 | 0.0711 | 0.2448 | 0.0556 | 0.2926 | 0.3847 | 0.3656 | 0.3989 | 0.4312 | 0.2791 | 0.242 | 1.3524 | 1.2675 | 0.4609 | 0.7192 | 0.4998 | 0.4661 | 0.3006 | 0.3043 | 0.4833
Load_TR9_F6_20 | prosumer | 0.0787 | 0.1963 | 0.1371 | 0.1848 | 0.1772 | 0.0615 | 0.2537 | 0.0969 | 0.05 | 0.1589 | 0.2031 | 0.05 | 0.2115 | 0.1504 | 0.0739 | 0.2881 | 0.05 | 0.2126 | 0.3631 | 0.2712 | 0.3035 | 0.2371 | 0.1525 | 0.1784 | 0.1609 | 0.2485 | 0.3003 | 0.881 | 0.1837 | 0.3193 | 0.2766 | 0.4681 | 0.2953 | 1.064 | 0.3438 | 0.2757 | 0.3545 | 0.2322 | 0.158 | 0.4381 | 0.332 | 0.3963 | 0.4858 | 0.4946 | 0.6232 | 0.8757 | 0.5518 | 0.7945
Load_TR9_F6_21 | customer | 0.1379 | 0.0791 | 0.057 | 0.1599 | 0.057 | 0.0791 | 0.1379 | 0.057 | 0.057 | 0.1599 | 0.057 | 0.057 | 0.1526 | 0.0644 | 0.057 | 0.1599 | 0.057 | 0.3124 | 2.2585 | 2.9768 | 0.9672 | 0.057 | 0.057 | 0.1935 | 0.057 | 0.057 | 0.1879 | 0.1329 | 0.0902 | 0.3141 | 0.0864 | 0.057 | 2.458 | 2.8762 | 0.6529 | 0.199 | 0.067 | 0.0627 | 0.2911 | 0.3588 | 0.4137 | 0.57 | 0.6139 | 0.5288 | 0.7143 | 0.7374 | 0.704 | 0.1232
Load_TR9_F6_22 | prosumer | 0.156 | 0.2423 | 0.059 | 0.1837 | 0.0867 | 0.1677 | 0.1682 | 0.1725 | 0.1358 | 0.2044 | 0.0659 | 0.123 | 0.1576 | 0.2215 | 0.1422 | 0.4851 | 0.0798 | 0.0654 | 0.2429 | 0.149 | 0.769 | 1.4466 | 0.187 | 0.1947 | 0.1133 | 0.1698 | 0.4289 | 0.16 | 0.1515 | 1.0742 | 0.5369 | 0.4872 | 0.6143 | 0.5038 | 0.5101 | 2.214 | 1.4007 | 0.3184 | 0.7006 | 0.6332 | 1.5705 | 0.3868 | 0.9106 | 0.5368 | 0.8006 | 0.3586 | 0.2631 | 0.1352
Load_TR9_F6_23 | customer | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.1403 | 0.0683 | 0.1676 | 0.095 | 0.0603 | 0.2496 | 0.5504 | 1.1195 | 0.4361 | 0.3277 | 0.2575 | 0.4459 | 0.3291 | 0.4991 | 1.1131 | 0.1818 | 1.0446 | 0.2906 | 0.5625 | 0.6073 | 0.7326 | 0.7114 | 0.4819 | 0.8153 | 0.2891 | 0.055 | 0.055 | 0.055
Load_TR9_F6_24 | customer | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.101 | 0.1178 | 0.1178 | 0.1949 | 0.2174 | 0.1874 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053
Load_TR9_F6_25 | prosumer | 0.1099 | 0.0949 | 0.2178 | 0.0765 | 0.1132 | 0.1349 | 0.1716 | 0.101 | 0.1349 | 0.2206 | 0.052 | 0.1278 | 0.2277 | 0.052 | 0.1274 | 0.1424 | 0.1604 | 0.1952 | 0.0742 | 0.1194 | 0.1349 | 0.1349 | 0.1377 | 0.1952 | 0.0842 | 0.2709 | 0.9023 | 0.2073 | 0.4138 | 0.0636 | 0.1377 | 0.2027 | 0.0671 | 0.183 | 0.1726 | 0.1194 | 0.1985 | 0.0897 | 0.198 | 0.1575 | 0.052 | 0.1377 | 0.165 | 0.1905 | 0.052 | 0.2178 | 0.1377 | 0.2027
Load_TR9_F6_26 | customer | 0.6389 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1474 | 0.0742 | 0.0919 | 0.1201 | 0.3111 | 0.05 | 0.2771 | 0.0695 | 0.0523 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0522 | 0.3299 | 0.2366 | 0.3456 | 0.0616 | 0.0519 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2573 | 0.2749 | 0.3586 | 0.05 | 0.05 | 0.05 | 0.05
Load_TR9_F6_27 | prosumer | 0.127 | 0.05 | 0.05 | 0.1578 | 0.05 | 0.1424 | 0.0654 | 0.05 | 0.1578 | 0.05 | 0.1424 | 0.2642 | 0.05 | 0.1578 | 0.05 | 0.0808 | 0.127 | 0.3171 | 0.2135 | 0.32 | 0.1935 | 0.5932 | 0.974 | 0.0581 | 1.0127 | 0.3863 | 1.8655 | 1.3416 | 1.436 | 1.7228 | 0.4947 | 0.1266 | 0.2609 | 1.6403 | 1.2782 | 0.2902 | 0.2698 | 0.2529 | 0.1935 | 0.1919 | 0.6105 | 0.515 | 0.6579 | 0.7414 | 0.05 | 0.05 | 0.05 | 0.1424
Load_TR9_F6_28 | prosumer | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.0546 | 0.0653 | 0.0968 | 0.1522 | 0.0629 | 0.3598 | 1.6063 | 0.2192 | 0.2314 | 0.1335 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.3376 | 0.4487 | 0.4591 | 0.4416 | 0.7366 | 0.345 | 0.298 | 0.3475 | 0.053 | 0.0627
Load_TR9_F6_29 | customer | 1.507 | 0.2281 | 0.1389 | 0.1572 | 0.318 | 0.1442 | 0.055 | 0.3078 | 0.0782 | 0.055 | 0.2477 | 0.2275 | 0.2229 | 0.055 | 0.1618 | 0.2241 | 0.1629 | 0.52 | 0.2801 | 0.7356 | 0.5802 | 0.2341 | 0.1758 | 0.2394 | 0.1442 | 0.1847 | 0.2904 | 0.055 | 0.3342 | 0.141 | 0.055 | 0.1779 | 0.2438 | 0.1183 | 0.2831 | 0.258 | 1.6771 | 1.4958 | 0.927 | 0.4027 | 0.3672 | 0.2547 | 0.4035 | 0.4954 | 1.7856 | 1.6459 | 0.3132 | 0.1442
Load_TR9_F6_3 | customer | 0.552 | 0.5336 | 0.0791 | 0.0852 | 0.047 | 0.1639 | 0.1108 | 0.1769 | 0.034 | 0.1249 | 0.1627 | 0.034 | 0.0535 | 0.2342 | 0.034 | 0.1108 | 0.1769 | 0.1162 | 0.1939 | 0.7136 | 1.6256 | 0.1821 | 0.1692 | 0.0511 | 0.1769 | 0.0894 | 0.0878 | 0.1444 | 0.1108 | 0.1769 | 0.034 | 0.0596 | 0.2216 | 0.0405 | 0.0766 | 0.211 | 0.034 | 0.2277 | 0.06 | 0.0917 | 0.196 | 0.0681 | 0.3383 | 0.2615 | 0.4739 | 0.7498 | 0.4101 | 0.5486
Load_TR9_F6_30 | prosumer | 0.6829 | 0.1487 | 0.1433 | 0.054 | 0.054 | 0.1433 | 0.054 | 0.0987 | 0.0987 | 0.054 | 0.1433 | 0.054 | 0.1242 | 0.0731 | 0.054 | 0.054 | 0.1709 | 0.054 | 0.054 | 0.1433 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 1.3204 | 1.0702 | 0.3336 | 0.5809 | 0.2345 | 0.504 | 0.5493 | 0.267 | 0.2337 | 0.1306 | 0.1097 | 0.3133 | 0.1131 | 0.0972 | 0.454 | 0.3174 | 0.4346 | 0.7294 | 0.5623 | 0.672 | 0.5912 | 0.5069 | 0.6457
Load_TR9_F6_31 | prosumer | 0.7337 | 0.4382 | 0.8315 | 0.6654 | 0.4899 | 0.5671 | 0.207 | 0.053 | 0.1706 | 0.302 | 0.1636 | 0.2451 | 0.1169 | 0.1636 | 0.246 | 0.1436 | 0.1359 | 0.067 | 0.5709 | 0.0806 | 0.197 | 0.3682 | 0.1509 | 0.2777 | 0.1251 | 0.2653 | 0.2073 | 0.165 | 0.2782 | 0.0824 | 1.5652 | 0.3238 | 0.7983 | 0.714 | 0.3466 | 0.3934 | 0.5162 | 0.1955 | 0.3509 | 0.6999 | 0.9316 | 0.6246 | 0.4953 | 0.4707 | 1.172 | 0.4837 | 0.7627 | 0.162
Load_TR9_F6_32 | customer | 0.102 | 0.1336 | 0.1508 | 0.05 | 0.2343 | 0.05 | 0.05 | 0.128 | 0.1563 | 0.05 | 0.1336 | 0.1378 | 0.063 | 0.2083 | 0.076 | 0.0673 | 0.1942 | 0.0728 | 0.128 | 0.2284 | 0.3522 | 0.3094 | 0.3283 | 0.1982 | 0.05 | 0.2127 | 0.0717 | 0.178 | 0.1063 | 0.05 | 0.2343 | 0.05 | 0.1563 | 0.05 | 0.1432 | 0.1411 | 0.05 | 0.204 | 0.0803 | 0.089 | 0.1953 | 0.05 | 0.05 | 0.377 | 0.2299 | 0.2557 | 0.3889 | 0.4533
Load_TR9_F6_33 | customer | 0.058 | 0.1998 | 0.0762 | 0.1901 | 0.0859 | 0.058 | 0.218 | 0.058 | 0.1139 | 0.0804 | 0.058 | 0.1998 | 0.0762 | 0.1139 | 0.1621 | 0.058 | 0.1589 | 0.1171 | 0.0853 | 0.1125 | 0.1362 | 0.0762 | 0.1551 | 0.1027 | 0.1261 | 0.1499 | 0.108 | 0.0898 | 0.1907 | 0.0853 | 0.0971 | 0.0971 | 0.1964 | 0.3697 | 0.1048 | 0.1815 | 0.1588 | 0.19 | 0.4683 | 0.4608 | 0.6936 | 0.8142 | 0.6415 | 0.5772 | 0.3928 | 0.5212 | 0.1499 | 0.1352
Load_TR9_F6_34 | prosumer | 0.1604 | 0.146 | 0.0993 | 0.2464 | 0.1486 | 0.2464 | 0.05 | 0.0893 | 0.1793 | 0.1764 | 0.1173 | 0.2214 | 0.1062 | 0.05 | 0.2609 | 0.05 | 1.0832 | 0.1787 | 0.1473 | 0.229 | 0.1154 | 0.1622 | 0.05 | 0.1486 | 0.2183 | 0.078 | 0.4863 | 0.1631 | 0.1437 | 1.6547 | 3.442 | 2.5557 | 0.4685 | 0.2429 | 0.2709 | 0.7899 | 0.4621 | 0.3407 | 0.2981 | 0.5661 | 0.3257 | 0.3186 | 0.4927 | 0.3999 | 0.4253 | 0.4266 | 0.05 | 0.05
Load_TR9_F6_35 | prosumer | 0.133 | 0.1726 | 0.1035 | 0.0899 | 0.2089 | 0.1444 | 0.049 | 0.1799 | 0.1735 | 0.1144 | 0.1435 | 0.1103 | 0.0831 | 0.1653 | 0.188 | 0.0926 | 0.1743 | 0.1471 | 0.2206 | 0.1971 | 0.3999 | 0.0776 | 0.1448 | 0.2017 | 0.4221 | 0.7898 | 0.1798 | 0.3244 | 0.0914 | 0.8639 | 0.494 | 0.2372 | 0.3199 | 0.0495 | 0.1368 | 0.2876 | 0.1581 | 1.5365 | 0.9181 | 0.1858 | 0.3383 | 0.3894 | 0.5756 | 0.768 | 1.7014 | 0.7933 | 0.263 | 0.0563
Load_TR9_F6_36 | customer | 0.1229 | 0.1048 | 0.2636 | 0.1733 | 0.0946 | 0.3423 | 0.051 | 0.1986 | 0.2383 | 0.0731 | 0.3254 | 0.0894 | 0.2783 | 0.051 | 0.305 | 0.5349 | 0.0803 | 0.4225 | 0.051 | 0.1342 | 0.3027 | 0.051 | 0.213 | 0.1731 | 0.1018 | 0.228 | 0.2307 | 0.1648 | 0.1763 | 0.1887 | 0.1656 | 0.1303 | 0.1848 | 0.252 | 0.08 | 0.1683 | 0.2396 | 0.051 | 0.2464 | 0.365 | 0.3026 | 0.5671 | 0.3052 | 0.5453 | 0.6002 | 0.7617 | 0.6653 | 0.1586
Load_TR9_F6_37 | prosumer | 0.1682 | 0.2022 | 0.054 | 0.2624 | 0.0859 | 0.5013 | 0.5032 | 0.229 | 0.154 | 0.1943 | 0.054 | 0.256 | 0.0923 | 0.054 | 0.2369 | 0.1114 | 0.1915 | 0.1568 | 0.0581 | 0.2657 | 0.0826 | 0.1178 | 0.2428 | 0.054 | 0.2425 | 0.109 | 0.0773 | 0.285 | 0.0595 | 0.2708 | 0.0939 | 0.143 | 0.2666 | 0.1469 | 0.3544 | 0.0599 | 0.3068 | 1.0344 | 0.3307 | 0.737 | 0.5354 | 0.5226 | 0.9581 | 1.6517 | 0.4325 | 0.4977 | 0.1752 | 0.1303
Load_TR9_F6_38 | prosumer | 0.7686 | 0.1095 | 0.2172 | 0.1095 | 0.033 | 0.1095 | 0.0581 | 0.1921 | 0.0925 | 0.2091 | 0.0581 | 0.1095 | 0.2172 | 0.0585 | 0.2514 | 0.0497 | 0.21 | 0.2476 | 0.0925 | 0.184 | 0.1512 | 0.1252 | 0.1335 | 0.1346 | 0.2214 | 0.3324 | 0.4193 | 0.1346 | 0.033 | 0.0879 | 0.379 | 0.0614 | 0.2287 | 0.5115 | 0.2686 | 0.2853 | 0.0986 | 0.0615 | 0.5209 | 1.4391 | 1.3432 | 0.4148 | 0.2032 | 0.4023 | 0.2672 | 0.5403 | 0.5171 | 0.168
Load_TR9_F6_39 | customer | 0.2067 | 0.1135 | 0.0562 | 0.2272 | 0.1012 | 0.0848 | 0.2436 | 0.048 | 0.048 | 0.2067 | 0.048 | 0.093 | 0.2282 | 0.0552 | 0.1418 | 0.1129 | 0.1219 | 0.0628 | 0.2538 | 0.1077 | 0.0637 | 0.0985 | 0.2067 | 0.048 | 0.1076 | 0.233 | 0.0954 | 0.048 | 0.2851 | 0.048 | 0.1217 | 0.2067 | 0.048 | 0.1866 | 0.1418 | 0.0573 | 0.2612 | 1.5529 | 1.5819 | 0.7079 | 0.3336 | 0.4709 | 1.0342 | 1.0734 | 0.4469 | 0.687 | 0.9072 | 1.0774
Load_TR9_F6_4 | prosumer | 0.3697 | 0.049 | 0.1196 | 0.1776 | 0.0866 | 0.2106 | 0.1243 | 0.1479 | 0.118 | 0.1251 | 0.1408 | 0.1808 | 0.1542 | 0.0498 | 1.1303 | 0.2848 | 0.2394 | 2.6547 | 2.7219 | 1.0703 | 1.3337 | 0.2487 | 0.1682 | 0.1479 | 0.4058 | 0.0747 | 0.3006 | 1.2539 | 0.1659 | 0.1245 | 0.2083 | 1.0122 | 0.2064 | 0.5365 | 1.2464 | 0.0623 | 0.3227 | 0.3625 | 0.0985 | 0.2618 | 0.3077 | 0.3057 | 0.1806 | 0.5383 | 0.587 | 0.4858 | 0.653 | 0.049
Load_TR9_F6_40 | prosumer | 0.2006 | 0.044 | 0.044 | 0.1827 | 0.174 | 0.044 | 0.2332 | 0.1234 | 0.1428 | 0.055 | 0.2962 | 0.0605 | 0.2563 | 0.1003 | 0.044 | 0.1538 | 0.2029 | 0.0879 | 0.3083 | 0.0657 | 0.1538 | 0.0615 | 0.5036 | 0.054 | 0.044 | 0.1538 | 0.3065 | 0.1355 | 0.069 | 0.1758 | 2.4487 | 0.1822 | 1.4102 | 1.289 | 0.0851 | 0.4381 | 0.3872 | 2.4522 | 0.1038 | 0.443 | 0.3028 | 0.4099 | 0.3691 | 0.2709 | 0.179 | 0.4276 | 0.3801 | 0.187
Load_TR9_F6_41 | prosumer | 0.163 | 0.05 | 0.2275 | 0.05 | 0.2033 | 0.0742 | 0.0823 | 0.1952 | 0.05 | 0.05 | 0.0742 | 0.2033 | 0.05 | 0.2275 | 0.05 | 0.1388 | 0.148 | 0.05 | 0.2275 | 0.2784 | 0.171 | 0.1255 | 0.062 | 1.3843 | 0.2022 | 1.5182 | 0.3755 | 0.4601 | 0.3149 | 0.1772 | 0.1193 | 0.0661 | 0.2114 | 0.05 | 0.4362 | 0.0818 | 0.5552 | 0.3192 | 0.12 | 0.3956 | 0.3684 | 0.577 | 0.7043 | 0.3784 | 0.5726 | 0.1673 | 0.1549 | 0.1226
Load_TR9_F6_42 | customer | 0.058 | 0.2545 | 0.137 | 0.058 | 0.2518 | 0.1397 | 0.058 | 0.193 | 0.1985 | 0.1709 | 0.058 | 0.1539 | 0.1858 | 0.1888 | 0.0919 | 0.2545 | 0.137 | 0.1745 | 0.217 | 0.058 | 0.4455 | 0.3984 | 0.529 | 0.2712 | 0.2841 | 1.0891 | 0.4307 | 0.2668 | 0.3747 | 0.1401 | 0.3792 | 0.2363 | 0.058 | 0.1923 | 0.1993 | 0.1257 | 0.2658 | 0.0749 | 0.2944 | 0.0802 | 0.4474 | 0.2472 | 0.633 | 0.2734 | 0.5181 | 0.5824 | 0.7108 | 0.5489
Load_TR9_F6_43 | prosumer | 0.2426 | 0.3286 | 0.3281 | 0.2313 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.1846 | 0.2832 | 0.1825 | 0.692 | 0.7799 | 0.2106 | 0.167 | 0.2106 | 0.1887 | 0.3292 | 1.1287 | 0.1342 | 0.1301 | 0.0705 | 0.0705 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.2827 | 0.1486 | 0.0755 | 0.171 | 0.1316 | 0.1852 | 0.1421 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Load_TR9_F6_44 | customer | 0.1238 | 0.035 | 0.035 | 0.2051 | 0.0885 | 0.0721 | 0.2215 | 0.035 | 0.035 | 0.035 | 0.191 | 0.1026 | 0.035 | 0.2385 | 0.0551 | 0.2359 | 1.1403 | 0.1932 | 0.3129 | 0.2945 | 0.1494 | 0.1631 | 0.0553 | 0.1984 | 0.035 | 0.1665 | 0.1142 | 0.4772 | 0.3645 | 0.1417 | 1.4256 | 1.0311 | 0.2018 | 0.0919 | 0.1613 | 0.0756 | 0.5024 | 0.2269 | 0.2199 | 0.4072 | 0.3589 | 0.391 | 0.035 | 0.1145 | 0.4529 | 0.1593 | 0.139 | 0.1546
Load_TR9_F6_45 | customer | 0.5746 | 0.5176 | 2.1448 | 0.5845 | 0.6833 | 0.4114 | 0.048 | 0.048 | 0.1128 | 0.101 | 0.1128 | 0.101 | 0.101 | 0.1128 | 0.0657 | 0.1481 | 0.2137 | 1.2125 | 0.3951 | 0.2607 | 0.4337 | 0.2745 | 0.4171 | 0.6796 | 0.2715 | 0.4233 | 0.2255 | 1.333 | 0.628 | 0.1127 | 0.2006 | 0.0715 | 0.1384 | 0.1649 | 0.048 | 0.4418 | 0.048 | 0.1422 | 0.0716 | 0.048 | 0.048 | 0.048 | 0.1658 | 0.048 | 0.3217 | 0.048 | 0.048 | 0.0833
Load_TR9_F6_46 | prosumer | 0.3078 | 0.6133 | 0.1305 | 0.1231 | 0.2202 | 0.1643 | 0.1467 | 0.3208 | 0.1176 | 0.235 | 0.155 | 0.1176 | 0.2533 | 0.2013 | 0.1872 | 0.3003 | 0.2046 | 0.2656 | 0.2848 | 1.0643 | 0.28 | 0.4218 | 0.6082 | 0.3813 | 0.125 | 0.1683 | 0.0885 | 0.2562 | 0.0604 | 0.1667 | 0.2879 | 0.1176 | 0.2183 | 0.1716 | 0.1899 | 0.1569 | 0.1608 | 0.1602 | 0.3485 | 0.053 | 0.2048 | 0.2498 | 0.0961 | 0.3437 | 0.1195 | 0.1166 | 0.2904 | 0.1265
Load_TR9_F6_47 | customer | 0.3379 | 0.052 | 0.289 | 0.1077 | 0.1016 | 0.2541 | 0.093 | 0.1551 | 0.2416 | 0.052 | 0.2277 | 0.169 | 0.2415 | 0.2745 | 0.3316 | 0.4695 | 0.3233 | 0.2317 | 0.3228 | 0.3136 | 0.1634 | 0.9055 | 0.6534 | 0.8715 | 0.9121 | 0.1922 | 0.2252 | 0.0794 | 0.052 | 0.2079 | 0.0999 | 0.1409 | 0.1938 | 0.203 | 0.052 | 0.1683 | 0.0725 | 0.6285 | 1.0438 | 0.3596 | 0.2108 | 0.1371 | 0.1136 | 0.1272 | 0.2079 | 0.1136 | 0.1272 | 0.1792
Load_TR9_F6_48 | prosumer | 0.084 | 0.1506 | 0.044 | 0.1373 | 0.0973 | 0.044 | 0.1106 | 0.1239 | 0.044 | 0.1573 | 0.0773 | 0.044 | 0.1906 | 0.044 | 0.064 | 0.1706 | 0.044 | 0.044 | 0.1944 | 0.6506 | 0.7751 | 0.1239 | 0.0533 | 0.1579 | 0.1029 | 0.1881 | 0.7824 | 0.4534 | 0.3136 | 0.0515 | 0.1053 | 0.2228 | 0.044 | 0.2368 | 0.7344 | 2.5742 | 0.7202 | 0.0742 | 0.2181 | 1.3551 | 0.044 | 0.044 | 0.1439 | 0.0906 | 0.104 | 0.1306 | 0.044 | 0.1706
Load_TR9_F6_49 | prosumer | 0.1289 | 0.1534 | 0.1549 | 0.108 | 0.1594 | 0.0722 | 0.2362 | 0.0619 | 0.2334 | 0.044 | 0.134 | 0.1744 | 0.0516 | 0.159 | 0.1442 | 0.1296 | 0.2367 | 0.2346 | 1.9013 | 3.0874 | 1.3577 | 0.9339 | 0.5932 | 0.1413 | 0.1134 | 0.0842 | 0.1418 | 0.134 | 0.3061 | 0.2381 | 0.206 | 0.2978 | 0.0465 | 0.7473 | 0.7334 | 0.2159 | 0.0824 | 0.4366 | 0.2262 | 0.294 | 0.3739 | 0.346 | 0.3132 | 0.2096 | 0.6818 | 0.3797 | 0.4277 | 0.3418
Load_TR9_F6_5 | customer | 0.2316 | 0.056 | 0.1677 | 0.1198 | 0.056 | 0.1518 | 0.1358 | 0.056 | 0.1677 | 0.1198 | 0.056 | 0.064 | 0.2236 | 0.056 | 0.056 | 0.1198 | 0.1677 | 0.056 | 0.4553 | 0.5333 | 0.3067 | 0.4007 | 0.2209 | 0.4955 | 0.4875 | 0.236 | 0.2565 | 0.3141 | 0.083 | 0.2411 | 0.0743 | 0.226 | 0.5896 | 0.6778 | 2.1056 | 3.097 | 2.6224 | 0.3382 | 0.1717 | 0.2164 | 1.0067 | 3.0857 | 2.4753 | 0.4186 | 0.4417 | 0.1706 | 0.056 | 0.056
Load_TR9_F6_50 | customer | 0.2139 | 0.4593 | 0.055 | 0.1638 | 0.055 | 0.055 | 0.125 | 0.0939 | 0.055 | 0.1638 | 0.055 | 0.1405 | 0.0783 | 0.055 | 0.055 | 0.1638 | 0.055 | 0.125 | 0.2254 | 0.055 | 0.1016 | 0.1172 | 0.055 | 0.2076 | 0.1865 | 0.1966 | 1.4683 | 0.7609 | 0.2884 | 0.0939 | 0.055 | 0.2882 | 0.4327 | 0.3842 | 0.4059 | 0.2594 | 0.5426 | 0.2689 | 0.2141 | 0.5307 | 0.9763 | 0.914 | 0.7853 | 0.7762 | 0.7911 | 0.6871 | 0.0628 | 0.156
Load_TR9_F6_51 | customer | 0.488 | 0.3739 | 0.2088 | 0.054 | 0.133 | 0.2088 | 0.1286 | 0.1639 | 0.1603 | 0.0759 | 0.2088 | 0.133 | 0.1384 | 0.1244 | 0.054 | 0.0962 | 0.2455 | 0.054 | 0.257 | 0.0847 | 0.054 | 0.2666 | 0.0751 | 0.163 | 0.1787 | 0.3201 | 0.2447 | 0.0759 | 0.1314 | 0.1489 | 0.1233 | 0.1786 | 0.22 | 0.1155 | 0.4894 | 0.3115 | 0.0856 | 0.1883 | 0.1959 | 0.0821 | 0.287 | 0.4311 | 0.112 | 0.1594 | 0.1736 | 0.0715 | 0.2421 | 0.0821
Load_TR9_F6_52 | customer | 0.3117 | 0.2526 | 0.055 | 0.055 | 0.2256 | 0.0819 | 0.0909 | 0.2167 | 0.055 | 0.2821 | 0.1089 | 0.055 | 0.2526 | 0.055 | 0.107 | 0.2223 | 0.6001 | 0.2823 | 0.2796 | 1.4458 | 0.2121 | 0.4856 | 0.3697 | 0.5585 | 0.2509 | 0.354 | 0.9902 | 1.3454 | 1.4232 | 0.1392 | 0.255 | 0.1089 | 0.0999 | 0.2077 | 0.055 | 0.3812 | 1.0898 | 0.0825 | 0.1539 | 0.4463 | 0.7194 | 0.7874 | 0.7894 | 0.8739 | 0.568 | 0.9417 | 0.6071 | 0.1179
Load_TR9_F6_53 | customer | 0.096 | 0.2337 | 0.033 | 0.1738 | 0.1436 | 0.1413 | 0.0778 | 0.1011 | 0.2286 | 0.033 | 0.1144 | 0.2153 | 0.033 | 0.1738 | 0.0541 | 0.2451 | 0.3517 | 0.928 | 0.033 | 0.2967 | 0.057 | 0.2646 | 0.1221 | 0.092 | 0.2968 | 0.1031 | 0.1234 | 0.1731 | 0.1605 | 0.129 | 0.1454 | 0.0966 | 0.4575 | 0.2244 | 0.36 | 0.3599 | 0.6117 | 1.0944 | 0.3033 | 0.5384 | 0.2263 | 0.0586 | 0.1482 | 0.033 | 0.1559 | 0.1674 | 0.0394 | 0.2071
Load_TR9_F6_54 | prosumer | 0.1868 | 0.183 | 0.05 | 0.2945 | 0.5435 | 0.152 | 0.2099 | 0.0781 | 0.1868 | 0.1344 | 0.1054 | 0.0681 | 0.2568 | 0.0574 | 0.094 | 0.2273 | 0.05 | 0.18 | 0.1993 | 0.098 | 0.1669 | 0.1063 | 0.05 | 0.2048 | 0.1165 | 0.1696 | 0.1406 | 1.3927 | 0.2237 | 0.182 | 0.4429 | 0.0732 | 0.2453 | 1.2111 | 0.3538 | 0.2055 | 0.2369 | 0.2057 | 0.1162 | 0.5075 | 0.3718 | 0.3054 | 0.5209 | 0.561 | 0.7387 | 0.0574 | 0.2079 | 0.1133
Load_TR9_F6_55 | prosumer | 0.2103 | 0.1774 | 0.2108 | 0.1261 | 0.2925 | 0.1164 | 0.0685 | 0.3653 | 0.06 | 0.1867 | 0.2056 | 0.1186 | 0.2575 | 0.1094 | 0.1104 | 0.1932 | 0.1243 | 0.1867 | 0.1422 | 0.2831 | 0.1261 | 0.13 | 0.2953 | 0.0708 | 0.2221 | 0.2032 | 2.087 | 0.4736 | 0.1371 | 0.195 | 0.1591 | 0.4045 | 0.5915 | 0.206 | 0.4661 | 0.1915 | 0.1739 | 0.2349 | 0.1261 | 0.1649 | 0.22 | 0.0924 | 0.2318 | 0.1935 | 0.0761 | 0.2818 | 0.1416 | 0.2441
Load_TR9_F6_56 | customer | 0.3816 | 0.725 | 0.6283 | 0.1576 | 0.1284 | 0.3015 | 0.0735 | 0.2469 | 0.2035 | 0.2087 | 0.0912 | 0.3218 | 0.1286 | 0.1898 | 0.1485 | 0.2168 | 0.1627 | 0.1512 | 0.261 | 0.1622 | 0.1826 | 0.2808 | 0.306 | 0.2001 | 0.053 | 0.392 | 0.0585 | 0.114 | 0.2338 | 0.1839 | 0.2023 | 0.1212 | 0.3292 | 0.0694 | 0.2815 | 0.1689 | 0.053 | 0.2789 | 0.1715 | 0.1077 | 0.2718 | 0.1239 | 0.4095 | 0.7198 | 0.7026 | 0.7129 | 0.2011 | 0.1994
Load_TR9_F6_57 | prosumer | 0.5848 | 0.6175 | 0.0481 | 0.1145 | 0.044 | 0.1186 | 0.044 | 0.1186 | 0.044 | 0.0937 | 0.0689 | 0.0937 | 0.0689 | 0.044 | 0.1186 | 0.044 | 0.1186 | 0.044 | 0.1186 | 0.044 | 0.044 | 0.1166 | 0.0891 | 0.045 | 0.054 | 0.1288 | 0.0564 | 0.0678 | 0.1767 | 0.044 | 0.1186 | 0.044 | 0.277 | 0.095 | 0.087 | 0.7807 | 0.7965 | 0.7302 | 0.3783 | 0.1873 | 0.3354 | 0.2381 | 0.1817 | 0.3686 | 0.2979 | 0.2712 | 0.3179 | 0.044
Load_TR9_F6_58 | prosumer | 0.3164 | 0.1479 | 0.046 | 0.1275 | 0.2323 | 0.046 | 0.129 | 0.2309 | 0.046 | 0.1986 | 0.1631 | 0.1371 | 0.1667 | 0.046 | 0.1479 | 0.129 | 0.2207 | 0.0639 | 0.168 | 0.595 | 0.6125 | 0.4441 | 0.4577 | 0.6638 | 0.1693 | 0.2236 | 0.139 | 0.2226 | 0.1731 | 0.0712 | 0.4136 | 0.1918 | 0.3458 | 0.4727 | 0.1512 | 0.296 | 0.2229 | 0.1699 | 0.5608 | 0.3071 | 0.3958 | 0.4561 | 0.4361 | 0.3612 | 0.6015 | 0.4034 | 0.2204 | 0.4602
Load_TR9_F6_59 | prosumer | 0.0605 | 0.1848 | 0.1348 | 0.1615 | 0.1491 | 0.2267 | 0.0693 | 0.2086 | 0.0428 | 0.1047 | 0.1074 | 0.426 | 0.0704 | 0.1956 | 1.0388 | 1.6863 | 1.432 | 0.1645 | 0.2344 | 0.0389 | 0.2629 | 0.1129 | 0.034 | 0.1645 | 0.1981 | 0.1383 | 0.1835 | 0.2346 | 0.1655 | 0.1942 | 0.187 | 0.1526 | 0.2295 | 0.0611 | 0.3527 | 0.13 | 0.1454 | 0.1831 | 0.1771 | 0.1467 | 0.1496 | 0.1019 | 0.2299 | 0.078 | 0.2923 | 0.4951 | 0.0914 | 0.0518
Load_TR9_F6_6 | prosumer | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.1076 | 0.052 | 0.052 | 0.1653 | 0.1311 | 0.096 | 0.052 | 0.052 | 0.052 | 0.064 | 0.1397 | 0.1592 | 0.054 | 0.4435 | 0.0547 | 0.062 | 0.099 | 0.1939 | 0.2703 | 0.1484 | 0.0915 | 0.2688 | 0.123 | 0.1105 | 0.2194 | 0.4573 | 0.604 | 0.4751 | 0.6807 | 0.8292 | 0.8359 | 0.618 | 0.4633 | 0.4774
Load_TR9_F6_60 | prosumer | 0.2064 | 0.1245 | 0.1582 | 0.1418 | 0.134 | 0.1737 | 0.109 | 0.2411 | 0.0897 | 0.1005 | 0.2304 | 0.055 | 0.055 | 0.055 | 0.2759 | 0.055 | 0.158 | 0.1728 | 0.1245 | 0.0756 | 0.2398 | 0.0704 | 0.2406 | 0.0902 | 0.109 | 0.1737 | 0.1032 | 0.1245 | 0.2064 | 0.055 | 0.1245 | 0.2064 | 0.055 | 0.207 | 0.1238 | 0.055 | 0.0589 | 0.1757 | 0.6901 | 0.4409 | 0.903 | 0.3902 | 0.5311 | 0.5967 | 0.4265 | 1.099 | 0.4718 | 0.7836
Load_TR9_F6_61 | prosumer | 0.2522 | 0.057 | 0.2256 | 0.0836 | 0.128 | 0.1812 | 0.0747 | 0.2344 | 0.057 | 0.2522 | 0.057 | 0.057 | 0.1901 | 1.2204 | 0.2301 | 0.1812 | 0.108 | 0.5179 | 0.1754 | 0.1589 | 0.0699 | 1.0475 | 0.8288 | 1.9315 | 0.4225 | 0.5142 | 0.1377 | 0.1635 | 0.1457 | 0.057 | 0.2256 | 0.0836 | 0.057 | 0.2078 | 0.2264 | 0.1942 | 0.4163 | 0.6415 | 0.3353 | 0.3832 | 0.3797 | 0.6907 | 0.4104 | 0.992 | 0.5511 | 0.818 | 0.6639 | 0.3058
Load_TR9_F6_62 | prosumer | 0.4125 | 0.2274 | 0.1744 | 0.1064 | 0.046 | 0.0899 | 0.1909 | 0.1031 | 0.0789 | 0.1448 | 0.125 | 0.046 | 0.204 | 0.0891 | 0.3897 | 0.3172 | 0.2034 | 0.1677 | 0.1963 | 0.1327 | 0.234 | 0.1334 | 0.2151 | 0.2682 | 0.1689 | 0.0508 | 0.1984 | 0.1915 | 0.4919 | 0.2434 | 0.1401 | 0.1946 | 0.0796 | 0.1354 | 0.125 | 0.3816 | 0.1186 | 0.1534 | 0.2668 | 0.2348 | 0.046 | 0.3142 | 0.1584 | 1.4963 | 0.5534 | 0.5384 | 0.3942 | 0.3171
Load_TR9_F6_63 | prosumer | 0.1087 | 0.0422 | 0.038 | 0.0838 | 0.0671 | 0.0754 | 0.0754 | 0.1004 | 0.0505 | 0.038 | 0.038 | 0.1129 | 0.038 | 0.1129 | 0.038 | 0.0879 | 0.063 | 0.038 | 0.0557 | 0.1102 | 0.0742 | 0.0706 | 0.13 | 0.2293 | 0.0754 | 0.3079 | 0.1701 | 0.126 | 0.1098 | 0.1164 | 0.0936 | 0.3741 | 0.2002 | 0.0754 | 0.1314 | 0.2829 | 0.4021 | 0.1808 | 0.4285 | 0.4053 | 0.3475 | 0.4972 | 0.453 | 0.2541 | 0.3054 | 0.1832 | 0.038 | 0.1129
Load_TR9_F6_64 | prosumer | 0.1046 | 0.2857 | 0.04 | 0.2733 | 0.1171 | 0.0717 | 0.2121 | 0.04 | 0.1323 | 0.1567 | 0.1585 | 0.119 | 0.2543 | 0.04 | 0.1213 | 0.2772 | 0.0463 | 0.2559 | 0.1394 | 0.1518 | 0.2918 | 0.1244 | 0.1667 | 0.1466 | 0.1678 | 0.1617 | 0.1009 | 0.2618 | 1.0548 | 0.1423 | 0.0644 | 0.3046 | 0.1162 | 0.1673 | 0.4754 | 0.3241 | 0.3022 | 0.5075 | 0.5436 | 0.4542 | 0.3911 | 0.391 | 0.4993 | 0.3277 | 0.2324 | 0.097 | 0.2236 | 0.1604
Load_TR9_F6_65 | prosumer | 0.1112 | 0.2475 | 0.052 | 0.0601 | 0.2225 | 0.052 | 0.1281 | 0.2306 | 0.1281 | 0.052 | 0.3067 | 0.052 | 0.1222 | 0.429 | 0.2712 | 0.4781 | 0.0647 | 0.2811 | 0.3787 | 0.3255 | 0.9973 | 0.4552 | 0.3125 | 0.052 | 0.3067 | 0.052 | 0.052 | 0.2856 | 0.0731 | 0.1819 | 0.1557 | 0.1543 | 0.1494 | 0.1154 | 0.2189 | 0.0764 | 0.1525 | 0.2062 | 0.1027 | 0.0774 | 0.0816 | 0.1148 | 0.2566 | 0.0858 | 0.2563 | 0.1024 | 0.052 | 0.2306
Load_TR9_F6_66 | customer | 0.1175 | 0.038 | 0.0512 | 0.1042 | 0.0645 | 0.091 | 0.038 | 0.038 | 0.038 | 0.1175 | 0.038 | 0.038 | 0.038 | 0.0822 | 0.0733 | 0.038 | 0.0645 | 0.091 | 0.0866 | 0.254 | 0.038 | 0.0866 | 0.0689 | 0.0733 | 0.0951 | 0.5115 | 1.0136 | 0.1834 | 1.9113 | 0.1043 | 0.038 | 0.091 | 0.0645 | 0.091 | 0.0645 | 0.038 | 0.1175 | 0.038 | 0.038 | 0.038 | 0.0601 | 0.0954 | 0.0733 | 0.0822 | 0.038 | 0.038 | 0.1175 | 1.6446
Load_TR9_F6_67 | prosumer | 0.4282 | 0.052 | 0.2065 | 0.052 | 0.1363 | 0.1222 | 0.052 | 0.052 | 0.052 | 0.052 | 0.2065 | 0.052 | 0.1995 | 0.059 | 0.052 | 0.3768 | 0.2139 | 1.1197 | 0.33 | 0.5507 | 0.5541 | 2.3993 | 0.5936 | 0.2742 | 0.2107 | 0.1686 | 0.1686 | 0.2487 | 0.052 | 0.2065 | 0.052 | 0.1292 | 0.1292 | 0.052 | 0.052 | 0.2065 | 0.0909 | 0.2528 | 0.2765 | 0.3891 | 0.2978 | 0.2763 | 0.4751 | 0.6542 | 0.4993 | 0.6071 | 0.4991 | 0.301
Load_TR9_F6_68 | customer | 0.3506 | 0.1022 | 0.033 | 0.1022 | 0.033 | 0.1022 | 0.033 | 0.1022 | 0.0484 | 0.0869 | 0.033 | 0.0907 | 0.0445 | 0.0753 | 0.0916 | 0.033 | 0.033 | 0.1093 | 0.0895 | 0.2902 | 0.0638 | 0.0523 | 0.0998 | 0.042 | 0.033 | 1.0814 | 0.4512 | 0.4879 | 0.3152 | 0.7303 | 0.9879 | 0.0999 | 0.1194 | 0.1932 | 0.1955 | 0.2254 | 0.1514 | 0.0864 | 0.1688 | 1.1556 | 0.422 | 0.405 | 0.4993 | 0.3265 | 0.2503 | 0.4095 | 0.425 | 0.6097
Load_TR9_F6_69 | customer | 0.4521 | 0.0657 | 0.1349 | 0.1503 | 0.0811 | 0.2041 | 0.058 | 0.2271 | 0.058 | 0.2118 | 0.0734 | 0.0734 | 0.2118 | 0.0964 | 0.3593 | 0.0735 | 0.0999 | 0.2365 | 0.2891 | 1.3897 | 0.1195 | 0.1656 | 0.0991 | 0.3088 | 0.1733 | 0.3478 | 0.181 | 0.1649 | 0.309 | 0.5353 | 0.2508 | 0.4174 | 0.2753 | 0.4674 | 0.4167 | 0.4939 | 0.2983 | 0.386 | 0.2995 | 0.3395 | 0.7573 | 0.8218 | 0.8418 | 0.822 | 0.7299 | 0.7708 | 0.9203 | 0.7834
Load_TR9_F6_7 | customer | 0.1759 | 0.1514 | 0.1122 | 0.19 | 0.1014 | 0.4124 | 0.439 | 0.2316 | 0.1227 | 0.2078 | 0.1132 | 0.0886 | 0.1012 | 0.1232 | 0.2292 | 0.1014 | 0.0347 | 0.093 | 0.1638 | 0.1886 | 0.145 | 0.0448 | 0.072 | 0.1426 | 0.2355 | 0.0756 | 0.0783 | 0.3884 | 0.1883 | 0.3382 | 0.1678 | 0.1772 | 0.1591 | 0.9888 | 0.6385 | 0.1951 | 0.1801 | 0.5166 | 0.041 | 0.4191 | 0.601 | 0.9414 | 1.5353 | 0.7815 | 1.5056 | 0.7617 | 0.9799 | 0.6753
Load_TR9_F6_70 | prosumer | 0.0797 | 0.1836 | 0.05 | 0.1316 | 0.1316 | 0.05 | 0.191 | 0.0723 | 0.05 | 0.1762 | 0.0871 | 0.05 | 0.1984 | 0.0648 | 0.1019 | 0.3767 | 0.2402 | 0.2894 | 0.2152 | 0.3127 | 0.2377 | 0.1101 | 0.515 | 0.2365 | 0.4019 | 0.2194 | 0.0554 | 0.1613 | 0.1046 | 0.0816 | 0.2756 | 0.0829 | 1.3722 | 2.7713 | 1.3607 | 1.5951 | 0.1459 | 0.2697 | 0.0527 | 0.2357 | 0.5016 | 0.4883 | 0.7732 | 0.2805 | 0.3149 | 0.2166 | 0.3907 | 0.3026
Load_TR9_F6_71 | prosumer | 0.4091 | 0.054 | 0.3727 | 0.054 | 0.054 | 0.2726 | 0.154 | 0.054 | 0.2894 | 0.1373 | 0.228 | 0.1986 | 0.054 | 0.3727 | 0.054 | 0.1995 | 0.2271 | 1.0987 | 0.3739 | 0.4022 | 0.5245 | 1.1093 | 0.31 | 0.0958 | 0.2484 | 1.0395 | 0.287 | 1.5477 | 0.3406 | 0.3245 | 0.3464 | 0.4228 | 0.5138 | 0.2921 | 0.2006 | 0.2342 | 0.1925 | 0.054 | 0.1887 | 0.238 | 0.166 | 0.0913 | 0.2233 | 0.217 | 0.8815 | 1.2473 | 0.8886 | 0.3052
Load_TR9_F6_72 | customer | 0.1411 | 0.1127 | 0.049 | 0.2048 | 0.049 | 0.1552 | 0.0986 | 0.049 | 0.134 | 0.1198 | 0.049 | 0.1411 | 0.1127 | 0.049 | 0.049 | 0.1623 | 0.0915 | 0.1198 | 0.1789 | 0.0893 | 0.2151 | 0.049 | 0.0561 | 0.1977 | 0.049 | 0.049 | 0.2048 | 0.0771 | 0.0825 | 0.2363 | 0.3069 | 0.4358 | 0.3893 | 0.4434 | 0.3434 | 0.4712 | 0.3397 | 0.049 | 0.2361 | 0.3762 | 0.6136 | 0.8487 | 0.7925 | 0.7317 | 1.5212 | 1.5655 | 3.1981 | 0.4896
Load_TR9_F6_73 | prosumer | 0.2678 | 0.3914 | 0.051 | 0.3163 | 0.051 | 0.1862 | 0.0723 | 0.0665 | 0.3008 | 0.051 | 0.051 | 0.3256 | 0.3054 | 0.2209 | 0.2111 | 0.3245 | 0.0733 | 0.3021 | 0.2656 | 0.141 | 0.2342 | 0.2657 | 0.3163 | 0.051 | 0.2803 | 0.5517 | 0.0769 | 0.2594 | 0.1304 | 0.1923 | 0.2669 | 0.1112 | 0.1359 | 0.2234 | 0.1004 | 0.2142 | 0.1861 | 0.1714 | 0.3207 | 0.2519 | 0.207 | 0.1928 | 0.454 | 0.1832 | 0.53 | 0.3986 | 0.2399 | 0.3818
Load_TR9_F6_74 | customer | 0.1185 | 0.1476 | 0.053 | 0.1476 | 0.1185 | 0.053 | 0.1185 | 0.1476 | 0.053 | 0.0748 | 0.1913 | 0.053 | 0.0748 | 0.1913 | 0.053 | 0.053 | 0.1622 | 0.1039 | 0.1112 | 0.1549 | 0.053 | 0.2131 | 0.053 | 0.2131 | 0.053 | 0.053 | 0.0748 | 0.1913 | 0.053 | 0.053 | 0.1986 | 0.0676 | 0.0849 | 0.3187 | 0.062 | 0.0821 | 0.2094 | 0.053 | 0.1738 | 0.6803 | 0.5511 | 0.5187 | 0.5699 | 0.3771 | 0.3351 | 0.053 | 0.1622 | 0.1039
Load_TR9_F6_75 | customer | 0.0722 | 0.3103 | 0.149 | 0.3805 | 0.1548 | 0.1048 | 0.451 | 0.1008 | 0.2771 | 0.2787 | 0.1349 | 0.3066 | 0.2299 | 0.124 | 0.2147 | 0.1543 | 0.0855 | 0.1469 | 0.2037 | 0.2985 | 0.2234 | 0.0915 | 0.3516 | 0.2824 | 0.1652 | 0.3472 | 1.2067 | 1.2153 | 0.5923 | 0.7285 | 0.683 | 0.3821 | 0.3044 | 0.5012 | 0.5124 | 0.1775 | 0.4849 | 0.6302 | 0.2076 | 0.3951 | 0.4691 | 0.7458 | 0.6979 | 0.3725 | 0.5737 | 0.098 | 0.3068 | 0.2232
Load_TR9_F6_76 | prosumer | 0.6958 | 0.3216 | 0.3174 | 0.1072 | 0.2296 | 0.2271 | 0.0633 | 0.2719 | 0.1887 | 0.0925 | 0.3057 | 0.1583 | 0.1901 | 0.1715 | 0.151 | 0.087 | 0.282 | 0.1711 | 0.3692 | 1.8138 | 0.4561 | 0.6232 | 0.8778 | 2.7397 | 2.6742 | 0.3291 | 0.2424 | 0.1686 | 0.1218 | 0.1321 | 0.1583 | 0.235 | 0.1861 | 0.173 | 0.3201 | 0.056 | 0.3992 | 0.2548 | 0.271 | 3.0238 | 3.0947 | 1.8008 | 1.7814 | 1.675 | 1.1614 | 1.1428 | 0.056 | 0.0856
Load_TR9_F6_77 | prosumer | 0.1834 | 0.2127 | 0.1942 | 0.1688 | 0.1733 | 0.192 | 0.2386 | 0.038 | 0.3175 | 0.1132 | 0.1544 | 0.2011 | 0.1132 | 0.1938 | 0.2294 | 0.0455 | 0.3325 | 0.0982 | 0.5805 | 0.2137 | 0.2628 | 0.0749 | 0.3715 | 0.0867 | 0.5413 | 0.1508 | 0.8751 | 0.4716 | 0.9902 | 0.1904 | 0.2688 | 0.1739 | 0.2663 | 0.2989 | 0.3601 | 0.9065 | 0.3491 | 0.3689 | 0.4308 | 0.5181 | 0.6978 | 0.6861 | 0.86 | 0.4694 | 0.1433 | 0.211 | 0.0909 | 0.1197
Load_TR9_F6_78 | customer | 0.044 | 0.044 | 0.1099 | 0.044 | 0.044 | 0.088 | 0.5282 | 0.2605 | 0.1063 | 0.044 | 0.088 | 0.066 | 0.1026 | 0.0513 | 0.044 | 0.044 | 0.0623 | 0.0916 | 0.044 | 0.044 | 0.3454 | 0.5769 | 2.6089 | 2.7093 | 0.6635 | 0.1753 | 0.1466 | 0.0607 | 0.044 | 0.0806 | 0.0733 | 0.0513 | 0.1026 | 0.044 | 0.1099 | 0.044 | 0.088 | 0.066 | 0.044 | 0.0513 | 0.1026 | 0.0513 | 0.1026 | 0.1283 | 0.044 | 0.044 | 0.1268 | 0.2645
Load_TR9_F6_79 | prosumer | 0.8376 | 0.8018 | 0.7576 | 0.553 | 0.3423 | 0.2725 | 0.1288 | 0.2082 | 0.0863 | 0.095 | 0.2593 | 0.056 | 0.1724 | 0.1819 | 0.076 | 0.971 | 0.1086 | 0.3083 | 0.056 | 0.1083 | 0.246 | 0.056 | 0.2609 | 0.0933 | 0.1158 | 0.1606 | 0.0839 | 1.6366 | 0.1273 | 0.2227 | 0.1316 | 0.1429 | 0.2114 | 0.069 | 0.121 | 0.181 | 1.1003 | 0.5638 | 0.4461 | 0.1093 | 0.1884 | 0.4546 | 0.4991 | 0.3911 | 0.5539 | 0.8141 | 0.612 | 0.718
Load_TR9_F6_8 | prosumer | 0.1217 | 0.0836 | 0.3321 | 0.049 | 0.2135 | 0.075 | 0.049 | 0.3408 | 0.075 | 0.049 | 0.1763 | 0.0669 | 0.0721 | 0.5892 | 0.049 | 0.2221 | 0.1936 | 0.049 | 0.3667 | 0.049 | 0.0763 | 0.149 | 0.2394 | 0.0672 | 0.2966 | 0.1009 | 0.1799 | 0.3281 | 0.0537 | 0.5273 | 0.6617 | 0.5165 | 1.237 | 0.4894 | 0.1757 | 0.3761 | 0.2265 | 0.1929 | 0.2199 | 1.3225 | 0.5626 | 0.4417 | 0.4003 | 0.8571 | 0.3669 | 0.2221 | 0.1936 | 0.1096
Load_TR9_F6_80 | prosumer | 0.207 | 0.0932 | 0.058 | 0.0844 | 0.1108 | 0.102 | 0.0932 | 0.058 | 0.1372 | 0.058 | 0.058 | 0.058 | 0.1064 | 0.0888 | 0.4081 | 0.3526 | 0.2187 | 0.4589 | 0.233 | 0.6357 | 1.2509 | 0.8798 | 2.15 | 1.4409 | 0.102 | 0.058 | 0.102 | 0.0932 | 0.1508 | 0.4158 | 0.3 | 0.5833 | 1.0208 | 0.1982 | 0.2414 | 0.1138 | 0.3618 | 1.3096 | 0.1351 | 0.4614 | 0.5523 | 0.2724 | 1.35 | 0.5052 | 0.5946 | 1.548 | 0.7613 | 1.1251
Load_TR9_F6_81 | customer | 0.5993 | 0.1015 | 0.056 | 0.056 | 0.0636 | 0.2153 | 0.056 | 0.2229 | 0.056 | 0.056 | 0.1698 | 0.1091 | 0.056 | 0.1926 | 0.0864 | 0.1093 | 0.2078 | 0.2563 | 1.4736 | 2.0163 | 1.0017 | 0.056 | 0.0939 | 0.185 | 0.056 | 0.0636 | 0.2153 | 0.056 | 0.056 | 0.2229 | 0.056 | 0.056 | 0.2571 | 0.1918 | 0.1838 | 0.3024 | 0.2053 | 0.3235 | 0.1766 | 0.6895 | 0.6729 | 0.6513 | 0.7243 | 0.5655 | 0.4277 | 0.398 | 0.703 | 0.7202
Load_TR9_F6_82 | prosumer | 0.03 | 0.1591 | 0.03 | 0.118 | 0.0711 | 0.03 | 0.1591 | 0.03 | 0.1356 | 0.0535 | 0.03 | 0.1474 | 0.0417 | 0.03 | 0.03 | 0.0535 | 0.1356 | 0.03 | 0.1591 | 0.0343 | 0.0652 | 0.1239 | 0.03 | 0.0593 | 0.1298 | 0.03 | 0.0887 | 0.1004 | 0.03 | 0.03 | 0.1591 | 0.03 | 0.03 | 0.1844 | 0.3631 | 0.0763 | 0.1472 | 0.1291 | 0.0963 | 0.5955 | 0.4332 | 0.5274 | 0.5753 | 0.4407 | 0.1591 | 0.03 | 0.1591 | 0.03
Load_TR9_F6_83 | prosumer | 0.0665 | 0.2058 | 0.051 | 0.1594 | 0.1129 | 0.051 | 0.2213 | 0.051 | 0.1516 | 0.1207 | 0.051 | 0.1826 | 0.0897 | 0.051 | 0.1207 | 0.1516 | 0.051 | 0.0897 | 0.1826 | 0.051 | 0.4136 | 0.051 | 0.2422 | 0.3702 | 0.1424 | 0.281 | 1.4221 | 0.051 | 0.051 | 0.2213 | 0.051 | 0.1594 | 0.1129 | 0.051 | 0.3015 | 0.1609 | 0.2643 | 0.3049 | 0.7426 | 1.0427 | 0.9848 | 0.457 | 0.5583 | 0.6197 | 0.9467 | 0.7198 | 0.5616 | 0.405
Load_TR9_F6_9 | prosumer | 0.1401 | 0.2123 | 0.0781 | 0.1955 | 0.1714 | 0.1022 | 0.1932 | 0.1593 | 0.1263 | 0.2261 | 0.0926 | 0.224 | 0.0898 | 0.0627 | 0.9496 | 0.1998 | 0.0926 | 0.138 | 0.2378 | 0.1209 | 0.2473 | 0.1239 | 0.993 | 0.7035 | 0.2721 | 0.3141 | 0.4246 | 0.0742 | 0.2203 | 0.054 | 0.191 | 0.1615 | 0.1408 | 0.054 | 0.1615 | 0.191 | 0.054 | 0.054 | 0.0781 | 0.1167 | 0.0755 | 0.2769 | 0.054 | 0.2984 | 0.054 | 0.1901 | 0.1623 | 0.1041

## 5. Raw batt charge
Raw batt charge
Verbatim copy of Charge_kW (TR9_analysis_data.xlsx). One row per half-hour, one column per battery (kW).
period | hour | BES_TR9_two267_C | BES_TR9_two275_C | BES_TR9_two292_B | BES_TR9_two306_A | BES_TR9_two308_A | BES_TR9_two312_C | BES_TR9_two313_C | BES_TR9_two315_A | BES_TR9_two316_A | BES_TR9_two339_A | BES_TR9_two225_C | BES_TR9_two233_A | BES_TR9_five147_C | BES_TR9_five149_A | BES_TR9_five160_C | BES_TR9_five170_A | BES_TR9_five177_A | BES_TR9_five220_C | BES_TR9_five67_C | BES_TR9_five284_C | BES_TR9_five345_A | BES_TR9_five355_A | BES_TR9_five78_A | BES_TR9_five394_C | BES_TR9_five445_C | BES_TR9_five499_B | BES_TR9_five92_A | BES_TR9_five520_C | BES_TR9_five545_B | BES_TR9_five588_A | BES_TR9_five670_C | BES_TR9_five685_B | BES_TR9_five704_A | BES_TR9_five719_A | BES_TR9_five748_B | BES_TR9_five117_B | BES_TR9_five778_B | BES_TR9_five799_C | BES_TR9_five801_C | BES_TR9_five881_C | BES_TR9_five123_B | BES_TR9_six186_A | BES_TR9_six191_B | BES_TR9_six203_A | BES_TR9_six232_C | BES_TR9_six238_A | BES_TR9_six249_B | BES_TR9_six269_C | BES_TR9_six289_C | BES_TR9_six326_A | BES_TR9_six349_A | BES_TR9_six362_C | BES_TR9_six365_C | BES_TR9_six385_B | BES_TR9_six387_A | BES_TR9_six431_C | BES_TR9_six441_A | BES_TR9_six501_A | BES_TR9_six512_B | BES_TR9_six82_A | BES_TR9_six523_C | BES_TR9_six534_B | BES_TR9_six583_A | BES_TR9_six625_A | BES_TR9_six646_B | BES_TR9_six651_C | BES_TR9_six718_C | BES_TR9_six721_A | BES_TR9_six740_A | BES_TR9_six758_B | BES_TR9_six784_B | BES_TR9_six90_B | BES_TR9_six799_B | BES_TR9_six801_C | BES_TR9_six807_A | BES_TR9_six844_C | BES_TR9_six852_B | BES_TR9_six860_C | BES_TR9_six885_A | BES_TR9_six914_A | BES_TR9_six921_B | BES_TR9_six938_A | BES_TR9_six967_B | BES_TR9_six974_C | BES_TR9_six990_B | BES_TR9_six111_C | BES_TR9_six1006_C | BES_TR9_six1025_B | BES_TR9_six1064_C | BES_TR9_six128_B
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 0 | 0.001 | 0 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4.5 | 0.126 | 0.184 | 0.114 | 0.187 | 0 | 0 | 0.188 | 0.158 | 0.013 | 0 | 0.122 | 0.103 | 0.125 | 0.064 | 0.093 | 0.127 | 0 | 0.113 | 0.068 | 0.154 | 0.133 | 0.021 | 0.101 | 0.084 | 0 | 0.101 | 0 | 0.065 | 0 | 0.124 | 0.091 | 0 | 0 | 0 | 0 | 0.114 | 0.153 | 0.151 | 0 | 0.035 | 0 | 0.063 | 0.117 | 0 | 0.06 | 0.019 | 0.07 | 0 | 0 | 0.028 | 0 | 0.095 | 0.092 | 0.12 | 0 | 0 | 0 | 0.038 | 0 | 0.107 | 0.149 | 0.037 | 0.178 | 0 | 0.075 | 0.13 | 0.098 | 0.017 | 0 | 0 | 0.128 | 0.064 | 0.074 | 0 | 0.088 | 0.078 | 0.018 | 0.181 | 0.181 | 0 | 0.008 | 0.065 | 0 | 0 | 0.138 | 0.125 | 0.146 | 0.179 | 0.112 | 0.007
11 | 5 | 0.084 | 0.412 | 0.363 | 0.306 | 0.291 | 0.193 | 0.323 | 0.247 | 0.121 | 0 | 0.294 | 0.319 | 0.297 | 0.062 | 0.294 | 0.413 | 0.116 | 0.194 | 0.105 | 0.354 | 0.348 | 0.237 | 0.248 | 0.214 | 0.21 | 0.415 | 0.393 | 0.413 | 0.086 | 0.415 | 0.171 | 0.224 | 0.277 | 0.046 | 0.163 | 0.126 | 0.273 | 0.243 | 0.354 | 0.299 | 0.142 | 0.178 | 0.222 | 0.252 | 0.292 | 0.14 | 0.309 | 0.131 | 0.085 | 0.395 | 0.236 | 0.146 | 0.235 | 0.203 | 0.067 | 0.171 | 0.029 | 0.407 | 0.288 | 0.321 | 0.107 | 0.099 | 0.406 | 0.306 | 0.384 | 0.212 | 0.356 | 0.198 | 0.104 | 0.068 | 0.354 | 0.179 | 0.116 | 0.174 | 0.336 | 0.193 | 0.187 | 0.155 | 0.255 | 0.201 | 0.06 | 0.18 | 0 | 0.019 | 0.202 | 0.17 | 0.346 | 0.431 | 0.41 | 0.369
12 | 5.5 | 0.196 | 0.693 | 0.61 | 0.696 | 0.7 | 0.503 | 0.697 | 0.4 | 0.589 | 0.226 | 0.504 | 0.549 | 0.491 | 0.219 | 0.256 | 0.605 | 0.113 | 0.416 | 0.323 | 0.599 | 0.422 | 0 | 0.623 | 0.174 | 0.534 | 0.538 | 0.486 | 0.628 | 0.318 | 0.696 | 0.41 | 0.406 | 0.548 | 0.058 | 0.189 | 0.45 | 0.593 | 0.596 | 0.445 | 0.61 | 0.496 | 0.316 | 0.59 | 0.428 | 0.458 | 0.177 | 0.519 | 0.129 | 0.414 | 0.619 | 0.336 | 0.199 | 0.411 | 0.502 | 0.126 | 0.242 | 0.168 | 0.486 | 0.447 | 0.561 | 0.589 | 0.075 | 0.687 | 0.624 | 0.698 | 0.382 | 0.674 | 0.531 | 0.184 | 0.234 | 0.316 | 0.319 | 0.501 | 0.314 | 0.696 | 0.258 | 0.437 | 0.69 | 0.69 | 0.414 | 0.265 | 0.045 | 0.12 | 0.077 | 0.686 | 0.489 | 0.591 | 0.594 | 0.559 | 0.518
13 | 6 | 0.57 | 0.999 | 0.938 | 0.817 | 0.866 | 0.739 | 0.947 | 0.871 | 0.565 | 0.466 | 0.734 | 0.88 | 0.719 | 0.472 | 0.734 | 0.938 | 0.262 | 0.771 | 0.463 | 0.867 | 0.804 | 0 | 0.908 | 0.593 | 0.891 | 1.002 | 1.002 | 0.946 | 0.402 | 0.849 | 0.569 | 0.481 | 0.896 | 0.271 | 0.469 | 0.542 | 0.951 | 0.818 | 0.867 | 0.82 | 0.451 | 0.396 | 0.858 | 0.455 | 0.923 | 0.483 | 0.668 | 0.311 | 0.443 | 0.89 | 0.427 | 0.605 | 0.602 | 0.662 | 0.407 | 0.549 | 0.31 | 0.956 | 0.569 | 0.894 | 0.661 | 0.343 | 0.993 | 0.795 | 0.857 | 0.734 | 0.791 | 0.659 | 0.324 | 0.357 | 0.977 | 0.472 | 0.731 | 0.334 | 0.844 | 0.486 | 0.532 | 0.926 | 0.848 | 0.457 | 0.601 | 0.219 | 0.203 | 0.28 | 0.876 | 0.714 | 0.811 | 1.006 | 0.958 | 0.958
14 | 6.5 | 0 | 1.309 | 1.304 | 1.312 | 1.101 | 1.034 | 1.275 | 0.939 | 1.021 | 0.546 | 0.966 | 1.311 | 0.951 | 0.534 | 0.816 | 1.282 | 0.299 | 0.942 | 0.566 | 1.138 | 1.132 | 0.376 | 1.191 | 0.712 | 1.304 | 1.168 | 1.245 | 1.31 | 0.092 | 1.312 | 0.763 | 0.751 | 1.145 | 0.409 | 0.439 | 0.923 | 1.233 | 1.074 | 1.068 | 1.309 | 0.958 | 0.499 | 0.979 | 0.813 | 1.214 | 0.436 | 0.981 | 0.37 | 0.698 | 1.136 | 0.797 | 0.691 | 0.796 | 0.945 | 0.515 | 0.799 | 0.344 | 1.304 | 0.96 | 1.308 | 1.088 | 0.282 | 1.173 | 1.156 | 1.314 | 0.859 | 1.3 | 1.079 | 0.465 | 0.633 | 1.162 | 0.627 | 0.963 | 0 | 1.269 | 0.566 | 0.978 | 0.929 | 1.299 | 0.784 | 0.476 | 0.458 | 0.338 | 0.315 | 1.176 | 0.429 | 1.099 | 1.328 | 1.307 | 1.295
15 | 7 | 0.956 | 1.56 | 1.524 | 1.49 | 1.393 | 1.4 | 1.621 | 1.301 | 1.189 | 0.551 | 1.197 | 1.581 | 0.975 | 0.663 | 0.863 | 1.443 | 0.525 | 1.34 | 0.746 | 1.354 | 1.245 | 1.147 | 1.56 | 0.912 | 1.366 | 1.606 | 1.454 | 1.57 | 0 | 1.527 | 0.987 | 0.821 | 1.361 | 0.326 | 0 | 1.073 | 1.367 | 1.405 | 1.324 | 1.042 | 0.961 | 0.693 | 1.399 | 0.998 | 1.407 | 0.792 | 1.131 | 0.449 | 0.967 | 1.524 | 0.914 | 0.991 | 0.988 | 1.195 | 0.587 | 0.78 | 0.437 | 1.429 | 0.998 | 0.536 | 1.414 | 0.575 | 1.383 | 1.479 | 1.602 | 1.105 | 1.572 | 1.347 | 0.506 | 0.685 | 0.627 | 0.725 | 0.974 | 0.603 | 1.276 | 0.795 | 1.128 | 1.395 | 1.614 | 0.939 | 0.987 | 0.622 | 0.474 | 0.395 | 1.59 | 1.2 | 1.05 | 1.636 | 1.545 | 0.716
16 | 7.5 | 0.059 | 0.587 | 1.408 | 1.525 | 1.717 | 1.365 | 1.07 | 1.578 | 0 | 0.755 | 1.372 | 1.687 | 1.414 | 0.931 | 1.429 | 1.912 | 0.521 | 1.614 | 0.9 | 1.624 | 1.601 | 1.395 | 1.761 | 1.075 | 1.842 | 1.904 | 1.871 | 1.112 | 0.785 | 1.403 | 1.117 | 1.141 | 1.74 | 0.557 | 0.012 | 1.261 | 1.501 | 1.567 | 1.673 | 0 | 1.375 | 0.786 | 1.526 | 1.019 | 1.742 | 0.869 | 1.334 | 0.629 | 0.946 | 1.49 | 1.092 | 1.153 | 1.181 | 1.427 | 0.844 | 1.184 | 0.648 | 1.863 | 1.431 | 1.69 | 1.574 | 0.602 | 1.792 | 1.674 | 1.252 | 1.351 | 1.747 | 1.535 | 0.696 | 0.858 | 0.288 | 0.935 | 1.426 | 0.806 | 1.657 | 0.899 | 1.204 | 1.497 | 1.598 | 0.857 | 1.035 | 0.663 | 0.654 | 0.695 | 1.004 | 1.259 | 1.375 | 0.926 | 0.542 | 1.775
17 | 8 | 1.153 | 0 | 0 | 0 | 1.823 | 0.069 | 0 | 1.321 | 1.521 | 1.059 | 0.739 | 0.928 | 0.786 | 0.943 | 1.494 | 1.041 | 0.744 | 1.304 | 1.076 | 0.149 | 1.415 | 1.346 | 0.192 | 1.217 | 1.139 | 0 | 0 | 0 | 0 | 0 | 1.109 | 1.255 | 1.03 | 0.002 | 0 | 1.258 | 0.37 | 0 | 0 | 0 | 1.56 | 0.973 | 0.659 | 1.372 | 1.871 | 0.967 | 1.36 | 0.681 | 1.365 | 0.695 | 1.255 | 1.288 | 1.362 | 1.527 | 0.996 | 0.332 | 0.675 | 1.17 | 1.488 | 1.396 | 1.001 | 0.701 | 0.203 | 1.604 | 0 | 1.462 | 0.809 | 1.704 | 0.731 | 0.911 | 0.832 | 1.08 | 1.54 | 1.024 | 0.675 | 1.069 | 1.652 | 0.852 | 0.05 | 1.175 | 1.188 | 1.059 | 0.567 | 0.517 | 2.156 | 1.505 | 0.359 | 0 | 0 | 1.148
18 | 8.5 | 1.575 | 0 | 0 | 0 | 0 | 1.883 | 0 | 0 | 1.863 | 0.924 | 0 | 0 | 0 | 1.111 | 0.764 | 0 | 0.835 | 0 | 1.151 | 0 | 0 | 1.857 | 0 | 1.537 | 0 | 0 | 0 | 0 | 0.579 | 0 | 0.897 | 1.476 | 0 | 0.813 | 0 | 1.24 | 0 | 0 | 0 | 0 | 1.004 | 1.215 | 0 | 0.924 | 0 | 1.155 | 1.597 | 0.812 | 1.373 | 0 | 1.39 | 1.051 | 0.138 | 0.328 | 1.201 | 1.407 | 0.804 | 0 | 1.004 | 0 | 0 | 0.901 | 0 | 0 | 0 | 0.486 | 0 | 0 | 0.907 | 1.204 | 1.945 | 1.103 | 0.475 | 0.75 | 0 | 1.23 | 0.55 | 0 | 0 | 1.296 | 0.487 | 0.966 | 0.78 | 0.853 | 0.143 | 0.865 | 0 | 0 | 0 | 0
19 | 9 | 1.5 | 0 | 0 | 0 | 0 | 0.783 | 0 | 0 | 1.5 | 1.287 | 0 | 0 | 0 | 1.275 | 1.226 | 0 | 0.808 | 0 | 0.725 | 0 | 0 | 1.597 | 0 | 0.289 | 0 | 0 | 0 | 0 | 1.083 | 0 | 0 | 1.414 | 0 | 0.911 | 0.088 | 0 | 0 | 0 | 0 | 0 | 0 | 0.694 | 0 | 0 | 0 | 0 | 0 | 0.996 | 0.372 | 0 | 0.196 | 0 | 0 | 0 | 0.813 | 1.364 | 0.818 | 0 | 0 | 0.047 | 0 | 0.811 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92 | 1.216 | 0 | 0.298 | 0 | 1.209 | 0 | 0.421 | 0 | 0 | 0 | 0.231 | 1.356 | 1.119 | 0.669 | 0.458 | 0 | 0 | 0.041 | 0 | 0 | 0
20 | 9.5 | 1.255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.331 | 0 | 0 | 0 | 1.268 | 0 | 0 | 0.958 | 0 | 0 | 0 | 0 | 0.251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.116 | 0 | 0 | 0 | 0 | 1.065 | 1.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.017 | 0 | 0.923 | 0 | 0 | 0 | 0 | 0 | 0 | 1.403 | 0 | 0.915 | 0 | 0 | 0.085 | 0 | 0.834 | 0 | 0 | 0 | 0 | 0 | 0 | 1.068 | 0.676 | 0 | 0 | 0 | 1.324 | 0 | 0 | 0 | 0 | 0 | 0 | 0.716 | 1.342 | 0 | 0.899 | 0 | 0 | 0.256 | 0 | 0 | 0
21 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.156 | 0.464 | 0 | 0 | 0.426 | 0 | 0 | 1.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.369 | 0 | 0 | 0 | 0 | 0.584 | 1.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.027 | 0 | 0.882 | 0 | 0 | 0 | 0 | 0 | 0 | 1.009 | 0 | 0.778 | 0 | 0 | 0 | 0 | 1.006 | 0 | 0 | 0 | 0.958 | 0 | 0 | 1.134 | 0 | 0 | 0 | 0 | 0.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.438 | 0.721 | 0.915 | 0 | 0 | 0 | 0 | 0 | 0
22 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.523 | 0 | 0 | 0 | 0 | 1.005 | 1.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79 | 0 | 0 | 0 | 0 | 0.242 | 0 | 0 | 0 | 0 | 0 | 0 | 0.185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.608 | 1.156 | 0 | 0 | 0.694 | 0 | 0.32 | 0
23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.403 | 0 | 0 | 0 | 0 | 0.627 | 1.544 | 0 | 0 | 0.222 | 0.0003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.392 | 0.065 | 0 | 0 | 0 | 0 | 0 | 0
24 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.345 | 0 | 0 | 0 | 0 | 0 | 0
25 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.462 | 0.542 | 0.419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.171 | 0 | 0 | 0 | 0 | 0.169 | 0
26 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.366 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.953 | 0.069 | 0 | 0 | 0 | 0 | 1.05 | 0
27 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.615 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.009 | 0 | 0 | 0 | 0.039 | 0 | 0 | 0
28 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.218 | 0 | 0 | 0.574 | 0 | 0.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.036 | 0.065 | 0 | 0 | 0.468 | 0 | 0.324 | 0
29 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.028 | 0 | 0 | 0 | 0.466 | 0 | 0.14 | 0
30 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.947 | 0 | 0 | 0 | 0.498 | 0 | 0.578 | 0
31 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.846 | 0 | 0 | 0 | 0 | 0 | 0.494 | 0
32 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0.251 | 0 | 0 | 0 | 0 | 0 | 0.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.556 | 0 | 0 | 0 | 0 | 0 | 0.749 | 0
33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0.415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.562 | 0 | 0 | 0 | 0.459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 18 | 0 | 0 | 0 | 0 | 0.568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47 | 0 | 0.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.747 | 0 | 0 | 0 | 0.304 | 0 | 0 | 0 | 0.178 | 0 | 0.461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.307 | 0 | 0 | 0 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 18.5 | 0.272 | 0 | 0 | 0 | 0.051 | 0 | 0 | 0.124 | 0 | 0 | 0 | 0 | 0.147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.579 | 0.494 | 0 | 0 | 0 | 0.116 | 0 | 0 | 0 | 0 | 0 | 0.321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.312 | 0 | 0.11 | 0 | 0 | 0.061 | 0.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.125 | 0 | 0 | 0 | 0 | 0.067 | 0 | 0 | 0 | 0 | 0
39 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.239 | 0 | 0 | 0 | 0 | 0 | 0.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.264 | 0.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038 | 0 | 0 | 0.218 | 0.018 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0.187 | 0 | 0 | 0
40 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 6. Raw batt discharge
Raw batt discharge
Verbatim copy of Discharge_kW (TR9_analysis_data.xlsx). One row per half-hour, one column per battery (kW).
period | hour | BES_TR9_two267_C | BES_TR9_two275_C | BES_TR9_two292_B | BES_TR9_two306_A | BES_TR9_two308_A | BES_TR9_two312_C | BES_TR9_two313_C | BES_TR9_two315_A | BES_TR9_two316_A | BES_TR9_two339_A | BES_TR9_two225_C | BES_TR9_two233_A | BES_TR9_five147_C | BES_TR9_five149_A | BES_TR9_five160_C | BES_TR9_five170_A | BES_TR9_five177_A | BES_TR9_five220_C | BES_TR9_five67_C | BES_TR9_five284_C | BES_TR9_five345_A | BES_TR9_five355_A | BES_TR9_five78_A | BES_TR9_five394_C | BES_TR9_five445_C | BES_TR9_five499_B | BES_TR9_five92_A | BES_TR9_five520_C | BES_TR9_five545_B | BES_TR9_five588_A | BES_TR9_five670_C | BES_TR9_five685_B | BES_TR9_five704_A | BES_TR9_five719_A | BES_TR9_five748_B | BES_TR9_five117_B | BES_TR9_five778_B | BES_TR9_five799_C | BES_TR9_five801_C | BES_TR9_five881_C | BES_TR9_five123_B | BES_TR9_six186_A | BES_TR9_six191_B | BES_TR9_six203_A | BES_TR9_six232_C | BES_TR9_six238_A | BES_TR9_six249_B | BES_TR9_six269_C | BES_TR9_six289_C | BES_TR9_six326_A | BES_TR9_six349_A | BES_TR9_six362_C | BES_TR9_six365_C | BES_TR9_six385_B | BES_TR9_six387_A | BES_TR9_six431_C | BES_TR9_six441_A | BES_TR9_six501_A | BES_TR9_six512_B | BES_TR9_six82_A | BES_TR9_six523_C | BES_TR9_six534_B | BES_TR9_six583_A | BES_TR9_six625_A | BES_TR9_six646_B | BES_TR9_six651_C | BES_TR9_six718_C | BES_TR9_six721_A | BES_TR9_six740_A | BES_TR9_six758_B | BES_TR9_six784_B | BES_TR9_six90_B | BES_TR9_six799_B | BES_TR9_six801_C | BES_TR9_six807_A | BES_TR9_six844_C | BES_TR9_six852_B | BES_TR9_six860_C | BES_TR9_six885_A | BES_TR9_six914_A | BES_TR9_six921_B | BES_TR9_six938_A | BES_TR9_six967_B | BES_TR9_six974_C | BES_TR9_six990_B | BES_TR9_six111_C | BES_TR9_six1006_C | BES_TR9_six1025_B | BES_TR9_six1064_C | BES_TR9_six128_B
1 | 0 | 0.048 | 0.049 | 0.054 | 0.117 | 0.577 | 0.594 | 0.045 | 0.211 | 0.145 | 0.156 | 0.052 | 0.706 | 0.049 | 1.047 | 1.071 | 0.57 | 0.1 | 0.046 | 0.061 | 0.082 | 0.288 | 0.045 | 0.055 | 0.164 | 0.75 | 0.103 | 0.046 | 0.048 | 0.104 | 0.046 | 0.054 | 0.599 | 0.144 | 0.165 | 0.131 | 0.149 | 0.149 | 0.053 | 0.148 | 0.081 | 0.06 | 0.053 | 0.059 | 0.111 | 0.499 | 0.152 | 0.055 | 0.149 | 0.079 | 0.156 | 0.11 | 0.127 | 0.053 | 0.683 | 0.734 | 0.16 | 0.133 | 0.168 | 0.769 | 0.37 | 0.201 | 0.163 | 0.243 | 0.308 | 0.084 | 0.129 | 0.187 | 0.21 | 0.585 | 0.316 | 0.061 | 0.052 | 0.206 | 0.252 | 0.412 | 0.109 | 0.105 | 0.111 | 0.428 | 0.08 | 0.409 | 0.268 | 0.696 | 0.183 | 0.838 | 0.122 | 0.207 | 0.03 | 0.066 | 0.14
2 | 0.5 | 0.1 | 0.049 | 0.215 | 0.085 | 0.49 | 0.572 | 0.139 | 0.046 | 0.198 | 0.293 | 0.114 | 0.136 | 0.049 | 0.574 | 1.043 | 0.713 | 0.122 | 0.159 | 0.052 | 0.125 | 0.375 | 0.305 | 0.127 | 0.048 | 0.257 | 0.089 | 0.107 | 0.21 | 0.171 | 0.199 | 0.172 | 0.544 | 0.23 | 0.047 | 0.055 | 0.17 | 0.139 | 0.053 | 0.106 | 0.28 | 0.243 | 0.053 | 0.148 | 0.141 | 0.621 | 0.041 | 0.32 | 0.082 | 0.196 | 0.242 | 0.095 | 0.05 | 0.053 | 0.149 | 0.438 | 0.146 | 0.173 | 0.202 | 0.109 | 0.049 | 0.044 | 0.05 | 0.329 | 0.613 | 0.151 | 0.153 | 0.183 | 0.177 | 0.618 | 0.148 | 0.185 | 0.052 | 0.124 | 0.057 | 0.227 | 0.042 | 0.286 | 0.247 | 0.052 | 0.184 | 0.054 | 0.391 | 0.322 | 0.213 | 0.802 | 0.084 | 0.093 | 0.159 | 0.206 | 0.212
3 | 1 | 0.304 | 0.049 | 0.058 | 0.054 | 0.273 | 0.563 | 0.045 | 0.316 | 0.171 | 0.121 | 0.118 | 0.149 | 0.049 | 0.77 | 0.058 | 0.093 | 0.116 | 0.119 | 0.121 | 0.055 | 0.216 | 0.088 | 0.218 | 0.309 | 0.054 | 0.208 | 0.191 | 0.048 | 0.098 | 0.046 | 0.079 | 0.548 | 0.161 | 0.221 | 0.087 | 0.22 | 0.083 | 0.161 | 0.05 | 0.049 | 0.152 | 0.053 | 0.12 | 0.036 | 0.268 | 0.243 | 0.062 | 0.042 | 0.137 | 0.059 | 0.218 | 0.05 | 0.053 | 0.143 | 0.831 | 0.099 | 0.104 | 0.054 | 0.217 | 0.12 | 0.044 | 0.228 | 0.328 | 0.131 | 0.044 | 0.155 | 0.05 | 0.211 | 0.048 | 0.046 | 0.135 | 0.052 | 0.158 | 0.226 | 0.174 | 0.038 | 0.04 | 0.052 | 0.206 | 0.05 | 0.373 | 0.051 | 0.317 | 0.194 | 0.751 | 0.332 | 0.058 | 0.03 | 0.051 | 0.078
4 | 1.5 | 0.077 | 0.049 | 0.054 | 0.223 | 0.085 | 0.058 | 0.139 | 0.089 | 0.348 | 0.222 | 0.052 | 0.186 | 0.049 | 0 | 0.219 | 0.171 | 0.16 | 0.288 | 0.048 | 0.152 | 0.056 | 0.051 | 0.055 | 0.069 | 0.26 | 0.241 | 0.073 | 0.048 | 0.059 | 0.158 | 0.082 | 0.656 | 0.153 | 0.122 | 0.163 | 0.177 | 0.034 | 0.053 | 0.05 | 0.203 | 0.19 | 0.053 | 0.079 | 0.066 | 0.176 | 0.041 | 0.126 | 0.189 | 0.185 | 0.184 | 0.076 | 0.158 | 0.053 | 0.054 | 0.387 | 0.246 | 0.09 | 0.262 | 0.109 | 0.178 | 0.183 | 0.05 | 0.231 | 0.123 | 0.137 | 0.108 | 0.294 | 0.126 | 0.114 | 0.128 | 0.161 | 0.052 | 0.142 | 0.084 | 0.106 | 0.084 | 0.273 | 0.06 | 0.052 | 0.132 | 0.054 | 0.316 | 0.107 | 0.169 | 0 | 0.049 | 0.084 | 0.118 | 0.159 | 0.195
5 | 2 | 0.12 | 0.049 | 0.131 | 0.067 | 0.288 | 0.291 | 0.045 | 0.089 | 0.154 | 0.083 | 0.052 | 0.174 | 0.049 | 0 | 0 | 0.142 | 0.057 | 0.057 | 0.126 | 0.05 | 0.056 | 0.342 | 0.177 | 0.048 | 0.054 | 0.277 | 0.199 | 0.072 | 0.26 | 0.088 | 0.089 | 0.043 | 0.096 | 0.082 | 0.055 | 0.048 | 0.191 | 0.145 | 0.204 | 0.158 | 0.185 | 0.053 | 0.188 | 0.17 | 0.187 | 0.041 | 0.351 | 0.042 | 0.177 | 0.087 | 0.113 | 0.05 | 0.053 | 0.054 | 0 | 0.149 | 0.209 | 0.086 | 0.033 | 0.087 | 0.174 | 0.203 | 0.055 | 0.22 | 0.097 | 0.159 | 0.543 | 0.292 | 0.044 | 0.232 | 0.149 | 0.052 | 0.134 | 0.128 | 0.046 | 0.067 | 0.117 | 0.222 | 0.136 | 0.132 | 0.054 | 0.051 | 0.23 | 0.173 | 0 | 0.213 | 0.111 | 0.071 | 0.113 | 0.171
6 | 2.5 | 0.269 | 0.049 | 0.142 | 0.1 | 0.143 | 0.13 | 0.139 | 0.304 | 0.184 | 0.287 | 0.052 | 0.047 | 0.049 | 0 | 0 | 0.048 | 0.079 | 0.046 | 0.052 | 0.147 | 0.142 | 0.051 | 0.167 | 0.247 | 0.08 | 0.046 | 0.046 | 0.143 | 0.053 | 0.046 | 0.054 | 0 | 0.304 | 0.091 | 0.055 | 0.22 | 0.146 | 0.068 | 0.05 | 0.049 | 0.21 | 0.053 | 0.059 | 0.036 | 0.272 | 0.213 | 0.28 | 0.042 | 0.061 | 0.168 | 0.135 | 0.142 | 0.053 | 0.143 | 0 | 0.246 | 0.144 | 0.501 | 0.109 | 0.211 | 0.044 | 0.074 | 0.055 | 0.164 | 0.044 | 0.072 | 0.152 | 0.116 | 0.119 | 0.046 | 0.227 | 0.052 | 0.174 | 0.181 | 0.09 | 0.075 | 0.072 | 0.052 | 0.122 | 0.05 | 0.273 | 0.186 | 0.227 | 0.192 | 0 | 0.075 | 0.102 | 0.03 | 0.051 | 0.102
7 | 3 | 0.106 | 0.049 | 0.054 | 0.046 | 0.199 | 0.101 | 0.045 | 0.058 | 0.235 | 0.167 | 0.052 | 0.18 | 0.049 | 0 | 0 | 0.265 | 0.276 | 0.231 | 0.121 | 0.061 | 0.198 | 0.159 | 0.105 | 0.13 | 0.206 | 0.175 | 0.243 | 0.048 | 0.132 | 0.199 | 0.054 | 0 | 0.094 | 0.192 | 0.195 | 0.177 | 0.034 | 0.053 | 0.127 | 0.136 | 0.06 | 0.053 | 0.059 | 0.2 | 0.179 | 0.071 | 0.373 | 0.122 | 0.254 | 0.168 | 0.172 | 0.065 | 0.053 | 0.054 | 0 | 0.05 | 0.049 | 0.503 | 0.058 | 0.124 | 0.233 | 0.082 | 0.055 | 0.147 | 0.111 | 0.236 | 0.21 | 0.068 | 0.044 | 0.129 | 0.069 | 0.052 | 0.109 | 0.075 | 0.191 | 0.075 | 0.212 | 0.128 | 0.052 | 0.191 | 0.154 | 0.072 | 0.063 | 0.239 | 0 | 0.049 | 0.093 | 0.159 | 0.221 | 0.193
8 | 3.5 | 0.237 | 0.046 | 0.051 | 0.152 | 0.236 | 0.082 | 0.042 | 0.139 | 0.168 | 0.228 | 0.049 | 0.12 | 0.046 | 0 | 0 | 0.045 | 0.085 | 0.185 | 0.051 | 0.047 | 0.053 | 0.042 | 0.236 | 0.046 | 0.078 | 0.071 | 0.078 | 0.045 | 0.185 | 0.043 | 0.115 | 0 | 0.18 | 0.082 | 0.053 | 0.132 | 0.185 | 0.15 | 0.124 | 0.198 | 0.332 | 0.051 | 0.206 | 0.034 | 0.188 | 0.051 | 0.824 | 0.108 | 0.095 | 0.169 | 0.099 | 0.048 | 0.051 | 0.096 | 0 | 0.087 | 0.179 | 0.226 | 0.19 | 0.144 | 0.12 | 0.194 | 0.052 | 0.317 | 0.121 | 0.059 | 0.075 | 0.362 | 0.117 | 0.229 | 0.205 | 0.05 | 0.239 | 0.233 | 0.1 | 0.099 | 0.037 | 0.227 | 0.049 | 0.07 | 0.052 | 0.065 | 0.271 | 0.037 | 0 | 0.338 | 0.055 | 0.027 | 0.048 | 0.156
9 | 4 | 0.142 | 0 | 0.093 | 0.072 | 0 | 0 | 0.089 | 0.098 | 0.168 | 0.196 | 0.015 | 0.143 | 0.012 | 0 | 0 | 0.158 | 0.075 | 0.114 | 0.097 | 0.114 | 0.226 | 0.202 | 0.005 | 0.285 | 0.004 | 0.068 | 0.036 | 0 | 0.028 | 0.087 | 0.023 | 0 | 0.141 | 0.187 | 0.094 | 0.213 | 0.053 | 0.017 | 0.006 | 0.023 | 0.023 | 0.028 | 0.015 | 0.005 | 0 | 0.15 | 0 | 0.05 | 0.019 | 0.086 | 0.104 | 0.127 | 0.022 | 0.061 | 0 | 0.148 | 0.155 | 0.104 | 0.055 | 0.068 | 0.099 | 0.031 | 0.005 | 0.068 | 0 | 0.196 | 0.137 | 0.017 | 0.025 | 0.021 | 0 | 0.027 | 0.052 | 0.032 | 0.029 | 0.026 | 0.095 | 0.078 | 0.002 | 0.019 | 0.258 | 0.276 | 0.158 | 0.299 | 0 | 0.038 | 0.094 | 0.086 | 0.102 | 0.077
10 | 4.5 | 0 | 0 | 0 | 0 | 0.036 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033 | 0 | 0.006 | 0 | 0.058 | 0 | 0 | 0 | 0.015 | 0.036 | 0.015 | 0 | 0 | 0 | 0.0002 | 0 | 0.016 | 0 | 0 | 0.055 | 0 | 0 | 0 | 0.075 | 0.014 | 0 | 0.075 | 0 | 0 | 0 | 0 | 0.031 | 0.027 | 0 | 0.035 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0.007 | 0.082 | 0 | 0 | 0 | 0.136 | 0 | 0 | 0 | 0 | 0 | 0.031 | 0 | 0 | 0 | 0.026 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 6.5 | 0.542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.634 | 0 | 0 | 0 | 0 | 0 | 1.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.419 | 0 | 0 | 0 | 0 | 0 | 0.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.323 | 0
18 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.105 | 0
19 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.223 | 0
20 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.701 | 0 | 0 | 0 | 0 | 0 | 0.063 | 0
21 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.411 | 0 | 0.475 | 0
22 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.201 | 0 | 0.104 | 0
24 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.413 | 0 | 0.379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.454 | 0 | 0 | 0 | 1.118 | 0 | 0.178 | 0
25 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.383 | 0 | 0 | 0 | 0.005 | 0 | 0 | 0
26 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.058 | 0 | 0 | 0 | 0 | 1.062 | 0
28 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0.226 | 1.768 | 0 | 0 | 0 | 0 | 0.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0.373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.593 | 1.647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 17.5 | 0 | 0 | 0 | 0 | 0.578 | 0 | 0 | 0 | 0.36 | 0 | 0 | 0 | 1.035 | 0 | 0.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.355 | 0.886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.988 | 0 | 0 | 0 | 0 | 0 | 0.024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.348 | 0 | 0 | 0 | 0.321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.829 | 0 | 0 | 0 | 0.447 | 0 | 0 | 0 | 0 | 0 | 0
37 | 18 | 0.661 | 0 | 0 | 0 | 0 | 0 | 0 | 0.679 | 0.328 | 0 | 0 | 0 | 0 | 0.612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086 | 0 | 0.478 | 0 | 0 | 0 | 0 | 0.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0.209 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053 | 0.003 | 0.177 | 0 | 0 | 0 | 0 | 0
38 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0.089 | 0 | 0 | 0.667 | 0 | 0 | 0 | 0 | 1.139 | 1.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.577 | 0 | 0 | 0 | 0 | 1.222 | 0 | 0 | 0.142 | 0 | 1.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0.404 | 0 | 0 | 1.9 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0.494 | 0 | 0 | 0 | 0 | 0.326 | 0 | 0 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0.018 | 0.132 | 0 | 0 | 0.758 | 0 | 0 | 0
39 | 19 | 0.026 | 0 | 0 | 0 | 0.226 | 1.319 | 0 | 0 | 1.916 | 0.513 | 0 | 0 | 1.315 | 0 | 0.227 | 0 | 0 | 0 | 0 | 0 | 0.068 | 0.016 | 0 | 0 | 0.154 | 0 | 0 | 0.197 | 0.172 | 0 | 0.218 | 0 | 0 | 0.031 | 0.024 | 0.268 | 0.809 | 0.276 | 0 | 0 | 0.373 | 0 | 0.072 | 0.01 | 0.231 | 0.092 | 0 | 0.017 | 0 | 0.332 | 0 | 0 | 0.107 | 0 | 0.167 | 0.068 | 0.78 | 0 | 0.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0.377 | 0 | 0.035 | 0.414 | 0.151 | 0 | 0.244 | 0.267 | 0 | 0 | 0 | 0 | 0.137 | 0.133 | 0.293 | 0.078 | 0 | 0 | 0 | 0.374 | 0
40 | 19.5 | 0.493 | 0 | 0.024 | 0.078 | 0.624 | 0.398 | 0.096 | 0 | 0.467 | 0.316 | 0.263 | 0 | 1.256 | 0.4 | 0 | 0.016 | 0.128 | 0.365 | 0.121 | 0.627 | 0.388 | 0.107 | 1.368 | 0.231 | 0.216 | 0.525 | 0.103 | 0.19 | 0.394 | 0.181 | 0.346 | 1.204 | 0.326 | 0.098 | 0.168 | 0.519 | 0.654 | 0.146 | 0.261 | 0 | 0.588 | 0.412 | 0.39 | 0.204 | 0.798 | 0.441 | 0.318 | 0.035 | 0.371 | 0.526 | 0.091 | 0.125 | 0.382 | 0.374 | 0.646 | 0.499 | 0.146 | 0.63 | 1.359 | 0.155 | 0.349 | 0.355 | 0.078 | 0 | 1.248 | 0.214 | 0.4 | 0.071 | 0.147 | 0.254 | 0.04 | 0.404 | 0.361 | 0.33 | 0.128 | 0.352 | 0.374 | 0 | 0.282 | 0.169 | 0.171 | 0.198 | 2.984 | 0.478 | 0.002 | 1.242 | 0.368 | 0.488 | 0.936 | 0.01
41 | 20 | 0.222 | 0.029 | 0.053 | 0.081 | 0.885 | 0.545 | 0.282 | 0.22 | 0.392 | 0.29 | 0.462 | 0.154 | 0.957 | 0.532 | 1.389 | 0.095 | 0.21 | 0.775 | 0.333 | 0.639 | 0.536 | 0.154 | 0.397 | 0.103 | 0.556 | 0.041 | 0.224 | 0.179 | 0.413 | 0.12 | 0.459 | 0.312 | 0.509 | 0.102 | 0.338 | 0.568 | 0.661 | 0.036 | 1.193 | 0.25 | 1.336 | 0.288 | 1.657 | 0.388 | 0.506 | 0.031 | 0.625 | 0.215 | 0.32 | 1.551 | 0.04 | 0.598 | 0.447 | 0.303 | 0.922 | 0.313 | 0.331 | 0.516 | 1.328 | 0.288 | 0.285 | 0.361 | 0.122 | 0.185 | 0.024 | 0.359 | 0.352 | 0.203 | 0.328 | 0.386 | 0.13 | 0.594 | 0.888 | 0.37 | 0.026 | 0.338 | 0.376 | 0.062 | 0.278 | 0.489 | 0.154 | 0.197 | 3.087 | 0.69 | 0.169 | 0.548 | 0.535 | 0.413 | 0.965 | 0.056
42 | 20.5 | 0.409 | 0.049 | 0.201 | 0.178 | 1.023 | 0.651 | 0.394 | 0.064 | 0.716 | 0.6 | 0.374 | 0.186 | 0.388 | 0.536 | 0.617 | 0.198 | 0.382 | 0.419 | 0.308 | 0.393 | 0.758 | 0.231 | 0.314 | 0.195 | 0.567 | 0.053 | 0.401 | 0.942 | 0.594 | 0.224 | 0.91 | 0.453 | 0.421 | 0.369 | 0.528 | 0.805 | 0.777 | 0.053 | 0.235 | 0.049 | 1.338 | 0.1 | 0.537 | 0.395 | 0.966 | 0.136 | 0.719 | 0.56 | 0.396 | 0.387 | 0.138 | 0.515 | 0.442 | 0.435 | 0.625 | 0.319 | 0.389 | 0.523 | 0.415 | 0.306 | 0.41 | 0.577 | 0.055 | 0.25 | 0.044 | 0.346 | 0.305 | 0.092 | 0.238 | 0.456 | 0.102 | 0.475 | 0.39 | 0.691 | 0.314 | 0.497 | 0.391 | 0.115 | 0.276 | 0.488 | 0.091 | 0.193 | 0.897 | 0.686 | 0.455 | 0.442 | 0.272 | 0.527 | 0.457 | 0.277
43 | 21 | 0.523 | 0.049 | 0.058 | 0.121 | 0.687 | 0.496 | 0.507 | 0.202 | 0.834 | 0.233 | 0.587 | 0.174 | 0.464 | 0.739 | 1.244 | 0.152 | 0.658 | 0.291 | 0.338 | 0.574 | 0.634 | 0.56 | 0.349 | 0.366 | 0.684 | 0.616 | 0.529 | 1.132 | 0.442 | 0.374 | 1.203 | 0.552 | 0.454 | 0.213 | 0.367 | 0.622 | 0.98 | 0.161 | 0.702 | 0.312 | 0.797 | 0.053 | 0.661 | 0.571 | 0.813 | 0.414 | 0.487 | 0.428 | 0.486 | 0.911 | 0.165 | 0.658 | 0.737 | 0.729 | 0.495 | 0.493 | 0.576 | 0.958 | 0.203 | 0.181 | 0.369 | 0.704 | 0.055 | 0.096 | 0.144 | 0.313 | 0.521 | 0.232 | 0.182 | 0.436 | 0.23 | 0.681 | 0.531 | 0.41 | 0.158 | 0.453 | 0.499 | 0.257 | 0.475 | 0.773 | 0.223 | 0.454 | 0 | 0.86 | 0.499 | 0.4 | 1.35 | 0.575 | 0.558 | 0.054
44 | 21.5 | 1.231 | 0.049 | 0.36 | 0.268 | 0.65 | 0.17 | 0.465 | 0.203 | 0.805 | 0.092 | 0.809 | 0.129 | 0.576 | 1.513 | 0.634 | 0.304 | 0.432 | 0.463 | 0.104 | 0.558 | 0.282 | 0.376 | 0.794 | 0.999 | 1.029 | 0.46 | 0.336 | 0.48 | 1.42 | 0.258 | 0.433 | 0.549 | 0.419 | 0.369 | 0.397 | 0.802 | 0.701 | 0.053 | 0.443 | 0.049 | 1.002 | 0.053 | 0.991 | 0.593 | 0.722 | 0.302 | 0.742 | 0.508 | 0.495 | 0.537 | 0.19 | 0.741 | 0.345 | 0.562 | 0.471 | 0.4 | 0.768 | 1.652 | 0.402 | 0.538 | 0.271 | 0.378 | 0.055 | 0.344 | 0.091 | 0.21 | 0.561 | 0.193 | 0.369 | 0.361 | 0.078 | 0.829 | 0.597 | 0.992 | 1.496 | 0.254 | 0.328 | 0.086 | 0.654 | 0.281 | 0.217 | 0.183 | 0 | 0.469 | 0.391 | 0.857 | 0.505 | 0.441 | 0.62 | 0.298
45 | 22 | 0.681 | 0.049 | 0.499 | 0.47 | 0.18 | 0.058 | 0.484 | 0.15 | 0.686 | 0.138 | 0.553 | 0.136 | 0.454 | 1.789 | 1.096 | 0.697 | 0.486 | 0.533 | 0.048 | 0.601 | 0.079 | 0.547 | 0.093 | 0.391 | 0.441 | 0.616 | 0.32 | 0.465 | 1.679 | 0.378 | 0.442 | 0.365 | 0.438 | 0.059 | 1.034 | 0.9 | 0.76 | 0.161 | 0.321 | 0.177 | 1.301 | 0.486 | 1.643 | 0.422 | 0.859 | 0.575 | 1.357 | 0.694 | 0.623 | 0.801 | 0.052 | 0.05 | 0.298 | 0.672 | 1.172 | 0.425 | 1.701 | 0.432 | 0.267 | 0.587 | 0.179 | 0.573 | 0.055 | 0.12 | 0.104 | 0.682 | 0.739 | 0.076 | 0.298 | 0.602 | 0.292 | 0.836 | 0.426 | 0.551 | 0.553 | 0.305 | 0.232 | 0.256 | 0.499 | 0.315 | 0.882 | 0.53 | 0 | 0.143 | 0.554 | 0.367 | 0.595 | 0.159 | 0.947 | 0.054
46 | 22.5 | 0.75 | 0.049 | 0.436 | 0.107 | 0.195 | 0.273 | 0.549 | 0.072 | 0 | 0.171 | 0.407 | 0.142 | 0.174 | 0 | 0.519 | 0.569 | 0.262 | 0.593 | 0.065 | 0.53 | 0.162 | 0.52 | 0.204 | 0.309 | 0.168 | 0.755 | 0.666 | 0.35 | 0.41 | 0.211 | 0.348 | 0.361 | 0.275 | 0.182 | 0.305 | 0.762 | 0.893 | 0.053 | 0.199 | 0.097 | 0.437 | 0.452 | 0 | 0.438 | 0.921 | 0.676 | 2.145 | 1.359 | 0.876 | 0.359 | 0.218 | 0.05 | 0.347 | 0.591 | 0.484 | 0.427 | 0.793 | 0.498 | 0.54 | 0.486 | 0.428 | 0.167 | 0.055 | 0.117 | 0.131 | 0.38 | 0.057 | 0.282 | 0.271 | 0.403 | 0.495 | 0.618 | 1.099 | 0.818 | 0.538 | 0.183 | 0.097 | 0.102 | 0.607 | 0.217 | 1.247 | 0.399 | 0 | 0.211 | 0.814 | 0.222 | 1.548 | 0.03 | 0.72 | 0.19
47 | 23 | 0.567 | 0.396 | 0.596 | 0.169 | 0.236 | 0.148 | 0.409 | 0.334 | 0 | 0.206 | 0.411 | 0.142 | 0.323 | 0 | 0 | 0.51 | 0.062 | 0.546 | 0.108 | 0.05 | 0.178 | 0.344 | 0.141 | 0.168 | 0.145 | 0.552 | 0.046 | 0.048 | 0.241 | 1.244 | 0.082 | 0.103 | 0.201 | 1.538 | 0.506 | 0.58 | 0.937 | 0.061 | 0.222 | 0.081 | 0 | 0.713 | 0 | 0.306 | 0.822 | 0.441 | 0.779 | 0.321 | 0.552 | 0.263 | 0.138 | 0.05 | 0.053 | 0.507 | 0.763 | 0.05 | 0.263 | 0.175 | 0.517 | 0.653 | 0.38 | 0.155 | 0.055 | 0.29 | 0.044 | 0.428 | 0.208 | 0.142 | 0.318 | 0.22 | 0.091 | 0.463 | 0.472 | 0.664 | 0.394 | 0.038 | 0.224 | 0.052 | 0.499 | 0.391 | 0.889 | 0.24 | 0 | 0.091 | 0.612 | 0.194 | 0.761 | 0.159 | 0.562 | 0.162
48 | 23.5 | 0.501 | 0.165 | 0.743 | 0.601 | 0.413 | 0.058 | 1.1 | 0.046 | 0 | 0.193 | 0.395 | 0.218 | 0.049 | 0 | 0 | 0.075 | 0.322 | 0.235 | 0.078 | 0.088 | 0.056 | 0.244 | 0.069 | 0.225 | 0.054 | 1.44 | 0.176 | 0.167 | 0.171 | 0.224 | 0.089 | 0.074 | 0.149 | 1.405 | 0.171 | 0.991 | 0 | 0.153 | 0.572 | 0.193 | 0 | 0.161 | 0 | 0.305 | 0.236 | 0.473 | 0 | 0.169 | 0.794 | 0.135 | 0.203 | 0.142 | 0.063 | 0.646 | 0.162 | 0.05 | 0.056 | 0.13 | 0.168 | 0.049 | 0.187 | 0.123 | 0.055 | 0.126 | 0.171 | 0.342 | 0.113 | 0.244 | 0.044 | 0.46 | 0.052 | 0.477 | 0.784 | 0.306 | 0.317 | 0.113 | 0.16 | 0.231 | 0.301 | 0.303 | 0.305 | 0.382 | 0 | 0.12 | 0.718 | 0.11 | 0.649 | 0.03 | 0.405 | 0.104

## 7. PV allocation (per period)
TR9 PV allocation — per half-hour
VIOLET = aggregated live from the raw sheets 3–6 (SUM / SUMIF). AMBER = priority split (MIN formulas): PV → prosumer load → battery → customer load → export.
period | hour (h) | PV (kW) | prosumer load (kW) | customer load (kW) | batt charge (kW) | batt discharge (kW) | batt net =chg−dis | PV→ prosumer | PV→ battery | PV→ customer | PV→ export | customer ←grid
1 | 0 | 0 | 20.9812 | 19.519 | 0 | 20.983 | -20.983 | 0 | 0 | 0 | 0 | 19.519
2 | 0.5 | 0 | 18.9665 | 16.3714 | 0 | 18.967 | -18.967 | 0 | 0 | 0 | 0 | 16.3714
3 | 1 | 0 | 14.6159 | 13.4279 | 0 | 14.449 | -14.449 | 0 | 0 | 0 | 0 | 13.4279
4 | 1.5 | 0 | 13.148 | 11.0852 | 0 | 12.225 | -12.225 | 0 | 0 | 0 | 0 | 11.0852
5 | 2 | 0 | 12.762 | 11.2356 | 0 | 11.412 | -11.412 | 0 | 0 | 0 | 0 | 11.2356
6 | 2.5 | 0 | 11.8935 | 10.2205 | 0 | 10.622 | -10.622 | 0 | 0 | 0 | 0 | 10.2205
7 | 3 | 0 | 11.9806 | 9.6378 | 0 | 11.331 | -11.331 | 0 | 0 | 0 | 0 | 9.6378
8 | 3.5 | 0.2379 | 13.0479 | 10.5542 | 0 | 11.287 | -11.287 | 0.2379 | 0 | 0 | 0 | 10.5542
9 | 4 | 3.45 | 11.0102 | 9.1705 | 0.024 | 6.851 | -6.827 | 3.45 | 0 | 0 | 0 | 9.1705
10 | 4.5 | 16.1357 | 11.0676 | 10.6873 | 6.197 | 0.9112 | 5.2858 | 11.0676 | 5.0681 | 0 | 0 | 10.6873
11 | 5 | 32.0044 | 11.3978 | 10.1862 | 20.769 | 0.031 | 20.738 | 11.3978 | 20.6066 | 0 | 0 | 10.1862
12 | 5.5 | 51.4676 | 13.6021 | 9.5791 | 38.99 | 1.128 | 37.862 | 13.6021 | 37.862 | 0.0035 | 0 | 9.5756
13 | 6 | 72.6981 | 12.951 | 12.7589 | 60.305 | 0.211 | 60.094 | 12.951 | 59.7471 | 0 | 0 | 12.7589
14 | 6.5 | 94.1925 | 14.9905 | 9.3488 | 80.292 | 1.084 | 79.208 | 14.9905 | 79.202 | 0 | 0 | 9.3488
15 | 7 | 115.5772 | 20.0008 | 13.7907 | 96.9 | 1.723 | 95.177 | 20.0008 | 95.177 | 0.3994 | 0 | 13.3913
16 | 7.5 | 136.9888 | 21.9619 | 19.6373 | 107.191 | 0.99 | 106.201 | 21.9619 | 106.201 | 8.8259 | 0 | 10.8114
17 | 8 | 157.0866 | 22.5715 | 28.9197 | 77.049 | 0.933 | 76.116 | 22.5715 | 76.116 | 28.9197 | 29.4794 | 0
18 | 8.5 | 175.9815 | 26.9247 | 21.1916 | 48.849 | 0.803 | 48.046 | 26.9247 | 48.046 | 21.1916 | 79.8192 | 0
19 | 9 | 192.0707 | 31.6773 | 26.9657 | 28.535 | 0.811 | 27.724 | 31.6773 | 27.724 | 26.9657 | 105.7037 | 0
20 | 9.5 | 205.794 | 33.9608 | 32.1727 | 19.922 | 2.045 | 17.877 | 33.9608 | 17.877 | 32.1727 | 121.7835 | 0
21 | 10 | 217.8375 | 32.0558 | 28.8352 | 15.144 | 1.221 | 13.923 | 32.0558 | 13.923 | 28.8352 | 143.0235 | 0
22 | 10.5 | 227.7802 | 26.4863 | 30.3401 | 8.143 | 0 | 8.143 | 26.4863 | 8.143 | 30.3401 | 162.8108 | 0
23 | 11 | 234.8339 | 27.2224 | 39.4027 | 3.2533 | 0.305 | 2.9483 | 27.2224 | 2.9483 | 39.4027 | 165.2605 | 0
24 | 11.5 | 237.9285 | 35.5228 | 33.0762 | 1.853 | 5.624 | -3.771 | 35.5228 | 0 | 33.0762 | 169.3295 | 0
25 | 12 | 238.8234 | 28.3414 | 32.0558 | 2.965 | 1.388 | 1.577 | 28.3414 | 1.577 | 32.0558 | 176.8492 | 0
26 | 12.5 | 237.1457 | 25.3616 | 35.9095 | 6.038 | 3.233 | 2.805 | 25.3616 | 2.805 | 35.9095 | 173.0696 | 0
27 | 13 | 231.5167 | 26.0941 | 39.725 | 5.526 | 4.033 | 1.493 | 26.0941 | 1.493 | 39.725 | 164.2046 | 0
28 | 13.5 | 222.9244 | 29.1395 | 26.8406 | 2.841 | 0 | 2.841 | 29.1395 | 2.841 | 26.8406 | 164.1033 | 0
29 | 14 | 212.6691 | 24.53 | 31.1618 | 1.634 | 0 | 1.634 | 24.53 | 1.634 | 31.1618 | 155.3433 | 0
30 | 14.5 | 199.6742 | 27.6466 | 30.0181 | 2.451 | 0.094 | 2.357 | 27.6466 | 2.357 | 30.0181 | 139.6525 | 0
31 | 15 | 185.8637 | 30.7023 | 25.9194 | 2.096 | 2.808 | -0.712 | 30.7023 | 0 | 25.9194 | 129.242 | 0
32 | 15.5 | 169.2457 | 25.7559 | 21.3668 | 3.099 | 1.467 | 1.632 | 25.7559 | 1.632 | 21.3668 | 120.491 | 0
33 | 16 | 150.5308 | 31.3904 | 22.7029 | 1.372 | 0.88 | 0.492 | 31.3904 | 0.492 | 22.7029 | 95.9455 | 0
34 | 16.5 | 127.9333 | 30.8723 | 25.5752 | 1.87 | 3.812 | -1.942 | 30.8723 | 0 | 25.5752 | 71.4858 | 0
35 | 17 | 106.782 | 34.6158 | 25.968 | 1.219 | 3.528 | -2.309 | 34.6158 | 0 | 25.968 | 46.1982 | 0
36 | 17.5 | 85.049 | 38.2084 | 29.7079 | 1.497 | 9.348 | -7.851 | 38.2084 | 0 | 29.7079 | 17.1327 | 0
37 | 18 | 64.0279 | 31.3578 | 36.2503 | 3.811 | 4.651 | -0.84 | 31.3578 | 0 | 32.6701 | 0 | 3.5802
38 | 18.5 | 43.7602 | 35.3432 | 31.3248 | 3.39 | 11.783 | -8.393 | 35.3432 | 0 | 8.417 | 0 | 22.9078
39 | 19 | 25.5516 | 31.2779 | 29.6548 | 1.635 | 13.012 | -11.377 | 25.5516 | 0 | 0 | 0 | 29.6548
40 | 19.5 | 7.437 | 41.1865 | 35.9164 | 0.07 | 34.02 | -33.95 | 7.437 | 0 | 0 | 0 | 35.9164
41 | 20 | 1.3727 | 42.042 | 39.867 | 0 | 40.669 | -40.669 | 1.3727 | 0 | 0 | 0 | 39.867
42 | 20.5 | 0 | 38.3195 | 43.3945 | 0 | 37.415 | -37.415 | 0 | 0 | 0 | 0 | 43.3945
43 | 21 | 0 | 45.2713 | 43.8796 | 0 | 43.491 | -43.491 | 0 | 0 | 0 | 0 | 43.8796
44 | 21.5 | 0 | 46.5627 | 38.4107 | 0 | 44.887 | -44.887 | 0 | 0 | 0 | 0 | 38.4107
45 | 22 | 0 | 47.7176 | 40.9881 | 0 | 45.795 | -45.795 | 0 | 0 | 0 | 0 | 40.9881
46 | 22.5 | 0 | 43.1127 | 35.3938 | 0 | 37.636 | -37.636 | 0 | 0 | 0 | 0 | 35.3938
47 | 23 | 0 | 33.2678 | 28.8786 | 0 | 29.195 | -29.195 | 0 | 0 | 0 | 0 | 28.8786
48 | 23.5 | 0 | 27.2736 | 21.1311 | 0 | 23.577 | -23.577 | 0 | 0 | 0 | 0 | 21.1311
TOTAL | kWh/day | 2241.1862 | 643.095 | 605.0775 | 327.4651 | 266.3346 | 61.1305 | 399.9009 | 306.736 | 319.0854 | 1215.4639 | 285.9921
Each half-hour is 0.5 h, so daily energy (kWh) = Σ(power in kW) × 0.5.
Trace any input: e.g. cell C5 = SUM of column C on sheet 3 (PV of all 172 connections at 00:00). Click it to see the formula.

## 8. Results & charts
TR9 PV allocation — results
Where the day's PV goes |  |  | How the customers (82) are supplied
Destination | kWh/day | % of PV | Source | kWh/day | % of cust. load
PV → prosumers' own load | 399.9009 | 17.84% | From prosumer PV (day) | 319.0854 | 52.73%
PV → battery storage | 306.736 | 13.69% | From grid import (night) | 285.9921 | 47.27%
PV → customers | 319.0854 | 14.24% | TOTAL customer load | 605.0775 | 100%
PV → export to grid | 1215.4639 | 54.23%
TOTAL (= PV) | 2241.1862 | 100%
Charts read live from sheet 7, which reads live from raw sheets 3–6.