## 1_Summary
TR9 rolling flexibility operating region (FOR)
How the region is built, column by column — 48 half-hourly rolling steps × 12 boundary directions, measured at the feeder PCC with TR9's batteries as the flexible resource.
WHAT THIS WORKBOOK IS
Purpose | Each half-hour of the day has its own FOR: the set of active/reactive power (P,Q) that can be presented at the feeder's point of common coupling for the next time slot, when TR9's batteries are the flexible resource. IMPORTANT: the PCC is the feeder's slack/HV bus, so every (P,Q) here is a whole-feeder quantity — all nine transformers, all 172+ loads and every PV panel — not TR9's own connection point. The eight other transformers are lumped as passive loads in this run, their batteries idle. The optimizer finds the region by pushing the operating point as far as it will go in 12 compass directions (0°,30°,…,330°). Joining those 12 points gives the boundary. This file shows the numbers and the formulas that turn them into the two pictures you have seen (absolute and deviation). Two flexibilities live here and must not be confused: the PV (uncontrollable, already in the baseline) and the battery (controllable — the deviation the operator can move).
Sign convention | P > 0 = IMPORT from the grid. P < 0 = EXPORT (surplus sent to the grid). Q > 0 = the inverters absorb reactive power. Q < 0 = they inject it. Units: MW / MVAr (per-unit × 1 MVA base).
AT A GLANCE (LIVE COUNTS FROM 4_ALL_PERIODS)
Rolling steps | 48
Boundary points solved | 576
Solves that are not optimal | 0
Points at the 1.10 pu voltage wall | 254
CONTENTS — HOW THE TABS ARE ORGANISED
1_Summary | This page: purpose, sign convention, column glossary and the recipe for building one FOR by hand.
2_Sample_00h00 | Worked example for period 1 = 00:00. The P/Q numbers are typed in, so you can overwrite them and watch the charts move.
3_Sample_12h00 | Worked example for period 25 = 12:00, in the midday solar window. Same layout, numbers typed in.
4_All_periods | Master data. All 48 periods × 12 directions = 576 boundary points, with the baseline and the deviation of each.
P02_00h30 … P48_23h30 | One tab per rolling step, each with its own absolute and deviation chart. These read from 4_All_periods, so they follow the master data.
COLUMN GLOSSARY
now | Rolling step = which half-hour we are planning from. 1 = 00:00, 2 = 00:30, … 48 = 23:30.
target | The service slot being offered = the next half-hour (t+1), so target = now + 1. The last step (now = 48 = 23:30) offers slot 1 = 00:00.
angle_deg | Direction the optimizer pushes in. 0° = as much IMPORT as possible, 90° = as much +Q, 180° = as much EXPORT, 270° = as much −Q. The 12 angles trace the boundary.
P | Active power at the PCC at that boundary point (MW). + import / − export.
Q | Reactive power at the PCC at that boundary point (MVAr).
proj | ‘Support’ value = how far the region reaches in the push direction. proj = P·cos(angle) + Q·sin(angle). (Column F recomputes it so you can check.)
status | Solver result. ‘Optimal’ = a valid boundary point. All 576 are Optimal here.
VmaxTrue | The TRUE highest voltage anywhere in the network at that point (per-unit). When it equals 1.10000 the over-voltage limit is what stops the region — the binding wall.
VminTrue | The true lowest network voltage (pu). Watches the under-voltage limit (0.94). (in the source CSV; not carried into this workbook)
OVviol / UVviol | Over-/under-voltage violation (pu). ≈0 means the point is genuinely AC-feasible. (in the source CSV; not carried into this workbook)
LinErr | Internal linearization-error check (pu). Small = the linear model tracked the exact AC solve. (in the source CSV; not carried into this workbook)
B_P , B_Q | The BASELINE for that half-hour = the PCC power with every battery ON THE FEEDER switched OFF. It is the whole feeder's passive imbalance: load − PV summed over all nine transformers, plus the network losses. Sanity check at period 25: B_P = −2.2582 MW, the nine transformers' load − PV sum to −2.2803 MW, and the 22 kW gap is losses. TR9 alone is only −0.1784 MW. This is the UNCONTROLLABLE part: the PV / self-consumption commitment already serving local load, neighbours' load and losses — nobody is paid for it. The batteries deviate around this point. Read from FOR_rolling_baseline.csv, one series shared by all nine per-transformer runs.
dP , dQ | The DEVIATION = P − B_P and Q − B_Q. This is the CONTROLLABLE flexibility a DSO/TSO can dispatch — the effect of TR9's batteries at the PCC (battery power, to within a small network-loss term). PV is NOT here; it is already inside the baseline. dP > 0 = the batteries can still charge (import more); dP < 0 = they can still discharge (export more). Use the deviation, not the absolute point, for fairness allocation and dispatch: the absolute regions of all nine transformers overlap on the shared baseline, so only the deviation separates them. Reference: measured from the batteries-OFF baseline, not from the committed self-consumption schedule.
STEP BY STEP: HOW TO BUILD ONE FOR BY HAND
Step 1 | Pick a half-hour (a ‘now’ value, e.g. 25 = 12:00).
Step 2 | Read its 12 boundary vertices (angle, P, Q) — columns A,B,C on the sample sheets. Each came from ONE optimization solve that maximised the push in that direction.
Step 3 | Read the baseline B = (B_P, B_Q) for that half-hour (the batteries-off PCC point).
Step 4 | Compute the deviation for every vertex: dP = P − B_P , dQ = Q − B_Q. (Column D,E do this with a formula.)
Step 5 | Plot P vs Q → the ABSOLUTE FOR (where the region really sits).
Step 6 | Plot dP vs dQ → the DEVIATION FOR (centred on the self-consumption plan). Right of the vertical axis = battery can still charge; left = still discharge.
Step 7 | Read the flexibility off it: import-reach = max(dP over the 12 points, but ≥0); export-reach = −min(dP), ≥0. If both > 0 the region straddles zero (can do both).
COLOUR KEY
INPUT | Numbers straight from the optimizer. Safe to overwrite on the two sample tabs if you want to test a what-if.
LIVE FORMULA | Calculated cell — click it to see the formula. Recomputes as soon as an input changes.
BASELINE B | The batteries-off PCC point (load − PV) that every deviation is measured from.
Source: rolling FOR solves exported as FOR_rolling_TR9.csv; baselines from FOR_rolling_baseline.csv. P, Q, proj and the baselines are stored rounded to 4 decimals and VmaxTrue to 5, so the proj check agrees with the solver's proj to about 1e-4 rather than exactly. Checked against the exports: all 576 solves optimal, true voltages within 1.10000 / 0.94454 pu and no limit violations. Editing a value on 4_All_periods updates every P## tab and chart that reads it.

## 2_Sample_00h00
TR9 rolling FOR — period 1 = 00:00 (worked example)
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 0.5454 | B_Q (MVAr) = | 0.112
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 0.775 | 0.0853 | 0.2296 | -0.0267 | 0.775 | charge/import
30 | 0.7285 | 0.2533 | 0.1831 | 0.1413 | 0.75755 | charge/import
60 | 0.6073 | 0.3755 | 0.0619 | 0.2635 | 0.62884 | charge/import
90 | 0.4554 | 0.4146 | -0.09 | 0.3026 | 0.4146 | discharge/export
120 | 0.2923 | 0.3713 | -0.2531 | 0.2593 | 0.17541 | discharge/export
150 | 0.2578 | 0.3477 | -0.2876 | 0.2357 | -0.049411 | discharge/export
180 | 0.2551 | -0.1119 | -0.2903 | -0.2239 | -0.2551 | discharge/export
210 | 0.2667 | -0.1651 | -0.2787 | -0.2771 | -0.14842 | discharge/export
240 | 0.3065 | -0.194 | -0.2389 | -0.306 | 0.014759 | discharge/export
270 | 0.4468 | -0.2297 | -0.0986 | -0.3417 | 0.2297 | discharge/export
300 | 0.6119 | -0.1854 | 0.0665 | -0.2974 | 0.46651 | charge/import
330 | 0.7327 | -0.0647 | 0.1873 | -0.1767 | 0.66689 | charge/import
(close) | 0.775 | 0.0853 | 0.2296 | -0.0267
Interpretation (all computed live):
P width (MW) |  | 0.5199
import-reach (charge) |  | 0.2296
export-reach (dischg) |  | 0.2903
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## 3_Sample_12h00
TR9 rolling FOR — period 25 = 12:00 (worked example)
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -2.2582 | B_Q (MVAr) = | 0.2073
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -2.259 | 0.2471 | -0.0008 | 0.0398 | -2.259 | discharge/export
30 | -2.274 | 0.515 | -0.0158 | 0.3077 | -1.7118 | discharge/export
60 | -2.2778 | 0.5183 | -0.0196 | 0.311 | -0.69004 | discharge/export
90 | -2.3207 | 0.5227 | -0.0625 | 0.3154 | 0.5227 | discharge/export
120 | -2.4081 | 0.5033 | -0.1499 | 0.296 | 1.6399 | discharge/export
150 | -2.5088 | 0.396 | -0.2506 | 0.1887 | 2.3707 | discharge/export
180 | -2.5456 | 0.2774 | -0.2874 | 0.0701 | 2.5456 | discharge/export
210 | -2.5269 | 0.2235 | -0.2687 | 0.0162 | 2.0766 | discharge/export
240 | -2.3268 | 0.0122 | -0.0686 | -0.1951 | 1.1528 | discharge/export
270 | -2.2763 | -0.0009 | -0.0181 | -0.2082 | 0.0009 | discharge/export
300 | -2.2673 | -0.0003 | -0.0091 | -0.2076 | -1.1334 | discharge/export
330 | -2.2673 | -0.0003 | -0.0091 | -0.2076 | -1.9634 | discharge/export
(close) | -2.259 | 0.2471 | -0.0008 | 0.0398
Interpretation (all computed live):
P width (MW) |  | 0.2866
import-reach (charge) |  | 0
export-reach (dischg) |  | 0.2874
verdict |  | one-sided → discharge/export only (no import headroom)
what stops it |  | blocked at 0°: Vmax there = 1.10000 pu → over-voltage limit is active
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## 4_All_periods
now | hour | angle_deg | P (MW) | Q (MVAr) | proj | status | VmaxTrue (pu) | B_P (MW) | B_Q (MVAr) | dP = P−B_P | dQ = Q−B_Q
1 | 00:00 | 0 | 0.775 | 0.0853 | 0.775 | Optimal | 1.0275 | 0.5454 | 0.112 | 0.2296 | -0.0267
1 | 00:00 | 30 | 0.7285 | 0.2533 | 0.7575 | Optimal | 1.0092 | 0.5454 | 0.112 | 0.1831 | 0.1413
1 | 00:00 | 60 | 0.6073 | 0.3755 | 0.6288 | Optimal | 1.0049 | 0.5454 | 0.112 | 0.0619 | 0.2635
1 | 00:00 | 90 | 0.4554 | 0.4146 | 0.4146 | Optimal | 1.0092 | 0.5454 | 0.112 | -0.09 | 0.3026
1 | 00:00 | 120 | 0.2923 | 0.3713 | 0.1754 | Optimal | 1.0274 | 0.5454 | 0.112 | -0.2531 | 0.2593
1 | 00:00 | 150 | 0.2578 | 0.3477 | -0.0495 | Optimal | 1.0445 | 0.5454 | 0.112 | -0.2876 | 0.2357
1 | 00:00 | 180 | 0.2551 | -0.1119 | -0.2551 | Optimal | 1.1 | 0.5454 | 0.112 | -0.2903 | -0.2239
1 | 00:00 | 210 | 0.2667 | -0.1651 | -0.1484 | Optimal | 1.1 | 0.5454 | 0.112 | -0.2787 | -0.2771
1 | 00:00 | 240 | 0.3065 | -0.194 | 0.0147 | Optimal | 1.1 | 0.5454 | 0.112 | -0.2389 | -0.306
1 | 00:00 | 270 | 0.4468 | -0.2297 | 0.2297 | Optimal | 1.0953 | 0.5454 | 0.112 | -0.0986 | -0.3417
1 | 00:00 | 300 | 0.6119 | -0.1854 | 0.4665 | Optimal | 1.0753 | 0.5454 | 0.112 | 0.0665 | -0.2974
1 | 00:00 | 330 | 0.7327 | -0.0647 | 0.6669 | Optimal | 1.0468 | 0.5454 | 0.112 | 0.1873 | -0.1767
2 | 00:30 | 0 | 0.6851 | 0.0676 | 0.6851 | Optimal | 1.0283 | 0.4511 | 0.0924 | 0.234 | -0.0248
2 | 00:30 | 30 | 0.6367 | 0.2389 | 0.6709 | Optimal | 1.0099 | 0.4511 | 0.0924 | 0.1856 | 0.1465
2 | 00:30 | 60 | 0.522 | 0.355 | 0.5685 | Optimal | 1.0052 | 0.4511 | 0.0924 | 0.0709 | 0.2626
2 | 00:30 | 90 | 0.3646 | 0.3963 | 0.3963 | Optimal | 1.0096 | 0.4511 | 0.0924 | -0.0865 | 0.3039
2 | 00:30 | 120 | 0.2101 | 0.3565 | 0.2037 | Optimal | 1.0295 | 0.4511 | 0.0924 | -0.241 | 0.2641
2 | 00:30 | 150 | 0.187 | 0.3413 | 0.0087 | Optimal | 1.0416 | 0.4511 | 0.0924 | -0.2641 | 0.2489
2 | 00:30 | 180 | 0.1845 | -0.1443 | -0.1845 | Optimal | 1.1 | 0.4511 | 0.0924 | -0.2666 | -0.2367
2 | 00:30 | 210 | 0.1963 | -0.1915 | -0.0742 | Optimal | 1.1 | 0.4511 | 0.0924 | -0.2548 | -0.2839
2 | 00:30 | 240 | 0.2297 | -0.2154 | 0.0717 | Optimal | 1.1 | 0.4511 | 0.0924 | -0.2214 | -0.3078
2 | 00:30 | 270 | 0.3579 | -0.2485 | 0.2485 | Optimal | 1.0988 | 0.4511 | 0.0924 | -0.0932 | -0.3409
2 | 00:30 | 300 | 0.5222 | -0.2044 | 0.4381 | Optimal | 1.0788 | 0.4511 | 0.0924 | 0.0711 | -0.2968
2 | 00:30 | 330 | 0.6424 | -0.0842 | 0.5985 | Optimal | 1.0482 | 0.4511 | 0.0924 | 0.1913 | -0.1766
3 | 01:00 | 0 | 0.669 | 0.0631 | 0.669 | Optimal | 1.0293 | 0.3612 | 0.0739 | 0.3078 | -0.0108
3 | 01:00 | 30 | 0.6206 | 0.2354 | 0.6551 | Optimal | 1.0113 | 0.3612 | 0.0739 | 0.2594 | 0.1615
3 | 01:00 | 60 | 0.5037 | 0.3528 | 0.5574 | Optimal | 1.0072 | 0.3612 | 0.0739 | 0.1425 | 0.2789
3 | 01:00 | 90 | 0.3485 | 0.3931 | 0.3931 | Optimal | 1.0116 | 0.3612 | 0.0739 | -0.0127 | 0.3192
3 | 01:00 | 120 | 0.2004 | 0.3553 | 0.2075 | Optimal | 1.0282 | 0.3612 | 0.0739 | -0.1608 | 0.2814
3 | 01:00 | 150 | 0.1855 | 0.3457 | 0.0122 | Optimal | 1.0368 | 0.3612 | 0.0739 | -0.1757 | 0.2718
3 | 01:00 | 180 | 0.1833 | -0.1595 | -0.1833 | Optimal | 1.1 | 0.3612 | 0.0739 | -0.1779 | -0.2334
3 | 01:00 | 210 | 0.1941 | -0.2041 | -0.066 | Optimal | 1.1 | 0.3612 | 0.0739 | -0.1671 | -0.278
3 | 01:00 | 240 | 0.2168 | -0.2201 | 0.0822 | Optimal | 1.1 | 0.3612 | 0.0739 | -0.1444 | -0.294
3 | 01:00 | 270 | 0.3423 | -0.2518 | 0.2518 | Optimal | 1.0962 | 0.3612 | 0.0739 | -0.0189 | -0.3257
3 | 01:00 | 300 | 0.5064 | -0.2077 | 0.4331 | Optimal | 1.0785 | 0.3612 | 0.0739 | 0.1452 | -0.2816
3 | 01:00 | 330 | 0.6266 | -0.0877 | 0.5865 | Optimal | 1.0486 | 0.3612 | 0.0739 | 0.2654 | -0.1616
4 | 01:30 | 0 | 0.638 | 0.0561 | 0.638 | Optimal | 1.0292 | 0.3453 | 0.0707 | 0.2927 | -0.0146
4 | 01:30 | 30 | 0.5894 | 0.2293 | 0.6251 | Optimal | 1.0124 | 0.3453 | 0.0707 | 0.2441 | 0.1586
4 | 01:30 | 60 | 0.4739 | 0.3459 | 0.5365 | Optimal | 1.0082 | 0.3453 | 0.0707 | 0.1286 | 0.2752
4 | 01:30 | 90 | 0.3176 | 0.3868 | 0.3868 | Optimal | 1.0126 | 0.3453 | 0.0707 | -0.0277 | 0.3161
4 | 01:30 | 120 | 0.1751 | 0.351 | 0.2164 | Optimal | 1.0266 | 0.3453 | 0.0707 | -0.1702 | 0.2803
4 | 01:30 | 150 | 0.167 | 0.3459 | 0.0283 | Optimal | 1.031 | 0.3453 | 0.0707 | -0.1783 | 0.2752
4 | 01:30 | 180 | 0.1648 | -0.1805 | -0.1648 | Optimal | 1.1 | 0.3453 | 0.0707 | -0.1805 | -0.2512
4 | 01:30 | 210 | 0.174 | -0.2157 | -0.0429 | Optimal | 1.1 | 0.3453 | 0.0707 | -0.1713 | -0.2864
4 | 01:30 | 240 | 0.1923 | -0.2285 | 0.1017 | Optimal | 1.1 | 0.3453 | 0.0707 | -0.153 | -0.2992
4 | 01:30 | 270 | 0.3116 | -0.2582 | 0.2582 | Optimal | 1.0982 | 0.3453 | 0.0707 | -0.0337 | -0.3289
4 | 01:30 | 300 | 0.4756 | -0.2142 | 0.4233 | Optimal | 1.0785 | 0.3453 | 0.0707 | 0.1303 | -0.2849
4 | 01:30 | 330 | 0.5957 | -0.0942 | 0.563 | Optimal | 1.0485 | 0.3453 | 0.0707 | 0.2504 | -0.1649
5 | 02:00 | 0 | 0.6293 | 0.0555 | 0.6293 | Optimal | 1.0298 | 0.3146 | 0.0643 | 0.3147 | -0.0088
5 | 02:00 | 30 | 0.5809 | 0.2273 | 0.6167 | Optimal | 1.0131 | 0.3146 | 0.0643 | 0.2663 | 0.163
5 | 02:00 | 60 | 0.4653 | 0.344 | 0.5306 | Optimal | 1.009 | 0.3146 | 0.0643 | 0.1507 | 0.2797
5 | 02:00 | 90 | 0.3084 | 0.3851 | 0.3851 | Optimal | 1.0134 | 0.3146 | 0.0643 | -0.0062 | 0.3208
5 | 02:00 | 120 | 0.1734 | 0.3526 | 0.2186 | Optimal | 1.026 | 0.3146 | 0.0643 | -0.1412 | 0.2883
5 | 02:00 | 150 | 0.1693 | 0.35 | 0.0284 | Optimal | 1.0281 | 0.3146 | 0.0643 | -0.1453 | 0.2857
5 | 02:00 | 180 | 0.1672 | -0.1886 | -0.1672 | Optimal | 1.1 | 0.3146 | 0.0643 | -0.1474 | -0.2529
5 | 02:00 | 210 | 0.1762 | -0.2231 | -0.0411 | Optimal | 1.1 | 0.3146 | 0.0643 | -0.1384 | -0.2874
5 | 02:00 | 240 | 0.1915 | -0.2337 | 0.1067 | Optimal | 1.1 | 0.3146 | 0.0643 | -0.1231 | -0.298
5 | 02:00 | 270 | 0.3028 | -0.2601 | 0.2601 | Optimal | 1.0974 | 0.3146 | 0.0643 | -0.0118 | -0.3244
5 | 02:00 | 300 | 0.4667 | -0.2161 | 0.4205 | Optimal | 1.0791 | 0.3146 | 0.0643 | 0.1521 | -0.2804
5 | 02:00 | 330 | 0.5867 | -0.0963 | 0.5562 | Optimal | 1.0491 | 0.3146 | 0.0643 | 0.2721 | -0.1606
6 | 02:30 | 0 | 0.6328 | 0.055 | 0.6328 | Optimal | 1.0298 | 0.3055 | 0.0625 | 0.3273 | -0.0075
6 | 02:30 | 30 | 0.5845 | 0.2275 | 0.62 | Optimal | 1.0138 | 0.3055 | 0.0625 | 0.279 | 0.165
6 | 02:30 | 60 | 0.4671 | 0.3456 | 0.5328 | Optimal | 1.0098 | 0.3055 | 0.0625 | 0.1616 | 0.2831
6 | 02:30 | 90 | 0.3122 | 0.3858 | 0.3858 | Optimal | 1.0141 | 0.3055 | 0.0625 | 0.0067 | 0.3233
6 | 02:30 | 120 | 0.1862 | 0.3571 | 0.2161 | Optimal | 1.0232 | 0.3055 | 0.0625 | -0.1193 | 0.2946
6 | 02:30 | 150 | 0.1838 | 0.3556 | 0.0186 | Optimal | 1.0242 | 0.3055 | 0.0625 | -0.1217 | 0.2931
6 | 02:30 | 180 | 0.1816 | -0.1997 | -0.1816 | Optimal | 1.1 | 0.3055 | 0.0625 | -0.1239 | -0.2622
6 | 02:30 | 210 | 0.1899 | -0.2288 | -0.05 | Optimal | 1.1 | 0.3055 | 0.0625 | -0.1156 | -0.2913
6 | 02:30 | 240 | 0.1993 | -0.2353 | 0.1041 | Optimal | 1.1 | 0.3055 | 0.0625 | -0.1062 | -0.2978
6 | 02:30 | 270 | 0.3066 | -0.2593 | 0.2593 | Optimal | 1.0961 | 0.3055 | 0.0625 | 0.0011 | -0.3218
6 | 02:30 | 300 | 0.4705 | -0.2153 | 0.4217 | Optimal | 1.0784 | 0.3055 | 0.0625 | 0.165 | -0.2778
6 | 02:30 | 330 | 0.5905 | -0.0954 | 0.5591 | Optimal | 1.0492 | 0.3055 | 0.0625 | 0.285 | -0.1579
7 | 03:00 | 0 | 0.636 | 0.0577 | 0.636 | Optimal | 1.0294 | 0.3093 | 0.0632 | 0.3267 | -0.0055
7 | 03:00 | 30 | 0.5875 | 0.2294 | 0.6235 | Optimal | 1.0125 | 0.3093 | 0.0632 | 0.2782 | 0.1662
7 | 03:00 | 60 | 0.4724 | 0.3459 | 0.5357 | Optimal | 1.0083 | 0.3093 | 0.0632 | 0.1631 | 0.2827
7 | 03:00 | 90 | 0.3152 | 0.3871 | 0.3871 | Optimal | 1.0128 | 0.3093 | 0.0632 | 0.0059 | 0.3239
7 | 03:00 | 120 | 0.1996 | 0.3624 | 0.214 | Optimal | 1.0193 | 0.3093 | 0.0632 | -0.1097 | 0.2992
7 | 03:00 | 150 | 0.1982 | 0.3615 | 0.0091 | Optimal | 1.0194 | 0.3093 | 0.0632 | -0.1111 | 0.2983
7 | 03:00 | 180 | 0.1958 | -0.2016 | -0.1958 | Optimal | 1.1 | 0.3093 | 0.0632 | -0.1135 | -0.2648
7 | 03:00 | 210 | 0.2031 | -0.231 | -0.0604 | Optimal | 1.1 | 0.3093 | 0.0632 | -0.1062 | -0.2942
7 | 03:00 | 240 | 0.211 | -0.2363 | 0.0992 | Optimal | 1.1 | 0.3093 | 0.0632 | -0.0983 | -0.2995
7 | 03:00 | 270 | 0.3094 | -0.258 | 0.258 | Optimal | 1.0982 | 0.3093 | 0.0632 | 0.0001 | -0.3212
7 | 03:00 | 300 | 0.4733 | -0.214 | 0.422 | Optimal | 1.079 | 0.3093 | 0.0632 | 0.164 | -0.2772
7 | 03:00 | 330 | 0.5934 | -0.0941 | 0.5609 | Optimal | 1.0488 | 0.3093 | 0.0632 | 0.2841 | -0.1573
8 | 03:30 | 0 | 0.5677 | 0.0512 | 0.5677 | Optimal | 1.0305 | 0.3123 | 0.0645 | 0.2554 | -0.0133
8 | 03:30 | 30 | 0.5191 | 0.2241 | 0.5616 | Optimal | 1.0149 | 0.3123 | 0.0645 | 0.2068 | 0.1596
8 | 03:30 | 60 | 0.4039 | 0.3407 | 0.497 | Optimal | 1.0107 | 0.3123 | 0.0645 | 0.0916 | 0.2762
8 | 03:30 | 90 | 0.2468 | 0.382 | 0.382 | Optimal | 1.0152 | 0.3123 | 0.0645 | -0.0655 | 0.3175
8 | 03:30 | 120 | 0.1424 | 0.361 | 0.2414 | Optimal | 1.0204 | 0.3123 | 0.0645 | -0.1699 | 0.2965
8 | 03:30 | 150 | 0.1414 | 0.3604 | 0.0577 | Optimal | 1.0205 | 0.3123 | 0.0645 | -0.1709 | 0.2959
8 | 03:30 | 180 | 0.1394 | -0.2162 | -0.1394 | Optimal | 1.0999 | 0.3123 | 0.0645 | -0.1729 | -0.2807
8 | 03:30 | 210 | 0.1458 | -0.2395 | -0.0065 | Optimal | 1.1 | 0.3123 | 0.0645 | -0.1665 | -0.304
8 | 03:30 | 240 | 0.1533 | -0.2446 | 0.1352 | Optimal | 1.1 | 0.3123 | 0.0645 | -0.159 | -0.3091
8 | 03:30 | 270 | 0.242 | -0.2634 | 0.2634 | Optimal | 1.0995 | 0.3123 | 0.0645 | -0.0703 | -0.3279
8 | 03:30 | 300 | 0.4055 | -0.2195 | 0.3929 | Optimal | 1.0795 | 0.3123 | 0.0645 | 0.0932 | -0.284
8 | 03:30 | 330 | 0.5252 | -0.0998 | 0.5048 | Optimal | 1.0499 | 0.3123 | 0.0645 | 0.2129 | -0.1643
9 | 04:00 | 0 | 0.4081 | 0.0588 | 0.4081 | Optimal | 1.0312 | 0.2443 | 0.0593 | 0.1638 | -0.0005
9 | 04:00 | 30 | 0.3607 | 0.2255 | 0.4251 | Optimal | 1.0162 | 0.2443 | 0.0593 | 0.1164 | 0.1662
9 | 04:00 | 60 | 0.2456 | 0.3421 | 0.419 | Optimal | 1.0123 | 0.2443 | 0.0593 | 0.0013 | 0.2828
9 | 04:00 | 90 | 0.0862 | 0.3843 | 0.3843 | Optimal | 1.0167 | 0.2443 | 0.0593 | -0.1581 | 0.325
9 | 04:00 | 120 | -0.0107 | 0.3656 | 0.322 | Optimal | 1.0234 | 0.2443 | 0.0593 | -0.255 | 0.3063
9 | 04:00 | 150 | -0.0116 | 0.3651 | 0.1926 | Optimal | 1.0235 | 0.2443 | 0.0593 | -0.2559 | 0.3058
9 | 04:00 | 180 | -0.0131 | -0.2082 | 0.0131 | Optimal | 1.1 | 0.2443 | 0.0593 | -0.2574 | -0.2675
9 | 04:00 | 210 | -0.0059 | -0.2385 | 0.1243 | Optimal | 1.1 | 0.2443 | 0.0593 | -0.2502 | -0.2978
9 | 04:00 | 240 | 0.0026 | -0.2441 | 0.2101 | Optimal | 1.1 | 0.2443 | 0.0593 | -0.2417 | -0.3034
9 | 04:00 | 270 | 0.0839 | -0.262 | 0.262 | Optimal | 1.1 | 0.2443 | 0.0593 | -0.1604 | -0.3213
9 | 04:00 | 300 | 0.2455 | -0.2184 | 0.3119 | Optimal | 1.0814 | 0.2443 | 0.0593 | 0.0012 | -0.2777
9 | 04:00 | 330 | 0.3649 | -0.099 | 0.3655 | Optimal | 1.051 | 0.2443 | 0.0593 | 0.1206 | -0.1583
10 | 04:30 | 0 | 0.1815 | 0.059 | 0.1815 | Optimal | 1.0327 | 0.0846 | 0.0612 | 0.0969 | -0.0022
10 | 04:30 | 30 | 0.1359 | 0.2219 | 0.2287 | Optimal | 1.0158 | 0.0846 | 0.0612 | 0.0513 | 0.1607
10 | 04:30 | 60 | 0.0191 | 0.3395 | 0.3036 | Optimal | 1.0131 | 0.0846 | 0.0612 | -0.0655 | 0.2783
10 | 04:30 | 90 | -0.1408 | 0.3822 | 0.3822 | Optimal | 1.0176 | 0.0846 | 0.0612 | -0.2254 | 0.321
10 | 04:30 | 120 | -0.2406 | 0.3623 | 0.4341 | Optimal | 1.0286 | 0.0846 | 0.0612 | -0.3252 | 0.3011
10 | 04:30 | 150 | -0.2423 | 0.3613 | 0.3904 | Optimal | 1.0289 | 0.0846 | 0.0612 | -0.3269 | 0.3001
10 | 04:30 | 180 | -0.2438 | 0.1505 | 0.2438 | Optimal | 1.1 | 0.0846 | 0.0612 | -0.3284 | 0.0893
10 | 04:30 | 210 | -0.2325 | -0.2319 | 0.3173 | Optimal | 1.1 | 0.0846 | 0.0612 | -0.3171 | -0.2931
10 | 04:30 | 240 | -0.2198 | -0.2428 | 0.3201 | Optimal | 1.1 | 0.0846 | 0.0612 | -0.3044 | -0.304
10 | 04:30 | 270 | -0.1347 | -0.2648 | 0.2648 | Optimal | 1.1 | 0.0846 | 0.0612 | -0.2193 | -0.326
10 | 04:30 | 300 | 0.0195 | -0.222 | 0.202 | Optimal | 1.0845 | 0.0846 | 0.0612 | -0.0651 | -0.2832
10 | 04:30 | 330 | 0.138 | -0.1034 | 0.1712 | Optimal | 1.0538 | 0.0846 | 0.0612 | 0.0534 | -0.1646
11 | 05:00 | 0 | -0.0594 | 0.0621 | -0.0594 | Optimal | 1.0347 | -0.1413 | 0.0585 | 0.0819 | 0.0036
11 | 05:00 | 30 | -0.1039 | 0.226 | 0.023 | Optimal | 1.0183 | -0.1413 | 0.0585 | 0.0374 | 0.1675
11 | 05:00 | 60 | -0.2218 | 0.3444 | 0.1874 | Optimal | 1.0169 | -0.1413 | 0.0585 | -0.0805 | 0.2859
11 | 05:00 | 90 | -0.3821 | 0.3874 | 0.3874 | Optimal | 1.0216 | -0.1413 | 0.0585 | -0.2408 | 0.3289
11 | 05:00 | 120 | -0.4952 | 0.3629 | 0.5619 | Optimal | 1.0394 | -0.1413 | 0.0585 | -0.3539 | 0.3044
11 | 05:00 | 150 | -0.501 | 0.359 | 0.6134 | Optimal | 1.0432 | -0.1413 | 0.0585 | -0.3597 | 0.3005
11 | 05:00 | 180 | -0.5033 | 0.1755 | 0.5033 | Optimal | 1.1 | -0.1413 | 0.0585 | -0.362 | 0.117
11 | 05:00 | 210 | -0.4825 | -0.2058 | 0.5208 | Optimal | 1.1 | -0.1413 | 0.0585 | -0.3412 | -0.2643
11 | 05:00 | 240 | -0.4456 | -0.2401 | 0.4307 | Optimal | 1.1 | -0.1413 | 0.0585 | -0.3043 | -0.2986
11 | 05:00 | 270 | -0.3692 | -0.2604 | 0.2604 | Optimal | 1.1 | -0.1413 | 0.0585 | -0.2279 | -0.3189
11 | 05:00 | 300 | -0.2208 | -0.2185 | 0.0788 | Optimal | 1.0839 | -0.1413 | 0.0585 | -0.0795 | -0.277
11 | 05:00 | 330 | -0.1029 | -0.1005 | -0.0389 | Optimal | 1.0549 | -0.1413 | 0.0585 | 0.0384 | -0.159
12 | 05:30 | 0 | -0.3256 | 0.0657 | -0.3256 | Optimal | 1.0366 | -0.3813 | 0.0631 | 0.0557 | 0.0026
12 | 05:30 | 30 | -0.3697 | 0.2308 | -0.2048 | Optimal | 1.0191 | -0.3813 | 0.0631 | 0.0116 | 0.1677
12 | 05:30 | 60 | -0.489 | 0.3502 | 0.0588 | Optimal | 1.0177 | -0.3813 | 0.0631 | -0.1077 | 0.2871
12 | 05:30 | 90 | -0.6487 | 0.3932 | 0.3932 | Optimal | 1.0248 | -0.3813 | 0.0631 | -0.2674 | 0.3301
12 | 05:30 | 120 | -0.779 | 0.362 | 0.703 | Optimal | 1.0512 | -0.3813 | 0.0631 | -0.3977 | 0.2989
12 | 05:30 | 150 | -0.7999 | 0.3461 | 0.8657 | Optimal | 1.0654 | -0.3813 | 0.0631 | -0.4186 | 0.283
12 | 05:30 | 180 | -0.8027 | 0.184 | 0.8027 | Optimal | 1.1 | -0.3813 | 0.0631 | -0.4214 | 0.1209
12 | 05:30 | 210 | -0.7765 | -0.153 | 0.749 | Optimal | 1.1 | -0.3813 | 0.0631 | -0.3952 | -0.2161
12 | 05:30 | 240 | -0.7012 | -0.2307 | 0.5504 | Optimal | 1.1 | -0.3813 | 0.0631 | -0.3199 | -0.2938
12 | 05:30 | 270 | -0.6183 | -0.2546 | 0.2546 | Optimal | 1.1 | -0.3813 | 0.0631 | -0.237 | -0.3177
12 | 05:30 | 300 | -0.4862 | -0.2146 | -0.0572 | Optimal | 1.0879 | -0.3813 | 0.0631 | -0.1049 | -0.2777
12 | 05:30 | 330 | -0.3692 | -0.0974 | -0.271 | Optimal | 1.057 | -0.3813 | 0.0631 | 0.0121 | -0.1605
13 | 06:00 | 0 | -0.5701 | 0.0741 | -0.5701 | Optimal | 1.039 | -0.6465 | 0.0681 | 0.0764 | 0.006
13 | 06:00 | 30 | -0.6145 | 0.2415 | -0.4114 | Optimal | 1.0218 | -0.6465 | 0.0681 | 0.032 | 0.1734
13 | 06:00 | 60 | -0.7343 | 0.3616 | -0.054 | Optimal | 1.0204 | -0.6465 | 0.0681 | -0.0878 | 0.2935
13 | 06:00 | 90 | -0.8932 | 0.4044 | 0.4044 | Optimal | 1.0312 | -0.6465 | 0.0681 | -0.2467 | 0.3363
13 | 06:00 | 120 | -1.0382 | 0.3672 | 0.837 | Optimal | 1.0607 | -0.6465 | 0.0681 | -0.3917 | 0.2991
13 | 06:00 | 150 | -1.0914 | 0.3195 | 1.1049 | Optimal | 1.0931 | -0.6465 | 0.0681 | -0.4449 | 0.2514
13 | 06:00 | 180 | -1.0983 | 0.1921 | 1.0983 | Optimal | 1.1 | -0.6465 | 0.0681 | -0.4518 | 0.124
13 | 06:00 | 210 | -1.0577 | -0.0854 | 0.9586 | Optimal | 1.1 | -0.6465 | 0.0681 | -0.4112 | -0.1535
13 | 06:00 | 240 | -0.9335 | -0.2141 | 0.6522 | Optimal | 1.1 | -0.6465 | 0.0681 | -0.287 | -0.2822
13 | 06:00 | 270 | -0.8429 | -0.2411 | 0.2411 | Optimal | 1.1 | -0.6465 | 0.0681 | -0.1964 | -0.3092
13 | 06:00 | 300 | -0.7298 | -0.2051 | -0.1873 | Optimal | 1.0929 | -0.6465 | 0.0681 | -0.0833 | -0.2732
13 | 06:00 | 330 | -0.6136 | -0.0886 | -0.4871 | Optimal | 1.0619 | -0.6465 | 0.0681 | 0.0329 | -0.1567
14 | 06:30 | 0 | -0.7611 | 0.0789 | -0.7611 | Optimal | 1.0403 | -0.8899 | 0.0787 | 0.1288 | 0.0002
14 | 06:30 | 30 | -0.7996 | 0.2679 | -0.5585 | Optimal | 1.0219 | -0.8899 | 0.0787 | 0.0903 | 0.1892
14 | 06:30 | 60 | -0.917 | 0.3848 | -0.1253 | Optimal | 1.0155 | -0.8899 | 0.0787 | -0.0271 | 0.3061
14 | 06:30 | 90 | -1.0754 | 0.4275 | 0.4275 | Optimal | 1.0338 | -0.8899 | 0.0787 | -0.1855 | 0.3488
14 | 06:30 | 120 | -1.2249 | 0.3883 | 0.9487 | Optimal | 1.0662 | -0.8899 | 0.0787 | -0.335 | 0.3096
14 | 06:30 | 150 | -1.3063 | 0.3117 | 1.2872 | Optimal | 1.1 | -0.8899 | 0.0787 | -0.4164 | 0.233
14 | 06:30 | 180 | -1.3249 | 0.2045 | 1.3249 | Optimal | 1.1 | -0.8899 | 0.0787 | -0.435 | 0.1258
14 | 06:30 | 210 | -1.2779 | -0.0035 | 1.1085 | Optimal | 1.1 | -0.8899 | 0.0787 | -0.388 | -0.0822
14 | 06:30 | 240 | -1.1045 | -0.1886 | 0.7156 | Optimal | 1.1 | -0.8899 | 0.0787 | -0.2146 | -0.2673
14 | 06:30 | 270 | -1.0124 | -0.2164 | 0.2164 | Optimal | 1.1 | -0.8899 | 0.0787 | -0.1225 | -0.2951
14 | 06:30 | 300 | -0.9117 | -0.1834 | -0.2971 | Optimal | 1.0962 | -0.8899 | 0.0787 | -0.0218 | -0.2621
14 | 06:30 | 330 | -0.7981 | -0.0702 | -0.6561 | Optimal | 1.0656 | -0.8899 | 0.0787 | 0.0918 | -0.1489
15 | 07:00 | 0 | -1.0116 | 0.0774 | -1.0116 | Optimal | 1.062 | -1.0713 | 0.1012 | 0.0597 | -0.0238
15 | 07:00 | 30 | -1.0374 | 0.3156 | -0.7406 | Optimal | 1.0234 | -1.0713 | 0.1012 | 0.0339 | 0.2144
15 | 07:00 | 60 | -1.1291 | 0.4042 | -0.2145 | Optimal | 1.0204 | -1.0713 | 0.1012 | -0.0578 | 0.303
15 | 07:00 | 90 | -1.2838 | 0.4453 | 0.4453 | Optimal | 1.0376 | -1.0713 | 0.1012 | -0.2125 | 0.3441
15 | 07:00 | 120 | -1.4362 | 0.405 | 1.0688 | Optimal | 1.0739 | -1.0713 | 0.1012 | -0.3649 | 0.3038
15 | 07:00 | 150 | -1.5229 | 0.323 | 1.4803 | Optimal | 1.1 | -1.0713 | 0.1012 | -0.4516 | 0.2218
15 | 07:00 | 180 | -1.5503 | 0.2124 | 1.5503 | Optimal | 1.1 | -1.0713 | 0.1012 | -0.479 | 0.1112
15 | 07:00 | 210 | -1.5025 | 0.0486 | 1.2769 | Optimal | 1.1 | -1.0713 | 0.1012 | -0.4312 | -0.0526
15 | 07:00 | 240 | -1.3016 | -0.1693 | 0.7975 | Optimal | 1.1 | -1.0713 | 0.1012 | -0.2303 | -0.2705
15 | 07:00 | 270 | -1.2104 | -0.1967 | 0.1967 | Optimal | 1.1 | -1.0713 | 0.1012 | -0.1391 | -0.2979
15 | 07:00 | 300 | -1.123 | -0.1683 | -0.4157 | Optimal | 1.0979 | -1.0713 | 0.1012 | -0.0517 | -0.2695
15 | 07:00 | 330 | -1.0357 | -0.084 | -0.8549 | Optimal | 1.0754 | -1.0713 | 0.1012 | 0.0356 | -0.1852
16 | 07:30 | 0 | -1.2052 | 0.08 | -1.2052 | Optimal | 1.0967 | -1.2792 | 0.1185 | 0.074 | -0.0385
16 | 07:30 | 30 | -1.2235 | 0.3954 | -0.8618 | Optimal | 1.028 | -1.2792 | 0.1185 | 0.0557 | 0.2769
16 | 07:30 | 60 | -1.277 | 0.4457 | -0.2525 | Optimal | 1.029 | -1.2792 | 0.1185 | 0.0022 | 0.3272
16 | 07:30 | 90 | -1.4036 | 0.4766 | 0.4766 | Optimal | 1.0418 | -1.2792 | 0.1185 | -0.1244 | 0.3581
16 | 07:30 | 120 | -1.5561 | 0.4362 | 1.1558 | Optimal | 1.0779 | -1.2792 | 0.1185 | -0.2769 | 0.3177
16 | 07:30 | 150 | -1.6376 | 0.3511 | 1.5938 | Optimal | 1.1 | -1.2792 | 0.1185 | -0.3584 | 0.2326
16 | 07:30 | 180 | -1.6686 | 0.2446 | 1.6686 | Optimal | 1.1 | -1.2792 | 0.1185 | -0.3894 | 0.1261
16 | 07:30 | 210 | -1.6226 | 0.0932 | 1.3586 | Optimal | 1.1 | -1.2792 | 0.1185 | -0.3434 | -0.0253
16 | 07:30 | 240 | -1.4062 | -0.1378 | 0.8224 | Optimal | 1.1 | -1.2792 | 0.1185 | -0.127 | -0.2563
16 | 07:30 | 270 | -1.3223 | -0.1625 | 0.1625 | Optimal | 1.1 | -1.2792 | 0.1185 | -0.0431 | -0.281
16 | 07:30 | 300 | -1.2709 | -0.1475 | -0.5077 | Optimal | 1.1 | -1.2792 | 0.1185 | 0.0083 | -0.266
16 | 07:30 | 330 | -1.2211 | -0.1 | -1.0075 | Optimal | 1.0896 | -1.2792 | 0.1185 | 0.0581 | -0.2185
17 | 08:00 | 0 | -1.3987 | 0.1209 | -1.3987 | Optimal | 1.1 | -1.399 | 0.1494 | 0.0003 | -0.0285
17 | 08:00 | 30 | -1.4173 | 0.4488 | -1.003 | Optimal | 1.0362 | -1.399 | 0.1494 | -0.0183 | 0.2994
17 | 08:00 | 60 | -1.4506 | 0.4805 | -0.3092 | Optimal | 1.0356 | -1.399 | 0.1494 | -0.0516 | 0.3311
17 | 08:00 | 90 | -1.545 | 0.5011 | 0.5011 | Optimal | 1.045 | -1.399 | 0.1494 | -0.146 | 0.3517
17 | 08:00 | 120 | -1.6891 | 0.4647 | 1.247 | Optimal | 1.0823 | -1.399 | 0.1494 | -0.2901 | 0.3153
17 | 08:00 | 150 | -1.7717 | 0.3742 | 1.7214 | Optimal | 1.1 | -1.399 | 0.1494 | -0.3727 | 0.2248
17 | 08:00 | 180 | -1.8061 | 0.2599 | 1.8061 | Optimal | 1.1 | -1.399 | 0.1494 | -0.4071 | 0.1105
17 | 08:00 | 210 | -1.7656 | 0.1399 | 1.4591 | Optimal | 1.1 | -1.399 | 0.1494 | -0.3666 | -0.0095
17 | 08:00 | 240 | -1.5289 | -0.1046 | 0.855 | Optimal | 1.1 | -1.399 | 0.1494 | -0.1299 | -0.254
17 | 08:00 | 270 | -1.4644 | -0.1261 | 0.1261 | Optimal | 1.1 | -1.399 | 0.1494 | -0.0654 | -0.2755
17 | 08:00 | 300 | -1.4323 | -0.1192 | -0.6129 | Optimal | 1.1 | -1.399 | 0.1494 | -0.0333 | -0.2686
17 | 08:00 | 330 | -1.413 | -0.0995 | -1.1739 | Optimal | 1.1 | -1.399 | 0.1494 | -0.014 | -0.2489
18 | 08:30 | 0 | -1.6019 | 0.1667 | -1.6019 | Optimal | 1.1 | -1.5392 | 0.1733 | -0.0627 | -0.0066
18 | 08:30 | 30 | -1.617 | 0.4768 | -1.162 | Optimal | 1.0477 | -1.5392 | 0.1733 | -0.0778 | 0.3035
18 | 08:30 | 60 | -1.639 | 0.4979 | -0.3883 | Optimal | 1.0467 | -1.5392 | 0.1733 | -0.0998 | 0.3246
18 | 08:30 | 90 | -1.7135 | 0.5122 | 0.5122 | Optimal | 1.0512 | -1.5392 | 0.1733 | -0.1743 | 0.3389
18 | 08:30 | 120 | -1.8528 | 0.4776 | 1.34 | Optimal | 1.0864 | -1.5392 | 0.1733 | -0.3136 | 0.3043
18 | 08:30 | 150 | -1.9365 | 0.3859 | 1.87 | Optimal | 1.1 | -1.5392 | 0.1733 | -0.3973 | 0.2126
18 | 08:30 | 180 | -1.9716 | 0.2697 | 1.9716 | Optimal | 1.1 | -1.5392 | 0.1733 | -0.4324 | 0.0964
18 | 08:30 | 210 | -1.9374 | 0.1698 | 1.5929 | Optimal | 1.1 | -1.5392 | 0.1733 | -0.3982 | -0.0035
18 | 08:30 | 240 | -1.7004 | -0.0779 | 0.9176 | Optimal | 1.1 | -1.5392 | 0.1733 | -0.1612 | -0.2512
18 | 08:30 | 270 | -1.6485 | -0.0947 | 0.0947 | Optimal | 1.1 | -1.5392 | 0.1733 | -0.1093 | -0.268
18 | 08:30 | 300 | -1.6178 | -0.0892 | -0.7316 | Optimal | 1.1 | -1.5392 | 0.1733 | -0.0786 | -0.2625
18 | 08:30 | 330 | -1.6107 | -0.0826 | -1.3536 | Optimal | 1.1 | -1.5392 | 0.1733 | -0.0715 | -0.2559
19 | 09:00 | 0 | -1.7447 | 0.1942 | -1.7447 | Optimal | 1.1 | -1.7076 | 0.1842 | -0.0371 | 0.01
19 | 09:00 | 30 | -1.7591 | 0.5038 | -1.2715 | Optimal | 1.0549 | -1.7076 | 0.1842 | -0.0515 | 0.3196
19 | 09:00 | 60 | -1.7727 | 0.5159 | -0.4396 | Optimal | 1.0542 | -1.7076 | 0.1842 | -0.0651 | 0.3317
19 | 09:00 | 90 | -1.8356 | 0.5267 | 0.5267 | Optimal | 1.0575 | -1.7076 | 0.1842 | -0.128 | 0.3425
19 | 09:00 | 120 | -1.9667 | 0.4951 | 1.4122 | Optimal | 1.0873 | -1.7076 | 0.1842 | -0.2591 | 0.3109
19 | 09:00 | 150 | -2.052 | 0.4044 | 1.9793 | Optimal | 1.1 | -1.7076 | 0.1842 | -0.3444 | 0.2202
19 | 09:00 | 180 | -2.0897 | 0.2824 | 2.0897 | Optimal | 1.1 | -1.7076 | 0.1842 | -0.3821 | 0.0982
19 | 09:00 | 210 | -2.0581 | 0.1871 | 1.6888 | Optimal | 1.1 | -1.7076 | 0.1842 | -0.3505 | 0.0029
19 | 09:00 | 240 | -1.8299 | -0.0492 | 0.9576 | Optimal | 1.1 | -1.7076 | 0.1842 | -0.1223 | -0.2334
19 | 09:00 | 270 | -1.7843 | -0.0641 | 0.0641 | Optimal | 1.1 | -1.7076 | 0.1842 | -0.0767 | -0.2483
19 | 09:00 | 300 | -1.7551 | -0.06 | -0.8256 | Optimal | 1.1 | -1.7076 | 0.1842 | -0.0475 | -0.2442
19 | 09:00 | 330 | -1.7529 | -0.0579 | -1.4891 | Optimal | 1.1 | -1.7076 | 0.1842 | -0.0453 | -0.2421
20 | 09:30 | 0 | -1.9368 | 0.2171 | -1.9368 | Optimal | 1.1 | -1.8297 | 0.1985 | -0.1071 | 0.0186
20 | 09:30 | 30 | -1.9515 | 0.5111 | -1.4345 | Optimal | 1.0581 | -1.8297 | 0.1985 | -0.1218 | 0.3126
20 | 09:30 | 60 | -1.9592 | 0.5183 | -0.5308 | Optimal | 1.0585 | -1.8297 | 0.1985 | -0.1295 | 0.3198
20 | 09:30 | 90 | -2.0155 | 0.5266 | 0.5266 | Optimal | 1.0607 | -1.8297 | 0.1985 | -0.1858 | 0.3281
20 | 09:30 | 120 | -2.1263 | 0.5025 | 1.4983 | Optimal | 1.0861 | -1.8297 | 0.1985 | -0.2966 | 0.304
20 | 09:30 | 150 | -2.2239 | 0.3984 | 2.1252 | Optimal | 1.1 | -1.8297 | 0.1985 | -0.3942 | 0.1999
20 | 09:30 | 180 | -2.2601 | 0.2789 | 2.2601 | Optimal | 1.1 | -1.8297 | 0.1985 | -0.4304 | 0.0804
20 | 09:30 | 210 | -2.2297 | 0.1958 | 1.8331 | Optimal | 1.1 | -1.8297 | 0.1985 | -0.4 | -0.0027
20 | 09:30 | 240 | -2.0115 | -0.0287 | 1.0307 | Optimal | 1.1 | -1.8297 | 0.1985 | -0.1818 | -0.2272
20 | 09:30 | 270 | -1.9615 | -0.0428 | 0.0428 | Optimal | 1.1 | -1.8297 | 0.1985 | -0.1318 | -0.2413
20 | 09:30 | 300 | -1.9459 | -0.0404 | -0.938 | Optimal | 1.1 | -1.8297 | 0.1985 | -0.1162 | -0.2389
20 | 09:30 | 330 | -1.9454 | -0.0399 | -1.6648 | Optimal | 1.1 | -1.8297 | 0.1985 | -0.1157 | -0.2384
21 | 10:00 | 0 | -2.0919 | 0.2454 | -2.0919 | Optimal | 1.1 | -2.0084 | 0.1978 | -0.0835 | 0.0476
21 | 10:00 | 30 | -2.1075 | 0.516 | -1.5671 | Optimal | 1.06 | -2.0084 | 0.1978 | -0.0991 | 0.3182
21 | 10:00 | 60 | -2.1131 | 0.5211 | -0.6053 | Optimal | 1.0604 | -2.0084 | 0.1978 | -0.1047 | 0.3233
21 | 10:00 | 90 | -2.1619 | 0.5272 | 0.5272 | Optimal | 1.0633 | -2.0084 | 0.1978 | -0.1535 | 0.3294
21 | 10:00 | 120 | -2.2578 | 0.5069 | 1.5679 | Optimal | 1.0917 | -2.0084 | 0.1978 | -0.2494 | 0.3091
21 | 10:00 | 150 | -2.3591 | 0.3995 | 2.2428 | Optimal | 1.1 | -2.0084 | 0.1978 | -0.3507 | 0.2017
21 | 10:00 | 180 | -2.3956 | 0.2806 | 2.3956 | Optimal | 1.1 | -2.0084 | 0.1978 | -0.3872 | 0.0828
21 | 10:00 | 210 | -2.3739 | 0.2154 | 1.9482 | Optimal | 1.1 | -2.0084 | 0.1978 | -0.3655 | 0.0176
21 | 10:00 | 240 | -2.1623 | -0.0034 | 1.0841 | Optimal | 1.1 | -2.0084 | 0.1978 | -0.1539 | -0.2012
21 | 10:00 | 270 | -2.1143 | -0.0163 | 0.0163 | Optimal | 1.1 | -2.0084 | 0.1978 | -0.1059 | -0.2141
21 | 10:00 | 300 | -2.1012 | -0.0147 | -1.0379 | Optimal | 1.1 | -2.0084 | 0.1978 | -0.0928 | -0.2125
21 | 10:00 | 330 | -2.1008 | -0.0144 | -1.8122 | Optimal | 1.1 | -2.0084 | 0.1978 | -0.0924 | -0.2122
22 | 10:30 | 0 | -2.182 | 0.2528 | -2.182 | Optimal | 1.1 | -2.1535 | 0.1977 | -0.0285 | 0.0551
22 | 10:30 | 30 | -2.1974 | 0.5193 | -1.6433 | Optimal | 1.0645 | -2.1535 | 0.1977 | -0.0439 | 0.3216
22 | 10:30 | 60 | -2.202 | 0.5236 | -0.6476 | Optimal | 1.0649 | -2.1535 | 0.1977 | -0.0485 | 0.3259
22 | 10:30 | 90 | -2.2462 | 0.5282 | 0.5282 | Optimal | 1.0682 | -2.1535 | 0.1977 | -0.0927 | 0.3305
22 | 10:30 | 120 | -2.3434 | 0.5073 | 1.6111 | Optimal | 1.0906 | -2.1535 | 0.1977 | -0.1899 | 0.3096
22 | 10:30 | 150 | -2.4451 | 0.3995 | 2.3173 | Optimal | 1.1 | -2.1535 | 0.1977 | -0.2916 | 0.2018
22 | 10:30 | 180 | -2.4799 | 0.2818 | 2.4799 | Optimal | 1.1 | -2.1535 | 0.1977 | -0.3264 | 0.0841
22 | 10:30 | 210 | -2.4623 | 0.227 | 2.019 | Optimal | 1.1 | -2.1535 | 0.1977 | -0.3088 | 0.0293
22 | 10:30 | 240 | -2.2563 | 0.0086 | 1.1207 | Optimal | 1.1 | -2.1535 | 0.1977 | -0.1028 | -0.1891
22 | 10:30 | 270 | -2.2 | -0.0067 | 0.0067 | Optimal | 1.1 | -2.1535 | 0.1977 | -0.0465 | -0.2044
22 | 10:30 | 300 | -2.1916 | -0.0057 | -1.0908 | Optimal | 1.1 | -2.1535 | 0.1977 | -0.0381 | -0.2034
22 | 10:30 | 330 | -2.1913 | -0.0055 | -1.895 | Optimal | 1.1 | -2.1535 | 0.1977 | -0.0378 | -0.2032
23 | 11:00 | 0 | -2.1943 | 0.2633 | -2.1943 | Optimal | 1.1 | -2.2382 | 0.1988 | 0.0439 | 0.0645
23 | 11:00 | 30 | -2.2089 | 0.5277 | -1.6491 | Optimal | 1.0583 | -2.2382 | 0.1988 | 0.0293 | 0.3289
23 | 11:00 | 60 | -2.2122 | 0.5306 | -0.6466 | Optimal | 1.059 | -2.2382 | 0.1988 | 0.026 | 0.3318
23 | 11:00 | 90 | -2.2554 | 0.535 | 0.535 | Optimal | 1.0621 | -2.2382 | 0.1988 | -0.0172 | 0.3362
23 | 11:00 | 120 | -2.3519 | 0.5147 | 1.6217 | Optimal | 1.0894 | -2.2382 | 0.1988 | -0.1137 | 0.3159
23 | 11:00 | 150 | -2.455 | 0.4074 | 2.3298 | Optimal | 1.1 | -2.2382 | 0.1988 | -0.2168 | 0.2086
23 | 11:00 | 180 | -2.4908 | 0.2878 | 2.4908 | Optimal | 1.1 | -2.2382 | 0.1988 | -0.2526 | 0.089
23 | 11:00 | 210 | -2.4703 | 0.2276 | 2.0255 | Optimal | 1.1 | -2.2382 | 0.1988 | -0.2321 | 0.0288
23 | 11:00 | 240 | -2.2595 | 0.0087 | 1.1222 | Optimal | 1.1 | -2.2382 | 0.1988 | -0.0213 | -0.1901
23 | 11:00 | 270 | -2.2095 | -0.0063 | 0.0063 | Optimal | 1.1 | -2.2382 | 0.1988 | 0.0287 | -0.2051
23 | 11:00 | 300 | -2.2034 | -0.0055 | -1.0969 | Optimal | 1.1 | -2.2382 | 0.1988 | 0.0348 | -0.2043
23 | 11:00 | 330 | -2.2034 | -0.0055 | -1.9055 | Optimal | 1.1 | -2.2382 | 0.1988 | 0.0348 | -0.2043
24 | 11:30 | 0 | -2.2023 | 0.2622 | -2.2023 | Optimal | 1.1 | -2.2476 | 0.2056 | 0.0453 | 0.0566
24 | 11:30 | 30 | -2.2181 | 0.5283 | -1.6568 | Optimal | 1.0589 | -2.2476 | 0.2056 | 0.0295 | 0.3227
24 | 11:30 | 60 | -2.2227 | 0.5326 | -0.6501 | Optimal | 1.0596 | -2.2476 | 0.2056 | 0.0249 | 0.327
24 | 11:30 | 90 | -2.2673 | 0.5374 | 0.5374 | Optimal | 1.0657 | -2.2476 | 0.2056 | -0.0197 | 0.3318
24 | 11:30 | 120 | -2.3534 | 0.5184 | 1.6256 | Optimal | 1.1 | -2.2476 | 0.2056 | -0.1058 | 0.3128
24 | 11:30 | 150 | -2.4545 | 0.4106 | 2.331 | Optimal | 1.1 | -2.2476 | 0.2056 | -0.2069 | 0.205
24 | 11:30 | 180 | -2.492 | 0.2903 | 2.492 | Optimal | 1.1 | -2.2476 | 0.2056 | -0.2444 | 0.0847
24 | 11:30 | 210 | -2.4748 | 0.2379 | 2.0243 | Optimal | 1.1 | -2.2476 | 0.2056 | -0.2272 | 0.0323
24 | 11:30 | 240 | -2.269 | 0.0201 | 1.1171 | Optimal | 1.1 | -2.2476 | 0.2056 | -0.0214 | -0.1855
24 | 11:30 | 270 | -2.2187 | 0.0051 | -0.0051 | Optimal | 1.1 | -2.2476 | 0.2056 | 0.0289 | -0.2005
24 | 11:30 | 300 | -2.2114 | 0.0055 | -1.1104 | Optimal | 1.1 | -2.2476 | 0.2056 | 0.0362 | -0.2001
24 | 11:30 | 330 | -2.2113 | 0.0055 | -1.9178 | Optimal | 1.1 | -2.2476 | 0.2056 | 0.0363 | -0.2001
25 | 12:00 | 0 | -2.259 | 0.2471 | -2.259 | Optimal | 1.1 | -2.2582 | 0.2073 | -0.0008 | 0.0398
25 | 12:00 | 30 | -2.274 | 0.515 | -1.7119 | Optimal | 1.0553 | -2.2582 | 0.2073 | -0.0158 | 0.3077
25 | 12:00 | 60 | -2.2778 | 0.5183 | -0.6901 | Optimal | 1.0559 | -2.2582 | 0.2073 | -0.0196 | 0.311
25 | 12:00 | 90 | -2.3207 | 0.5227 | 0.5227 | Optimal | 1.0641 | -2.2582 | 0.2073 | -0.0625 | 0.3154
25 | 12:00 | 120 | -2.4081 | 0.5033 | 1.6399 | Optimal | 1.0992 | -2.2582 | 0.2073 | -0.1499 | 0.296
25 | 12:00 | 150 | -2.5088 | 0.396 | 2.3707 | Optimal | 1.1 | -2.2582 | 0.2073 | -0.2506 | 0.1887
25 | 12:00 | 180 | -2.5456 | 0.2774 | 2.5456 | Optimal | 1.1 | -2.2582 | 0.2073 | -0.2874 | 0.0701
25 | 12:00 | 210 | -2.5269 | 0.2235 | 2.0766 | Optimal | 1.1 | -2.2582 | 0.2073 | -0.2687 | 0.0162
25 | 12:00 | 240 | -2.3268 | 0.0122 | 1.1529 | Optimal | 1.1 | -2.2582 | 0.2073 | -0.0686 | -0.1951
25 | 12:00 | 270 | -2.2763 | -0.0009 | 0.0009 | Optimal | 1.1 | -2.2582 | 0.2073 | -0.0181 | -0.2082
25 | 12:00 | 300 | -2.2673 | -0.0003 | -1.1334 | Optimal | 1.1 | -2.2582 | 0.2073 | -0.0091 | -0.2076
25 | 12:00 | 330 | -2.2673 | -0.0003 | -1.9634 | Optimal | 1.1 | -2.2582 | 0.2073 | -0.0091 | -0.2076
26 | 12:30 | 0 | -2.1733 | 0.2449 | -2.1733 | Optimal | 1.1 | -2.3117 | 0.1926 | 0.1384 | 0.0523
26 | 12:30 | 30 | -2.1883 | 0.515 | -1.6376 | Optimal | 1.0604 | -2.3117 | 0.1926 | 0.1234 | 0.3224
26 | 12:30 | 60 | -2.1907 | 0.5172 | -0.6475 | Optimal | 1.061 | -2.3117 | 0.1926 | 0.121 | 0.3246
26 | 12:30 | 90 | -2.2332 | 0.5215 | 0.5215 | Optimal | 1.065 | -2.3117 | 0.1926 | 0.0785 | 0.3289
26 | 12:30 | 120 | -2.3327 | 0.5003 | 1.5996 | Optimal | 1.1 | -2.3117 | 0.1926 | -0.021 | 0.3077
26 | 12:30 | 150 | -2.4318 | 0.3941 | 2.303 | Optimal | 1.1 | -2.3117 | 0.1926 | -0.1201 | 0.2015
26 | 12:30 | 180 | -2.4667 | 0.2775 | 2.4667 | Optimal | 1.1 | -2.3117 | 0.1926 | -0.155 | 0.0849
26 | 12:30 | 210 | -2.444 | 0.2162 | 2.0085 | Optimal | 1.1 | -2.3117 | 0.1926 | -0.1323 | 0.0236
26 | 12:30 | 240 | -2.2511 | 0.0095 | 1.1173 | Optimal | 1.1 | -2.3117 | 0.1926 | 0.0606 | -0.1831
26 | 12:30 | 270 | -2.1928 | -0.0052 | 0.0052 | Optimal | 1.1 | -2.3117 | 0.1926 | 0.1189 | -0.1978
26 | 12:30 | 300 | -2.1821 | -0.0042 | -1.0874 | Optimal | 1.1 | -2.3117 | 0.1926 | 0.1296 | -0.1968
26 | 12:30 | 330 | -2.182 | -0.0042 | -1.8876 | Optimal | 1.1 | -2.3117 | 0.1926 | 0.1297 | -0.1968
27 | 13:00 | 0 | -2.1207 | 0.2264 | -2.1207 | Optimal | 1.1 | -2.2251 | 0.1918 | 0.1044 | 0.0346
27 | 13:00 | 30 | -2.1353 | 0.5012 | -1.5986 | Optimal | 1.0526 | -2.2251 | 0.1918 | 0.0898 | 0.3094
27 | 13:00 | 60 | -2.1383 | 0.5038 | -0.6329 | Optimal | 1.0532 | -2.2251 | 0.1918 | 0.0868 | 0.312
27 | 13:00 | 90 | -2.1803 | 0.5079 | 0.5079 | Optimal | 1.062 | -2.2251 | 0.1918 | 0.0448 | 0.3161
27 | 13:00 | 120 | -2.2892 | 0.4848 | 1.5645 | Optimal | 1.1 | -2.2251 | 0.1918 | -0.0641 | 0.293
27 | 13:00 | 150 | -2.3816 | 0.3865 | 2.2558 | Optimal | 1.1 | -2.2251 | 0.1918 | -0.1565 | 0.1947
27 | 13:00 | 180 | -2.4185 | 0.2631 | 2.4185 | Optimal | 1.1 | -2.2251 | 0.1918 | -0.1934 | 0.0713
27 | 13:00 | 210 | -2.3969 | 0.2048 | 1.9734 | Optimal | 1.1 | -2.2251 | 0.1918 | -0.1718 | 0.013
27 | 13:00 | 240 | -2.1877 | -0.0142 | 1.1061 | Optimal | 1.1 | -2.2251 | 0.1918 | 0.0374 | -0.206
27 | 13:00 | 270 | -2.1373 | -0.0279 | 0.0279 | Optimal | 1.1 | -2.2251 | 0.1918 | 0.0878 | -0.2197
27 | 13:00 | 300 | -2.1287 | -0.027 | -1.041 | Optimal | 1.1 | -2.2251 | 0.1918 | 0.0964 | -0.2188
27 | 13:00 | 330 | -2.1287 | -0.027 | -1.83 | Optimal | 1.1 | -2.2251 | 0.1918 | 0.0964 | -0.2188
28 | 13:30 | 0 | -1.996 | 0.2162 | -1.996 | Optimal | 1.1 | -2.172 | 0.1783 | 0.176 | 0.0379
28 | 13:30 | 30 | -2.0099 | 0.4984 | -1.4914 | Optimal | 1.0501 | -2.172 | 0.1783 | 0.1621 | 0.3201
28 | 13:30 | 60 | -2.0122 | 0.5005 | -0.5727 | Optimal | 1.0507 | -2.172 | 0.1783 | 0.1598 | 0.3222
28 | 13:30 | 90 | -2.053 | 0.5043 | 0.5043 | Optimal | 1.0537 | -2.172 | 0.1783 | 0.119 | 0.326
28 | 13:30 | 120 | -2.1648 | 0.4801 | 1.4981 | Optimal | 1.0897 | -2.172 | 0.1783 | 0.0072 | 0.3018
28 | 13:30 | 150 | -2.2626 | 0.376 | 2.1475 | Optimal | 1.1 | -2.172 | 0.1783 | -0.0906 | 0.1977
28 | 13:30 | 180 | -2.2979 | 0.2581 | 2.2979 | Optimal | 1.1 | -2.172 | 0.1783 | -0.1259 | 0.0798
28 | 13:30 | 210 | -2.2698 | 0.1839 | 1.8738 | Optimal | 1.1 | -2.172 | 0.1783 | -0.0978 | 0.0056
28 | 13:30 | 240 | -2.0626 | -0.03 | 1.0573 | Optimal | 1.1 | -2.172 | 0.1783 | 0.1094 | -0.2083
28 | 13:30 | 270 | -2.012 | -0.0437 | 0.0437 | Optimal | 1.1 | -2.172 | 0.1783 | 0.16 | -0.222
28 | 13:30 | 300 | -2.0039 | -0.0431 | -0.9646 | Optimal | 1.1 | -2.172 | 0.1783 | 0.1681 | -0.2214
28 | 13:30 | 330 | -2.0039 | -0.0431 | -1.7139 | Optimal | 1.1 | -2.172 | 0.1783 | 0.1681 | -0.2214
29 | 14:00 | 0 | -1.844 | 0.2122 | -1.844 | Optimal | 1.1 | -2.0454 | 0.1752 | 0.2014 | 0.037
29 | 14:00 | 30 | -1.8575 | 0.4926 | -1.3623 | Optimal | 1.0525 | -2.0454 | 0.1752 | 0.1879 | 0.3174
29 | 14:00 | 60 | -1.8588 | 0.4935 | -0.502 | Optimal | 1.0528 | -2.0454 | 0.1752 | 0.1866 | 0.3183
29 | 14:00 | 90 | -1.8987 | 0.4971 | 0.4971 | Optimal | 1.0562 | -2.0454 | 0.1752 | 0.1467 | 0.3219
29 | 14:00 | 120 | -2.0199 | 0.47 | 1.4169 | Optimal | 1.0885 | -2.0454 | 0.1752 | 0.0255 | 0.2948
29 | 14:00 | 150 | -2.1153 | 0.3678 | 2.0158 | Optimal | 1.1 | -2.0454 | 0.1752 | -0.0699 | 0.1926
29 | 14:00 | 180 | -2.15 | 0.2543 | 2.15 | Optimal | 1.1 | -2.0454 | 0.1752 | -0.1046 | 0.0791
29 | 14:00 | 210 | -2.1227 | 0.1726 | 1.752 | Optimal | 1.1 | -2.0454 | 0.1752 | -0.0773 | -0.0026
29 | 14:00 | 240 | -1.9133 | -0.0475 | 0.9978 | Optimal | 1.1 | -2.0454 | 0.1752 | 0.1321 | -0.2227
29 | 14:00 | 270 | -1.8614 | -0.0625 | 0.0625 | Optimal | 1.1 | -2.0454 | 0.1752 | 0.184 | -0.2377
29 | 14:00 | 300 | -1.8522 | -0.0618 | -0.8726 | Optimal | 1.1 | -2.0454 | 0.1752 | 0.1932 | -0.237
29 | 14:00 | 330 | -1.8522 | -0.0618 | -1.5732 | Optimal | 1.1 | -2.0454 | 0.1752 | 0.1932 | -0.237
30 | 14:30 | 0 | -1.6777 | 0.1838 | -1.6777 | Optimal | 1.1 | -1.8919 | 0.1684 | 0.2142 | 0.0154
30 | 14:30 | 30 | -1.6899 | 0.4896 | -1.2187 | Optimal | 1.0503 | -1.8919 | 0.1684 | 0.202 | 0.3212
30 | 14:30 | 60 | -1.6899 | 0.4896 | -0.421 | Optimal | 1.0503 | -1.8919 | 0.1684 | 0.202 | 0.3212
30 | 14:30 | 90 | -1.7287 | 0.4928 | 0.4928 | Optimal | 1.0538 | -1.8919 | 0.1684 | 0.1632 | 0.3244
30 | 14:30 | 120 | -1.864 | 0.46 | 1.3304 | Optimal | 1.0819 | -1.8919 | 0.1684 | 0.0279 | 0.2916
30 | 14:30 | 150 | -1.953 | 0.3694 | 1.8761 | Optimal | 1.1 | -1.8919 | 0.1684 | -0.0611 | 0.201
30 | 14:30 | 180 | -1.9896 | 0.2548 | 1.9896 | Optimal | 1.1 | -1.8919 | 0.1684 | -0.0977 | 0.0864
30 | 14:30 | 210 | -1.9571 | 0.1479 | 1.621 | Optimal | 1.1 | -1.8919 | 0.1684 | -0.0652 | -0.0205
30 | 14:30 | 240 | -1.7497 | -0.0681 | 0.9338 | Optimal | 1.1 | -1.8919 | 0.1684 | 0.1422 | -0.2365
30 | 14:30 | 270 | -1.6934 | -0.0848 | 0.0848 | Optimal | 1.1 | -1.8919 | 0.1684 | 0.1985 | -0.2532
30 | 14:30 | 300 | -1.6852 | -0.0842 | -0.7697 | Optimal | 1.1 | -1.8919 | 0.1684 | 0.2067 | -0.2526
30 | 14:30 | 330 | -1.6852 | -0.0842 | -1.4173 | Optimal | 1.1 | -1.8919 | 0.1684 | 0.2067 | -0.2526
31 | 15:00 | 0 | -1.4844 | 0.1808 | -1.4844 | Optimal | 1.1 | -1.723 | 0.1648 | 0.2386 | 0.016
31 | 15:00 | 30 | -1.4959 | 0.4814 | -1.0548 | Optimal | 1.0457 | -1.723 | 0.1648 | 0.2271 | 0.3166
31 | 15:00 | 60 | -1.4963 | 0.4817 | -0.331 | Optimal | 1.0457 | -1.723 | 0.1648 | 0.2267 | 0.3169
31 | 15:00 | 90 | -1.5354 | 0.4848 | 0.4848 | Optimal | 1.0486 | -1.723 | 0.1648 | 0.1876 | 0.32
31 | 15:00 | 120 | -1.6804 | 0.448 | 1.2282 | Optimal | 1.0807 | -1.723 | 0.1648 | 0.0426 | 0.2832
31 | 15:00 | 150 | -1.765 | 0.3612 | 1.7092 | Optimal | 1.1 | -1.723 | 0.1648 | -0.042 | 0.1964
31 | 15:00 | 180 | -1.8031 | 0.2416 | 1.8031 | Optimal | 1.1 | -1.723 | 0.1648 | -0.0801 | 0.0768
31 | 15:00 | 210 | -1.7685 | 0.1351 | 1.464 | Optimal | 1.1 | -1.723 | 0.1648 | -0.0455 | -0.0297
31 | 15:00 | 240 | -1.5546 | -0.0878 | 0.8534 | Optimal | 1.1 | -1.723 | 0.1648 | 0.1684 | -0.2526
31 | 15:00 | 270 | -1.5025 | -0.1055 | 0.1055 | Optimal | 1.1 | -1.723 | 0.1648 | 0.2205 | -0.2703
31 | 15:00 | 300 | -1.4915 | -0.1046 | -0.6552 | Optimal | 1.1 | -1.723 | 0.1648 | 0.2315 | -0.2694
31 | 15:00 | 330 | -1.4915 | -0.1046 | -1.2394 | Optimal | 1.1 | -1.723 | 0.1648 | 0.2315 | -0.2694
32 | 15:30 | 0 | -1.1769 | 0.1653 | -1.1769 | Optimal | 1.1 | -1.5298 | 0.1571 | 0.3529 | 0.0082
32 | 15:30 | 30 | -1.1865 | 0.4888 | -0.7832 | Optimal | 1.0397 | -1.5298 | 0.1571 | 0.3433 | 0.3317
32 | 15:30 | 60 | -1.1879 | 0.4902 | -0.1695 | Optimal | 1.0398 | -1.5298 | 0.1571 | 0.3419 | 0.3331
32 | 15:30 | 90 | -1.2237 | 0.4926 | 0.4926 | Optimal | 1.0432 | -1.5298 | 0.1571 | 0.3061 | 0.3355
32 | 15:30 | 120 | -1.3791 | 0.4509 | 1.08 | Optimal | 1.0723 | -1.5298 | 0.1571 | 0.1507 | 0.2938
32 | 15:30 | 150 | -1.4749 | 0.3564 | 1.4555 | Optimal | 1.1 | -1.5298 | 0.1571 | 0.0549 | 0.1993
32 | 15:30 | 180 | -1.5085 | 0.2518 | 1.5085 | Optimal | 1.1 | -1.5298 | 0.1571 | 0.0213 | 0.0947
32 | 15:30 | 210 | -1.4708 | 0.1257 | 1.2109 | Optimal | 1.1 | -1.5298 | 0.1571 | 0.059 | -0.0314
32 | 15:30 | 240 | -1.258 | -0.0976 | 0.7135 | Optimal | 1.1 | -1.5298 | 0.1571 | 0.2718 | -0.2547
32 | 15:30 | 270 | -1.1985 | -0.1173 | 0.1173 | Optimal | 1.1 | -1.5298 | 0.1571 | 0.3313 | -0.2744
32 | 15:30 | 300 | -1.1847 | -0.1157 | -0.4921 | Optimal | 1.1 | -1.5298 | 0.1571 | 0.3451 | -0.2728
32 | 15:30 | 330 | -1.1839 | -0.1149 | -0.9678 | Optimal | 1.1 | -1.5298 | 0.1571 | 0.3459 | -0.272
33 | 16:00 | 0 | -0.8247 | 0.1535 | -0.8247 | Optimal | 1.1 | -1.2201 | 0.1659 | 0.3954 | -0.0124
33 | 16:00 | 30 | -0.8315 | 0.4966 | -0.4718 | Optimal | 1.0324 | -1.2201 | 0.1659 | 0.3886 | 0.3307
33 | 16:00 | 60 | -0.8321 | 0.497 | 0.0144 | Optimal | 1.0324 | -1.2201 | 0.1659 | 0.388 | 0.3311
33 | 16:00 | 90 | -0.8674 | 0.4994 | 0.4994 | Optimal | 1.0358 | -1.2201 | 0.1659 | 0.3527 | 0.3335
33 | 16:00 | 120 | -1.025 | 0.4571 | 0.9084 | Optimal | 1.0626 | -1.2201 | 0.1659 | 0.1951 | 0.2912
33 | 16:00 | 150 | -1.1364 | 0.3487 | 1.1585 | Optimal | 1.1 | -1.2201 | 0.1659 | 0.0837 | 0.1828
33 | 16:00 | 180 | -1.1669 | 0.248 | 1.1669 | Optimal | 1.1 | -1.2201 | 0.1659 | 0.0532 | 0.0821
33 | 16:00 | 210 | -1.1232 | 0.1016 | 0.922 | Optimal | 1.1 | -1.2201 | 0.1659 | 0.0969 | -0.0643
33 | 16:00 | 240 | -0.9214 | -0.1091 | 0.5552 | Optimal | 1.1 | -1.2201 | 0.1659 | 0.2987 | -0.275
33 | 16:00 | 270 | -0.8388 | -0.1355 | 0.1355 | Optimal | 1.1 | -1.2201 | 0.1659 | 0.3813 | -0.3014
33 | 16:00 | 300 | -0.8312 | -0.1344 | -0.2992 | Optimal | 1.1 | -1.2201 | 0.1659 | 0.3889 | -0.3003
33 | 16:00 | 330 | -0.831 | -0.1342 | -0.6525 | Optimal | 1.1 | -1.2201 | 0.1659 | 0.3891 | -0.3001
34 | 16:30 | 0 | -0.5049 | 0.1584 | -0.5049 | Optimal | 1.1 | -0.8661 | 0.1739 | 0.3612 | -0.0155
34 | 16:30 | 30 | -0.5099 | 0.5014 | -0.1909 | Optimal | 1.0223 | -0.8661 | 0.1739 | 0.3562 | 0.3275
34 | 16:30 | 60 | -0.5105 | 0.5017 | 0.1793 | Optimal | 1.0222 | -0.8661 | 0.1739 | 0.3556 | 0.3278
34 | 16:30 | 90 | -0.5472 | 0.5047 | 0.5047 | Optimal | 1.0249 | -0.8661 | 0.1739 | 0.3189 | 0.3308
34 | 16:30 | 120 | -0.7064 | 0.462 | 0.7533 | Optimal | 1.0569 | -0.8661 | 0.1739 | 0.1597 | 0.2881
34 | 16:30 | 150 | -0.8217 | 0.3481 | 0.8857 | Optimal | 1.1 | -0.8661 | 0.1739 | 0.0444 | 0.1742
34 | 16:30 | 180 | -0.8542 | 0.2351 | 0.8542 | Optimal | 1.1 | -0.8661 | 0.1739 | 0.0119 | 0.0612
34 | 16:30 | 210 | -0.8116 | 0.0893 | 0.6583 | Optimal | 1.1 | -0.8661 | 0.1739 | 0.0545 | -0.0846
34 | 16:30 | 240 | -0.62 | -0.1129 | 0.4078 | Optimal | 1.1 | -0.8661 | 0.1739 | 0.2461 | -0.2868
34 | 16:30 | 270 | -0.5312 | -0.1404 | 0.1404 | Optimal | 1.1 | -0.8661 | 0.1739 | 0.3349 | -0.3143
34 | 16:30 | 300 | -0.5142 | -0.1376 | -0.138 | Optimal | 1.1 | -0.8661 | 0.1739 | 0.3519 | -0.3115
34 | 16:30 | 330 | -0.5106 | -0.1352 | -0.3746 | Optimal | 1.1 | -0.8661 | 0.1739 | 0.3555 | -0.3091
35 | 17:00 | 0 | -0.0567 | 0.3397 | -0.0567 | Optimal | 1.0649 | -0.5473 | 0.1799 | 0.4906 | 0.1598
35 | 17:00 | 30 | -0.0586 | 0.5311 | 0.2148 | Optimal | 1.0128 | -0.5473 | 0.1799 | 0.4887 | 0.3512
35 | 17:00 | 60 | -0.0594 | 0.5316 | 0.4307 | Optimal | 1.0126 | -0.5473 | 0.1799 | 0.4879 | 0.3517
35 | 17:00 | 90 | -0.0971 | 0.5349 | 0.5349 | Optimal | 1.0155 | -0.5473 | 0.1799 | 0.4502 | 0.355
35 | 17:00 | 120 | -0.2589 | 0.4914 | 0.555 | Optimal | 1.0473 | -0.5473 | 0.1799 | 0.2884 | 0.3115
35 | 17:00 | 150 | -0.3779 | 0.3727 | 0.5136 | Optimal | 1.1 | -0.5473 | 0.1799 | 0.1694 | 0.1928
35 | 17:00 | 180 | -0.4133 | 0.2432 | 0.4133 | Optimal | 1.1 | -0.5473 | 0.1799 | 0.134 | 0.0633
35 | 17:00 | 210 | -0.371 | 0.0904 | 0.2761 | Optimal | 1.1 | -0.5473 | 0.1799 | 0.1763 | -0.0895
35 | 17:00 | 240 | -0.2098 | -0.079 | 0.1733 | Optimal | 1.1 | -0.5473 | 0.1799 | 0.3375 | -0.2589
35 | 17:00 | 270 | -0.0972 | -0.112 | 0.112 | Optimal | 1.1 | -0.5473 | 0.1799 | 0.4501 | -0.2919
35 | 17:00 | 300 | -0.0636 | -0.109 | 0.0626 | Optimal | 1.1 | -0.5473 | 0.1799 | 0.4837 | -0.2889
35 | 17:00 | 330 | -0.0618 | -0.1076 | 0.0002 | Optimal | 1.1 | -0.5473 | 0.1799 | 0.4855 | -0.2875
36 | 17:30 | 0 | 0.1821 | 0.3378 | 0.1821 | Optimal | 1.0654 | -0.0998 | 0.2113 | 0.2819 | 0.1265
36 | 17:30 | 30 | 0.1815 | 0.5167 | 0.4156 | Optimal | 1.0078 | -0.0998 | 0.2113 | 0.2813 | 0.3054
36 | 17:30 | 60 | 0.178 | 0.52 | 0.5393 | Optimal | 1.0079 | -0.0998 | 0.2113 | 0.2778 | 0.3087
36 | 17:30 | 90 | 0.1358 | 0.5242 | 0.5242 | Optimal | 1.0119 | -0.0998 | 0.2113 | 0.2356 | 0.3129
36 | 17:30 | 120 | -0.0274 | 0.4804 | 0.4297 | Optimal | 1.0423 | -0.0998 | 0.2113 | 0.0724 | 0.2691
36 | 17:30 | 150 | -0.1478 | 0.36 | 0.308 | Optimal | 1.0977 | -0.0998 | 0.2113 | -0.048 | 0.1487
36 | 17:30 | 180 | -0.1842 | 0.2274 | 0.1842 | Optimal | 1.1 | -0.0998 | 0.2113 | -0.0844 | 0.0161
36 | 17:30 | 210 | -0.1421 | 0.0632 | 0.0914 | Optimal | 1.1 | -0.0998 | 0.2113 | -0.0423 | -0.1481
36 | 17:30 | 240 | 0.0036 | -0.0886 | 0.0749 | Optimal | 1.1 | -0.0998 | 0.2113 | 0.1034 | -0.2999
36 | 17:30 | 270 | 0.1298 | -0.1217 | 0.1217 | Optimal | 1.1 | -0.0998 | 0.2113 | 0.2296 | -0.333
36 | 17:30 | 300 | 0.1745 | -0.1167 | 0.1883 | Optimal | 1.0961 | -0.0998 | 0.2113 | 0.2743 | -0.328
36 | 17:30 | 330 | 0.1775 | -0.114 | 0.2107 | Optimal | 1.0962 | -0.0998 | 0.2113 | 0.2773 | -0.3253
37 | 18:00 | 0 | 0.4123 | 0.5079 | 0.4123 | Optimal | 1.0077 | 0.1318 | 0.2013 | 0.2805 | 0.3066
37 | 18:00 | 30 | 0.4122 | 0.508 | 0.611 | Optimal | 1.0077 | 0.1318 | 0.2013 | 0.2804 | 0.3067
37 | 18:00 | 60 | 0.4095 | 0.5104 | 0.6468 | Optimal | 1.007 | 0.1318 | 0.2013 | 0.2777 | 0.3091
37 | 18:00 | 90 | 0.3661 | 0.5151 | 0.5151 | Optimal | 1.0108 | 0.1318 | 0.2013 | 0.2343 | 0.3138
37 | 18:00 | 120 | 0.2008 | 0.4706 | 0.3072 | Optimal | 1.0354 | 0.1318 | 0.2013 | 0.069 | 0.2693
37 | 18:00 | 150 | 0.0794 | 0.3493 | 0.1059 | Optimal | 1.0781 | 0.1318 | 0.2013 | -0.0524 | 0.148
37 | 18:00 | 180 | 0.0381 | 0.2059 | -0.0381 | Optimal | 1.1 | 0.1318 | 0.2013 | -0.0937 | 0.0046
37 | 18:00 | 210 | 0.0822 | 0.0393 | -0.0908 | Optimal | 1.1 | 0.1318 | 0.2013 | -0.0496 | -0.162
37 | 18:00 | 240 | 0.2127 | -0.0934 | -0.0254 | Optimal | 1.1 | 0.1318 | 0.2013 | 0.0809 | -0.2947
37 | 18:00 | 270 | 0.3546 | -0.1291 | 0.1291 | Optimal | 1.0954 | 0.1318 | 0.2013 | 0.2228 | -0.3304
37 | 18:00 | 300 | 0.4038 | -0.1237 | 0.309 | Optimal | 1.0922 | 0.1318 | 0.2013 | 0.272 | -0.325
37 | 18:00 | 330 | 0.4066 | -0.1211 | 0.4127 | Optimal | 1.0925 | 0.1318 | 0.2013 | 0.2748 | -0.3224
38 | 18:30 | 0 | 0.67 | 0.5068 | 0.67 | Optimal | 1.004 | 0.3603 | 0.193 | 0.3097 | 0.3138
38 | 18:30 | 30 | 0.6697 | 0.5077 | 0.8338 | Optimal | 1.0037 | 0.3603 | 0.193 | 0.3094 | 0.3147
38 | 18:30 | 60 | 0.6673 | 0.5097 | 0.7751 | Optimal | 1.0044 | 0.3603 | 0.193 | 0.307 | 0.3167
38 | 18:30 | 90 | 0.6154 | 0.5168 | 0.5168 | Optimal | 1.0069 | 0.3603 | 0.193 | 0.2551 | 0.3238
38 | 18:30 | 120 | 0.4493 | 0.4721 | 0.1842 | Optimal | 1.0274 | 0.3603 | 0.193 | 0.089 | 0.2791
38 | 18:30 | 150 | 0.3275 | 0.3505 | -0.1084 | Optimal | 1.0822 | 0.3603 | 0.193 | -0.0328 | 0.1575
38 | 18:30 | 180 | 0.2869 | 0.2075 | -0.2869 | Optimal | 1.1 | 0.3603 | 0.193 | -0.0734 | 0.0145
38 | 18:30 | 210 | 0.3342 | 0.033 | -0.3059 | Optimal | 1.1 | 0.3603 | 0.193 | -0.0261 | -0.16
38 | 18:30 | 240 | 0.4555 | -0.0887 | -0.1509 | Optimal | 1.1 | 0.3603 | 0.193 | 0.0952 | -0.2817
38 | 18:30 | 270 | 0.6028 | -0.1269 | 0.1269 | Optimal | 1.0935 | 0.3603 | 0.193 | 0.2425 | -0.3199
38 | 18:30 | 300 | 0.6616 | -0.1185 | 0.4334 | Optimal | 1.0844 | 0.3603 | 0.193 | 0.3013 | -0.3115
38 | 18:30 | 330 | 0.6643 | -0.1165 | 0.6335 | Optimal | 1.0844 | 0.3603 | 0.193 | 0.304 | -0.3095
39 | 19:00 | 0 | 1.0837 | 0.5184 | 1.0837 | Optimal | 1 | 0.6091 | 0.195 | 0.4746 | 0.3234
39 | 19:00 | 30 | 1.0802 | 0.5341 | 1.2025 | Optimal | 1 | 0.6091 | 0.195 | 0.4711 | 0.3391
39 | 19:00 | 60 | 1.0701 | 0.5418 | 1.0042 | Optimal | 1 | 0.6091 | 0.195 | 0.461 | 0.3468
39 | 19:00 | 90 | 1.0194 | 0.5503 | 0.5503 | Optimal | 1 | 0.6091 | 0.195 | 0.4103 | 0.3553
39 | 19:00 | 120 | 0.8503 | 0.5048 | 0.012 | Optimal | 1.013 | 0.6091 | 0.195 | 0.2412 | 0.3098
39 | 19:00 | 150 | 0.7266 | 0.3814 | -0.4385 | Optimal | 1.0687 | 0.6091 | 0.195 | 0.1175 | 0.1864
39 | 19:00 | 180 | 0.6837 | 0.23 | -0.6837 | Optimal | 1.1 | 0.6091 | 0.195 | 0.0746 | 0.035
39 | 19:00 | 210 | 0.73 | 0.0639 | -0.6641 | Optimal | 1.1 | 0.6091 | 0.195 | 0.1209 | -0.1311
39 | 19:00 | 240 | 0.8427 | -0.05 | -0.3781 | Optimal | 1.1 | 0.6091 | 0.195 | 0.2336 | -0.245
39 | 19:00 | 270 | 0.9999 | -0.0909 | 0.0909 | Optimal | 1.0852 | 0.6091 | 0.195 | 0.3908 | -0.2859
39 | 19:00 | 300 | 1.0698 | -0.0801 | 0.6043 | Optimal | 1.079 | 0.6091 | 0.195 | 0.4607 | -0.2751
39 | 19:00 | 330 | 1.0746 | -0.0764 | 0.9688 | Optimal | 1.078 | 0.6091 | 0.195 | 0.4655 | -0.2714
40 | 19:30 | 0 | 1.2639 | 0.5004 | 1.2639 | Optimal | 1 | 1.0097 | 0.2297 | 0.2542 | 0.2707
40 | 19:30 | 30 | 1.2549 | 0.5323 | 1.3529 | Optimal | 1 | 1.0097 | 0.2297 | 0.2452 | 0.3026
40 | 19:30 | 60 | 1.2371 | 0.5468 | 1.0921 | Optimal | 1 | 1.0097 | 0.2297 | 0.2274 | 0.3171
40 | 19:30 | 90 | 1.1606 | 0.564 | 0.564 | Optimal | 1 | 1.0097 | 0.2297 | 0.1509 | 0.3343
40 | 19:30 | 120 | 0.9969 | 0.5185 | -0.0494 | Optimal | 1.0125 | 1.0097 | 0.2297 | -0.0128 | 0.2888
40 | 19:30 | 150 | 0.8725 | 0.3945 | -0.5583 | Optimal | 1.0656 | 1.0097 | 0.2297 | -0.1372 | 0.1648
40 | 19:30 | 180 | 0.8294 | 0.2396 | -0.8294 | Optimal | 1.1 | 1.0097 | 0.2297 | -0.1803 | 0.0099
40 | 19:30 | 210 | 0.8731 | 0.0791 | -0.7957 | Optimal | 1.1 | 1.0097 | 0.2297 | -0.1366 | -0.1506
40 | 19:30 | 240 | 0.9858 | -0.0342 | -0.4633 | Optimal | 1.1 | 1.0097 | 0.2297 | -0.0239 | -0.2639
40 | 19:30 | 270 | 1.1454 | -0.076 | 0.076 | Optimal | 1.0832 | 1.0097 | 0.2297 | 0.1357 | -0.3057
40 | 19:30 | 300 | 1.2436 | -0.0575 | 0.6716 | Optimal | 1.0783 | 1.0097 | 0.2297 | 0.2339 | -0.2872
40 | 19:30 | 330 | 1.2543 | -0.0485 | 1.1105 | Optimal | 1.077 | 1.0097 | 0.2297 | 0.2446 | -0.2782
41 | 20:00 | 0 | 1.3748 | 0.4771 | 1.3748 | Optimal | 1 | 1.1563 | 0.2442 | 0.2185 | 0.2329
41 | 20:00 | 30 | 1.3601 | 0.5232 | 1.4395 | Optimal | 1 | 1.1563 | 0.2442 | 0.2038 | 0.279
41 | 20:00 | 60 | 1.3297 | 0.552 | 1.1429 | Optimal | 1 | 1.1563 | 0.2442 | 0.1734 | 0.3078
41 | 20:00 | 90 | 1.2333 | 0.5762 | 0.5762 | Optimal | 1.0003 | 1.1563 | 0.2442 | 0.077 | 0.332
41 | 20:00 | 120 | 1.0729 | 0.5314 | -0.0763 | Optimal | 1.0132 | 1.1563 | 0.2442 | -0.0834 | 0.2872
41 | 20:00 | 150 | 0.9498 | 0.4087 | -0.6182 | Optimal | 1.0676 | 1.1563 | 0.2442 | -0.2065 | 0.1645
41 | 20:00 | 180 | 0.9081 | 0.2568 | -0.9081 | Optimal | 1.1 | 1.1563 | 0.2442 | -0.2482 | 0.0126
41 | 20:00 | 210 | 0.9508 | 0.0894 | -0.8681 | Optimal | 1.1 | 1.1563 | 0.2442 | -0.2055 | -0.1548
41 | 20:00 | 240 | 1.0619 | -0.0219 | -0.512 | Optimal | 1.1 | 1.1563 | 0.2442 | -0.0944 | -0.2661
41 | 20:00 | 270 | 1.2202 | -0.0633 | 0.0633 | Optimal | 1.0828 | 1.1563 | 0.2442 | 0.0639 | -0.3075
41 | 20:00 | 300 | 1.3419 | -0.037 | 0.7029 | Optimal | 1.0761 | 1.1563 | 0.2442 | 0.1856 | -0.2812
41 | 20:00 | 330 | 1.3645 | -0.0169 | 1.1901 | Optimal | 1.0737 | 1.1563 | 0.2442 | 0.2082 | -0.2611
42 | 20:30 | 0 | 1.4133 | 0.4157 | 1.4133 | Optimal | 1.0154 | 1.2314 | 0.2568 | 0.1819 | 0.1589
42 | 20:30 | 30 | 1.3938 | 0.5009 | 1.4575 | Optimal | 1 | 1.2314 | 0.2568 | 0.1624 | 0.2441
42 | 20:30 | 60 | 1.3453 | 0.5473 | 1.1466 | Optimal | 1 | 1.2314 | 0.2568 | 0.1139 | 0.2905
42 | 20:30 | 90 | 1.2363 | 0.5769 | 0.5769 | Optimal | 1 | 1.2314 | 0.2568 | 0.0049 | 0.3201
42 | 20:30 | 120 | 1.0794 | 0.5323 | -0.0787 | Optimal | 1.0119 | 1.2314 | 0.2568 | -0.152 | 0.2755
42 | 20:30 | 150 | 0.957 | 0.4107 | -0.6235 | Optimal | 1.0615 | 1.2314 | 0.2568 | -0.2744 | 0.1539
42 | 20:30 | 180 | 0.9156 | 0.2432 | -0.9156 | Optimal | 1.1 | 1.2314 | 0.2568 | -0.3158 | -0.0136
42 | 20:30 | 210 | 0.9567 | 0.0893 | -0.8732 | Optimal | 1.1 | 1.2314 | 0.2568 | -0.2747 | -0.1675
42 | 20:30 | 240 | 1.0664 | -0.0203 | -0.5156 | Optimal | 1.1 | 1.2314 | 0.2568 | -0.165 | -0.2771
42 | 20:30 | 270 | 1.2251 | -0.0619 | 0.0619 | Optimal | 1.0821 | 1.2314 | 0.2568 | -0.0063 | -0.3187
42 | 20:30 | 300 | 1.3649 | -0.0288 | 0.7074 | Optimal | 1.0723 | 1.2314 | 0.2568 | 0.1335 | -0.2856
42 | 20:30 | 330 | 1.402 | 0.0047 | 1.2118 | Optimal | 1.0687 | 1.2314 | 0.2568 | 0.1706 | -0.2521
43 | 21:00 | 0 | 1.4057 | 0.3497 | 1.4057 | Optimal | 1.0178 | 1.2369 | 0.258 | 0.1688 | 0.0917
43 | 21:00 | 30 | 1.3832 | 0.4702 | 1.433 | Optimal | 1 | 1.2369 | 0.258 | 0.1463 | 0.2122
43 | 21:00 | 60 | 1.3164 | 0.5356 | 1.122 | Optimal | 1 | 1.2369 | 0.258 | 0.0795 | 0.2776
43 | 21:00 | 90 | 1.1982 | 0.5685 | 0.5685 | Optimal | 1 | 1.2369 | 0.258 | -0.0387 | 0.3105
43 | 21:00 | 120 | 1.038 | 0.524 | -0.0652 | Optimal | 1.0101 | 1.2369 | 0.258 | -0.1989 | 0.266
43 | 21:00 | 150 | 0.9199 | 0.4071 | -0.5931 | Optimal | 1.0675 | 1.2369 | 0.258 | -0.317 | 0.1491
43 | 21:00 | 180 | 0.8808 | 0.239 | -0.8808 | Optimal | 1.1 | 1.2369 | 0.258 | -0.3561 | -0.019
43 | 21:00 | 210 | 0.9216 | 0.0757 | -0.8359 | Optimal | 1.1 | 1.2369 | 0.258 | -0.3153 | -0.1823
43 | 21:00 | 240 | 1.0273 | -0.03 | -0.4876 | Optimal | 1.1 | 1.2369 | 0.258 | -0.2096 | -0.288
43 | 21:00 | 270 | 1.1842 | -0.0711 | 0.0711 | Optimal | 1.0814 | 1.2369 | 0.258 | -0.0527 | -0.3291
43 | 21:00 | 300 | 1.3344 | -0.0338 | 0.6965 | Optimal | 1.0684 | 1.2369 | 0.258 | 0.0975 | -0.2918
43 | 21:00 | 330 | 1.3914 | 0.0182 | 1.1959 | Optimal | 1.0617 | 1.2369 | 0.258 | 0.1545 | -0.2398
44 | 21:30 | 0 | 1.3925 | 0.3036 | 1.3925 | Optimal | 1.026 | 1.1953 | 0.2491 | 0.1972 | 0.0545
44 | 21:30 | 30 | 1.3693 | 0.4305 | 1.4011 | Optimal | 1 | 1.1953 | 0.2491 | 0.174 | 0.1814
44 | 21:30 | 60 | 1.2753 | 0.5257 | 1.0929 | Optimal | 1 | 1.1953 | 0.2491 | 0.08 | 0.2766
44 | 21:30 | 90 | 1.154 | 0.5592 | 0.5592 | Optimal | 1 | 1.1953 | 0.2491 | -0.0413 | 0.3101
44 | 21:30 | 120 | 0.9964 | 0.5154 | -0.0519 | Optimal | 1.0105 | 1.1953 | 0.2491 | -0.1989 | 0.2663
44 | 21:30 | 150 | 0.8849 | 0.405 | -0.5639 | Optimal | 1.0675 | 1.1953 | 0.2491 | -0.3104 | 0.1559
44 | 21:30 | 180 | 0.849 | 0.2002 | -0.849 | Optimal | 1.1 | 1.1953 | 0.2491 | -0.3463 | -0.0489
44 | 21:30 | 210 | 0.8868 | 0.0595 | -0.7977 | Optimal | 1.1 | 1.1953 | 0.2491 | -0.3085 | -0.1896
44 | 21:30 | 240 | 0.9862 | -0.04 | -0.4585 | Optimal | 1.1 | 1.1953 | 0.2491 | -0.2091 | -0.2891
44 | 21:30 | 270 | 1.1413 | -0.0803 | 0.0803 | Optimal | 1.083 | 1.1953 | 0.2491 | -0.054 | -0.3294
44 | 21:30 | 300 | 1.2985 | -0.0402 | 0.6841 | Optimal | 1.0675 | 1.1953 | 0.2491 | 0.1032 | -0.2893
44 | 21:30 | 330 | 1.3735 | 0.0307 | 1.1741 | Optimal | 1.0576 | 1.1953 | 0.2491 | 0.1782 | -0.2184
45 | 22:00 | 0 | 1.2932 | 0.2497 | 1.2932 | Optimal | 1.0264 | 1.1524 | 0.2399 | 0.1408 | 0.0098
45 | 22:00 | 30 | 1.2626 | 0.4 | 1.2934 | Optimal | 1 | 1.1524 | 0.2399 | 0.1102 | 0.1601
45 | 22:00 | 60 | 1.162 | 0.5001 | 1.0141 | Optimal | 1 | 1.1524 | 0.2399 | 0.0096 | 0.2602
45 | 22:00 | 90 | 1.0381 | 0.5346 | 0.5346 | Optimal | 1 | 1.1524 | 0.2399 | -0.1143 | 0.2947
45 | 22:00 | 120 | 0.885 | 0.4929 | -0.0156 | Optimal | 1.0091 | 1.1524 | 0.2399 | -0.2674 | 0.253
45 | 22:00 | 150 | 0.7823 | 0.3925 | -0.4813 | Optimal | 1.0568 | 1.1524 | 0.2399 | -0.3701 | 0.1526
45 | 22:00 | 180 | 0.7501 | 0.1396 | -0.7501 | Optimal | 1.1 | 1.1524 | 0.2399 | -0.4023 | -0.1003
45 | 22:00 | 210 | 0.7834 | 0.0236 | -0.6903 | Optimal | 1.1 | 1.1524 | 0.2399 | -0.369 | -0.2163
45 | 22:00 | 240 | 0.8757 | -0.0681 | -0.3789 | Optimal | 1.1 | 1.1524 | 0.2399 | -0.2767 | -0.308
45 | 22:00 | 270 | 1.0227 | -0.106 | 0.106 | Optimal | 1.0856 | 1.1524 | 0.2399 | -0.1297 | -0.3459
45 | 22:00 | 300 | 1.1838 | -0.0642 | 0.6475 | Optimal | 1.0692 | 1.1524 | 0.2399 | 0.0314 | -0.3041
45 | 22:00 | 330 | 1.2716 | 0.0203 | 1.0911 | Optimal | 1.0554 | 1.1524 | 0.2399 | 0.1192 | -0.2196
46 | 22:30 | 0 | 1.1258 | 0.2028 | 1.1258 | Optimal | 1.0252 | 1.0326 | 0.2143 | 0.0932 | -0.0115
46 | 22:30 | 30 | 1.0941 | 0.3566 | 1.1258 | Optimal | 1.001 | 1.0326 | 0.2143 | 0.0615 | 0.1423
46 | 22:30 | 60 | 0.9878 | 0.4625 | 0.8944 | Optimal | 1 | 1.0326 | 0.2143 | -0.0448 | 0.2482
46 | 22:30 | 90 | 0.8575 | 0.4969 | 0.4969 | Optimal | 1.0038 | 1.0326 | 0.2143 | -0.1751 | 0.2826
46 | 22:30 | 120 | 0.7075 | 0.4575 | 0.0424 | Optimal | 1.0156 | 1.0326 | 0.2143 | -0.3251 | 0.2432
46 | 22:30 | 150 | 0.6169 | 0.369 | -0.3498 | Optimal | 1.0538 | 1.0326 | 0.2143 | -0.4157 | 0.1547
46 | 22:30 | 180 | 0.5881 | 0.1046 | -0.5881 | Optimal | 1.1 | 1.0326 | 0.2143 | -0.4445 | -0.1097
46 | 22:30 | 210 | 0.6201 | -0.0272 | -0.5234 | Optimal | 1.1 | 1.0326 | 0.2143 | -0.4125 | -0.2415
46 | 22:30 | 240 | 0.7037 | -0.1099 | -0.2566 | Optimal | 1.1 | 1.0326 | 0.2143 | -0.3289 | -0.3242
46 | 22:30 | 270 | 0.8423 | -0.1452 | 0.1452 | Optimal | 1.0845 | 1.0326 | 0.2143 | -0.1903 | -0.3595
46 | 22:30 | 300 | 1.0042 | -0.1027 | 0.591 | Optimal | 1.0669 | 1.0326 | 0.2143 | -0.0284 | -0.317
46 | 22:30 | 330 | 1.0996 | -0.0095 | 0.9571 | Optimal | 1.0489 | 1.0326 | 0.2143 | 0.067 | -0.2238
47 | 23:00 | 0 | 0.9354 | 0.137 | 0.9354 | Optimal | 1.0257 | 0.85 | 0.1759 | 0.0854 | -0.0389
47 | 23:00 | 30 | 0.9002 | 0.3167 | 0.9379 | Optimal | 1.0041 | 0.85 | 0.1759 | 0.0502 | 0.1408
47 | 23:00 | 60 | 0.7953 | 0.4198 | 0.7612 | Optimal | 1.0002 | 0.85 | 0.1759 | -0.0547 | 0.2439
47 | 23:00 | 90 | 0.6551 | 0.4551 | 0.4551 | Optimal | 1.0054 | 0.85 | 0.1759 | -0.1949 | 0.2792
47 | 23:00 | 120 | 0.5126 | 0.4181 | 0.1057 | Optimal | 1.0204 | 0.85 | 0.1759 | -0.3374 | 0.2422
47 | 23:00 | 150 | 0.428 | 0.3349 | -0.2032 | Optimal | 1.0539 | 0.85 | 0.1759 | -0.422 | 0.159
47 | 23:00 | 180 | 0.402 | 0.0745 | -0.402 | Optimal | 1.1 | 0.85 | 0.1759 | -0.448 | -0.1014
47 | 23:00 | 210 | 0.4304 | -0.0745 | -0.3355 | Optimal | 1.1 | 0.85 | 0.1759 | -0.4196 | -0.2504
47 | 23:00 | 240 | 0.513 | -0.1554 | -0.1219 | Optimal | 1.1 | 0.85 | 0.1759 | -0.337 | -0.3313
47 | 23:00 | 270 | 0.6426 | -0.1878 | 0.1878 | Optimal | 1.0931 | 0.85 | 0.1759 | -0.2074 | -0.3637
47 | 23:00 | 300 | 0.8051 | -0.1449 | 0.528 | Optimal | 1.074 | 0.85 | 0.1759 | -0.0449 | -0.3208
47 | 23:00 | 330 | 0.9062 | -0.0451 | 0.8074 | Optimal | 1.0496 | 0.85 | 0.1759 | 0.0562 | -0.221
48 | 23:30 | 0 | 0.839 | 0.1445 | 0.839 | Optimal | 1.0241 | 0.6488 | 0.1337 | 0.1902 | 0.0108
48 | 23:30 | 30 | 0.8035 | 0.292 | 0.8419 | Optimal | 1.0078 | 0.6488 | 0.1337 | 0.1547 | 0.1583
48 | 23:30 | 60 | 0.6978 | 0.3966 | 0.6924 | Optimal | 1.0042 | 0.6488 | 0.1337 | 0.049 | 0.2629
48 | 23:30 | 90 | 0.5504 | 0.4339 | 0.4339 | Optimal | 1.0087 | 0.6488 | 0.1337 | -0.0984 | 0.3002
48 | 23:30 | 120 | 0.415 | 0.3989 | 0.1379 | Optimal | 1.0188 | 0.6488 | 0.1337 | -0.2338 | 0.2652
48 | 23:30 | 150 | 0.3359 | 0.322 | -0.1299 | Optimal | 1.0552 | 0.6488 | 0.1337 | -0.3129 | 0.1883
48 | 23:30 | 180 | 0.3145 | 0.0186 | -0.3145 | Optimal | 1.1 | 0.6488 | 0.1337 | -0.3343 | -0.1151
48 | 23:30 | 210 | 0.3421 | -0.104 | -0.2442 | Optimal | 1.1 | 0.6488 | 0.1337 | -0.3067 | -0.2377
48 | 23:30 | 240 | 0.4205 | -0.1798 | -0.0545 | Optimal | 1.1 | 0.6488 | 0.1337 | -0.2283 | -0.3135
48 | 23:30 | 270 | 0.5405 | -0.2099 | 0.2099 | Optimal | 1.0949 | 0.6488 | 0.1337 | -0.1083 | -0.3436
48 | 23:30 | 300 | 0.7035 | -0.1666 | 0.496 | Optimal | 1.0744 | 0.6488 | 0.1337 | 0.0547 | -0.3003
48 | 23:30 | 330 | 0.8068 | -0.0642 | 0.7308 | Optimal | 1.049 | 0.6488 | 0.1337 | 0.158 | -0.1979

## P02_00h30
TR9 rolling FOR — period 2 = 00:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 0.4511 | B_Q (MVAr) = | 0.0924
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 0.6851 | 0.0676 | 0.234 | -0.0248 | 0.6851 | charge/import
30 | 0.6367 | 0.2389 | 0.1856 | 0.1465 | 0.67085 | charge/import
60 | 0.522 | 0.355 | 0.0709 | 0.2626 | 0.56844 | charge/import
90 | 0.3646 | 0.3963 | -0.0865 | 0.3039 | 0.3963 | discharge/export
120 | 0.2101 | 0.3565 | -0.241 | 0.2641 | 0.20369 | discharge/export
150 | 0.187 | 0.3413 | -0.2641 | 0.2489 | 0.0087032 | discharge/export
180 | 0.1845 | -0.1443 | -0.2666 | -0.2367 | -0.1845 | discharge/export
210 | 0.1963 | -0.1915 | -0.2548 | -0.2839 | -0.074251 | discharge/export
240 | 0.2297 | -0.2154 | -0.2214 | -0.3078 | 0.071692 | discharge/export
270 | 0.3579 | -0.2485 | -0.0932 | -0.3409 | 0.2485 | discharge/export
300 | 0.5222 | -0.2044 | 0.0711 | -0.2968 | 0.43812 | charge/import
330 | 0.6424 | -0.0842 | 0.1913 | -0.1766 | 0.59843 | charge/import
(close) | 0.6851 | 0.0676 | 0.234 | -0.0248
Interpretation (all computed live):
P width (MW) |  | 0.5006
import-reach (charge) |  | 0.234
export-reach (dischg) |  | 0.2666
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P03_01h00
TR9 rolling FOR — period 3 = 01:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 0.3612 | B_Q (MVAr) = | 0.0739
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 0.669 | 0.0631 | 0.3078 | -0.0108 | 0.669 | charge/import
30 | 0.6206 | 0.2354 | 0.2594 | 0.1615 | 0.65516 | charge/import
60 | 0.5037 | 0.3528 | 0.1425 | 0.2789 | 0.55738 | charge/import
90 | 0.3485 | 0.3931 | -0.0127 | 0.3192 | 0.3931 | discharge/export
120 | 0.2004 | 0.3553 | -0.1608 | 0.2814 | 0.2075 | discharge/export
150 | 0.1855 | 0.3457 | -0.1757 | 0.2718 | 0.012202 | discharge/export
180 | 0.1833 | -0.1595 | -0.1779 | -0.2334 | -0.1833 | discharge/export
210 | 0.1941 | -0.2041 | -0.1671 | -0.278 | -0.066046 | discharge/export
240 | 0.2168 | -0.2201 | -0.1444 | -0.294 | 0.082212 | discharge/export
270 | 0.3423 | -0.2518 | -0.0189 | -0.3257 | 0.2518 | discharge/export
300 | 0.5064 | -0.2077 | 0.1452 | -0.2816 | 0.43307 | charge/import
330 | 0.6266 | -0.0877 | 0.2654 | -0.1616 | 0.5865 | charge/import
(close) | 0.669 | 0.0631 | 0.3078 | -0.0108
Interpretation (all computed live):
P width (MW) |  | 0.4857
import-reach (charge) |  | 0.3078
export-reach (dischg) |  | 0.1779
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P04_01h30
TR9 rolling FOR — period 4 = 01:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 0.3453 | B_Q (MVAr) = | 0.0707
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 0.638 | 0.0561 | 0.2927 | -0.0146 | 0.638 | charge/import
30 | 0.5894 | 0.2293 | 0.2441 | 0.1586 | 0.62509 | charge/import
60 | 0.4739 | 0.3459 | 0.1286 | 0.2752 | 0.53651 | charge/import
90 | 0.3176 | 0.3868 | -0.0277 | 0.3161 | 0.3868 | discharge/export
120 | 0.1751 | 0.351 | -0.1702 | 0.2803 | 0.21642 | discharge/export
150 | 0.167 | 0.3459 | -0.1783 | 0.2752 | 0.028324 | discharge/export
180 | 0.1648 | -0.1805 | -0.1805 | -0.2512 | -0.1648 | discharge/export
210 | 0.174 | -0.2157 | -0.1713 | -0.2864 | -0.042838 | discharge/export
240 | 0.1923 | -0.2285 | -0.153 | -0.2992 | 0.10174 | discharge/export
270 | 0.3116 | -0.2582 | -0.0337 | -0.3289 | 0.2582 | discharge/export
300 | 0.4756 | -0.2142 | 0.1303 | -0.2849 | 0.4233 | charge/import
330 | 0.5957 | -0.0942 | 0.2504 | -0.1649 | 0.56299 | charge/import
(close) | 0.638 | 0.0561 | 0.2927 | -0.0146
Interpretation (all computed live):
P width (MW) |  | 0.4732
import-reach (charge) |  | 0.2927
export-reach (dischg) |  | 0.1805
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P05_02h00
TR9 rolling FOR — period 5 = 02:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 0.3146 | B_Q (MVAr) = | 0.0643
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 0.6293 | 0.0555 | 0.3147 | -0.0088 | 0.6293 | charge/import
30 | 0.5809 | 0.2273 | 0.2663 | 0.163 | 0.61672 | charge/import
60 | 0.4653 | 0.344 | 0.1507 | 0.2797 | 0.53056 | charge/import
90 | 0.3084 | 0.3851 | -0.0062 | 0.3208 | 0.3851 | discharge/export
120 | 0.1734 | 0.3526 | -0.1412 | 0.2883 | 0.21866 | discharge/export
150 | 0.1693 | 0.35 | -0.1453 | 0.2857 | 0.028382 | discharge/export
180 | 0.1672 | -0.1886 | -0.1474 | -0.2529 | -0.1672 | discharge/export
210 | 0.1762 | -0.2231 | -0.1384 | -0.2874 | -0.041044 | discharge/export
240 | 0.1915 | -0.2337 | -0.1231 | -0.298 | 0.10664 | discharge/export
270 | 0.3028 | -0.2601 | -0.0118 | -0.3244 | 0.2601 | discharge/export
300 | 0.4667 | -0.2161 | 0.1521 | -0.2804 | 0.4205 | charge/import
330 | 0.5867 | -0.0963 | 0.2721 | -0.1606 | 0.55625 | charge/import
(close) | 0.6293 | 0.0555 | 0.3147 | -0.0088
Interpretation (all computed live):
P width (MW) |  | 0.4621
import-reach (charge) |  | 0.3147
export-reach (dischg) |  | 0.1474
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P06_02h30
TR9 rolling FOR — period 6 = 02:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 0.3055 | B_Q (MVAr) = | 0.0625
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 0.6328 | 0.055 | 0.3273 | -0.0075 | 0.6328 | charge/import
30 | 0.5845 | 0.2275 | 0.279 | 0.165 | 0.61994 | charge/import
60 | 0.4671 | 0.3456 | 0.1616 | 0.2831 | 0.53285 | charge/import
90 | 0.3122 | 0.3858 | 0.0067 | 0.3233 | 0.3858 | charge/import
120 | 0.1862 | 0.3571 | -0.1193 | 0.2946 | 0.21616 | discharge/export
150 | 0.1838 | 0.3556 | -0.1217 | 0.2931 | 0.018625 | discharge/export
180 | 0.1816 | -0.1997 | -0.1239 | -0.2622 | -0.1816 | discharge/export
210 | 0.1899 | -0.2288 | -0.1156 | -0.2913 | -0.050058 | discharge/export
240 | 0.1993 | -0.2353 | -0.1062 | -0.2978 | 0.10413 | discharge/export
270 | 0.3066 | -0.2593 | 0.0011 | -0.3218 | 0.2593 | charge/import
300 | 0.4705 | -0.2153 | 0.165 | -0.2778 | 0.42171 | charge/import
330 | 0.5905 | -0.0954 | 0.285 | -0.1579 | 0.55909 | charge/import
(close) | 0.6328 | 0.055 | 0.3273 | -0.0075
Interpretation (all computed live):
P width (MW) |  | 0.4512
import-reach (charge) |  | 0.3273
export-reach (dischg) |  | 0.1239
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P07_03h00
TR9 rolling FOR — period 7 = 03:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 0.3093 | B_Q (MVAr) = | 0.0632
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 0.636 | 0.0577 | 0.3267 | -0.0055 | 0.636 | charge/import
30 | 0.5875 | 0.2294 | 0.2782 | 0.1662 | 0.62349 | charge/import
60 | 0.4724 | 0.3459 | 0.1631 | 0.2827 | 0.53576 | charge/import
90 | 0.3152 | 0.3871 | 0.0059 | 0.3239 | 0.3871 | charge/import
120 | 0.1996 | 0.3624 | -0.1097 | 0.2992 | 0.21405 | discharge/export
150 | 0.1982 | 0.3615 | -0.1111 | 0.2983 | 0.0091038 | discharge/export
180 | 0.1958 | -0.2016 | -0.1135 | -0.2648 | -0.1958 | discharge/export
210 | 0.2031 | -0.231 | -0.1062 | -0.2942 | -0.06039 | discharge/export
240 | 0.211 | -0.2363 | -0.0983 | -0.2995 | 0.099142 | discharge/export
270 | 0.3094 | -0.258 | 0.0001 | -0.3212 | 0.258 | charge/import
300 | 0.4733 | -0.214 | 0.164 | -0.2772 | 0.42198 | charge/import
330 | 0.5934 | -0.0941 | 0.2841 | -0.1573 | 0.56095 | charge/import
(close) | 0.636 | 0.0577 | 0.3267 | -0.0055
Interpretation (all computed live):
P width (MW) |  | 0.4402
import-reach (charge) |  | 0.3267
export-reach (dischg) |  | 0.1135
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P08_03h30
TR9 rolling FOR — period 8 = 03:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 0.3123 | B_Q (MVAr) = | 0.0645
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 0.5677 | 0.0512 | 0.2554 | -0.0133 | 0.5677 | charge/import
30 | 0.5191 | 0.2241 | 0.2068 | 0.1596 | 0.5616 | charge/import
60 | 0.4039 | 0.3407 | 0.0916 | 0.2762 | 0.497 | charge/import
90 | 0.2468 | 0.382 | -0.0655 | 0.3175 | 0.382 | discharge/export
120 | 0.1424 | 0.361 | -0.1699 | 0.2965 | 0.24144 | discharge/export
150 | 0.1414 | 0.3604 | -0.1709 | 0.2959 | 0.057744 | discharge/export
180 | 0.1394 | -0.2162 | -0.1729 | -0.2807 | -0.1394 | discharge/export
210 | 0.1458 | -0.2395 | -0.1665 | -0.304 | -0.0065165 | discharge/export
240 | 0.1533 | -0.2446 | -0.159 | -0.3091 | 0.13518 | discharge/export
270 | 0.242 | -0.2634 | -0.0703 | -0.3279 | 0.2634 | discharge/export
300 | 0.4055 | -0.2195 | 0.0932 | -0.284 | 0.39284 | charge/import
330 | 0.5252 | -0.0998 | 0.2129 | -0.1643 | 0.50474 | charge/import
(close) | 0.5677 | 0.0512 | 0.2554 | -0.0133
Interpretation (all computed live):
P width (MW) |  | 0.4283
import-reach (charge) |  | 0.2554
export-reach (dischg) |  | 0.1729
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P09_04h00
TR9 rolling FOR — period 9 = 04:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 0.2443 | B_Q (MVAr) = | 0.0593
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 0.4081 | 0.0588 | 0.1638 | -0.0005 | 0.4081 | charge/import
30 | 0.3607 | 0.2255 | 0.1164 | 0.1662 | 0.42513 | charge/import
60 | 0.2456 | 0.3421 | 0.0013 | 0.2828 | 0.41907 | charge/import
90 | 0.0862 | 0.3843 | -0.1581 | 0.325 | 0.3843 | discharge/export
120 | -0.0107 | 0.3656 | -0.255 | 0.3063 | 0.32197 | discharge/export
150 | -0.0116 | 0.3651 | -0.2559 | 0.3058 | 0.1926 | discharge/export
180 | -0.0131 | -0.2082 | -0.2574 | -0.2675 | 0.0131 | discharge/export
210 | -0.0059 | -0.2385 | -0.2502 | -0.2978 | 0.12436 | discharge/export
240 | 0.0026 | -0.2441 | -0.2417 | -0.3034 | 0.2101 | discharge/export
270 | 0.0839 | -0.262 | -0.1604 | -0.3213 | 0.262 | discharge/export
300 | 0.2455 | -0.2184 | 0.0012 | -0.2777 | 0.31189 | charge/import
330 | 0.3649 | -0.099 | 0.1206 | -0.1583 | 0.36551 | charge/import
(close) | 0.4081 | 0.0588 | 0.1638 | -0.0005
Interpretation (all computed live):
P width (MW) |  | 0.4212
import-reach (charge) |  | 0.1638
export-reach (dischg) |  | 0.2574
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P10_04h30
TR9 rolling FOR — period 10 = 04:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 0.0846 | B_Q (MVAr) = | 0.0612
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 0.1815 | 0.059 | 0.0969 | -0.0022 | 0.1815 | charge/import
30 | 0.1359 | 0.2219 | 0.0513 | 0.1607 | 0.22864 | charge/import
60 | 0.0191 | 0.3395 | -0.0655 | 0.2783 | 0.30357 | discharge/export
90 | -0.1408 | 0.3822 | -0.2254 | 0.321 | 0.3822 | discharge/export
120 | -0.2406 | 0.3623 | -0.3252 | 0.3011 | 0.43406 | discharge/export
150 | -0.2423 | 0.3613 | -0.3269 | 0.3001 | 0.39049 | discharge/export
180 | -0.2438 | 0.1505 | -0.3284 | 0.0893 | 0.2438 | discharge/export
210 | -0.2325 | -0.2319 | -0.3171 | -0.2931 | 0.3173 | discharge/export
240 | -0.2198 | -0.2428 | -0.3044 | -0.304 | 0.32017 | discharge/export
270 | -0.1347 | -0.2648 | -0.2193 | -0.326 | 0.2648 | discharge/export
300 | 0.0195 | -0.222 | -0.0651 | -0.2832 | 0.20201 | discharge/export
330 | 0.138 | -0.1034 | 0.0534 | -0.1646 | 0.17121 | charge/import
(close) | 0.1815 | 0.059 | 0.0969 | -0.0022
Interpretation (all computed live):
P width (MW) |  | 0.4253
import-reach (charge) |  | 0.0969
export-reach (dischg) |  | 0.3284
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P11_05h00
TR9 rolling FOR — period 11 = 05:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -0.1413 | B_Q (MVAr) = | 0.0585
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -0.0594 | 0.0621 | 0.0819 | 0.0036 | -0.0594 | charge/import
30 | -0.1039 | 0.226 | 0.0374 | 0.1675 | 0.02302 | charge/import
60 | -0.2218 | 0.3444 | -0.0805 | 0.2859 | 0.18736 | discharge/export
90 | -0.3821 | 0.3874 | -0.2408 | 0.3289 | 0.3874 | discharge/export
120 | -0.4952 | 0.3629 | -0.3539 | 0.3044 | 0.56188 | discharge/export
150 | -0.501 | 0.359 | -0.3597 | 0.3005 | 0.61338 | discharge/export
180 | -0.5033 | 0.1755 | -0.362 | 0.117 | 0.5033 | discharge/export
210 | -0.4825 | -0.2058 | -0.3412 | -0.2643 | 0.52076 | discharge/export
240 | -0.4456 | -0.2401 | -0.3043 | -0.2986 | 0.43073 | discharge/export
270 | -0.3692 | -0.2604 | -0.2279 | -0.3189 | 0.2604 | discharge/export
300 | -0.2208 | -0.2185 | -0.0795 | -0.277 | 0.078827 | discharge/export
330 | -0.1029 | -0.1005 | 0.0384 | -0.159 | -0.038864 | charge/import
(close) | -0.0594 | 0.0621 | 0.0819 | 0.0036
Interpretation (all computed live):
P width (MW) |  | 0.4439
import-reach (charge) |  | 0.0819
export-reach (dischg) |  | 0.362
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P12_05h30
TR9 rolling FOR — period 12 = 05:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -0.3813 | B_Q (MVAr) = | 0.0631
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -0.3256 | 0.0657 | 0.0557 | 0.0026 | -0.3256 | charge/import
30 | -0.3697 | 0.2308 | 0.0116 | 0.1677 | -0.20477 | charge/import
60 | -0.489 | 0.3502 | -0.1077 | 0.2871 | 0.058782 | discharge/export
90 | -0.6487 | 0.3932 | -0.2674 | 0.3301 | 0.3932 | discharge/export
120 | -0.779 | 0.362 | -0.3977 | 0.2989 | 0.703 | discharge/export
150 | -0.7999 | 0.3461 | -0.4186 | 0.283 | 0.86578 | discharge/export
180 | -0.8027 | 0.184 | -0.4214 | 0.1209 | 0.8027 | discharge/export
210 | -0.7765 | -0.153 | -0.3952 | -0.2161 | 0.74897 | discharge/export
240 | -0.7012 | -0.2307 | -0.3199 | -0.2938 | 0.55039 | discharge/export
270 | -0.6183 | -0.2546 | -0.237 | -0.3177 | 0.2546 | discharge/export
300 | -0.4862 | -0.2146 | -0.1049 | -0.2777 | -0.057251 | discharge/export
330 | -0.3692 | -0.0974 | 0.0121 | -0.1605 | -0.27104 | charge/import
(close) | -0.3256 | 0.0657 | 0.0557 | 0.0026
Interpretation (all computed live):
P width (MW) |  | 0.4771
import-reach (charge) |  | 0.0557
export-reach (dischg) |  | 0.4214
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P13_06h00
TR9 rolling FOR — period 13 = 06:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -0.6465 | B_Q (MVAr) = | 0.0681
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -0.5701 | 0.0741 | 0.0764 | 0.006 | -0.5701 | charge/import
30 | -0.6145 | 0.2415 | 0.032 | 0.1734 | -0.41142 | charge/import
60 | -0.7343 | 0.3616 | -0.0878 | 0.2935 | -0.053995 | discharge/export
90 | -0.8932 | 0.4044 | -0.2467 | 0.3363 | 0.4044 | discharge/export
120 | -1.0382 | 0.3672 | -0.3917 | 0.2991 | 0.8371 | discharge/export
150 | -1.0914 | 0.3195 | -0.4449 | 0.2514 | 1.1049 | discharge/export
180 | -1.0983 | 0.1921 | -0.4518 | 0.124 | 1.0983 | discharge/export
210 | -1.0577 | -0.0854 | -0.4112 | -0.1535 | 0.9587 | discharge/export
240 | -0.9335 | -0.2141 | -0.287 | -0.2822 | 0.65217 | discharge/export
270 | -0.8429 | -0.2411 | -0.1964 | -0.3092 | 0.2411 | discharge/export
300 | -0.7298 | -0.2051 | -0.0833 | -0.2732 | -0.18728 | discharge/export
330 | -0.6136 | -0.0886 | 0.0329 | -0.1567 | -0.48709 | charge/import
(close) | -0.5701 | 0.0741 | 0.0764 | 0.006
Interpretation (all computed live):
P width (MW) |  | 0.5282
import-reach (charge) |  | 0.0764
export-reach (dischg) |  | 0.4518
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P14_06h30
TR9 rolling FOR — period 14 = 06:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -0.8899 | B_Q (MVAr) = | 0.0787
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -0.7611 | 0.0789 | 0.1288 | 0.0002 | -0.7611 | charge/import
30 | -0.7996 | 0.2679 | 0.0903 | 0.1892 | -0.55852 | charge/import
60 | -0.917 | 0.3848 | -0.0271 | 0.3061 | -0.12525 | discharge/export
90 | -1.0754 | 0.4275 | -0.1855 | 0.3488 | 0.4275 | discharge/export
120 | -1.2249 | 0.3883 | -0.335 | 0.3096 | 0.94873 | discharge/export
150 | -1.3063 | 0.3117 | -0.4164 | 0.233 | 1.2871 | discharge/export
180 | -1.3249 | 0.2045 | -0.435 | 0.1258 | 1.3249 | discharge/export
210 | -1.2779 | -0.0035 | -0.388 | -0.0822 | 1.1084 | discharge/export
240 | -1.1045 | -0.1886 | -0.2146 | -0.2673 | 0.71558 | discharge/export
270 | -1.0124 | -0.2164 | -0.1225 | -0.2951 | 0.2164 | discharge/export
300 | -0.9117 | -0.1834 | -0.0218 | -0.2621 | -0.29702 | discharge/export
330 | -0.7981 | -0.0702 | 0.0918 | -0.1489 | -0.65607 | charge/import
(close) | -0.7611 | 0.0789 | 0.1288 | 0.0002
Interpretation (all computed live):
P width (MW) |  | 0.5638
import-reach (charge) |  | 0.1288
export-reach (dischg) |  | 0.435
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P15_07h00
TR9 rolling FOR — period 15 = 07:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -1.0713 | B_Q (MVAr) = | 0.1012
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -1.0116 | 0.0774 | 0.0597 | -0.0238 | -1.0116 | charge/import
30 | -1.0374 | 0.3156 | 0.0339 | 0.2144 | -0.74061 | charge/import
60 | -1.1291 | 0.4042 | -0.0578 | 0.303 | -0.2145 | discharge/export
90 | -1.2838 | 0.4453 | -0.2125 | 0.3441 | 0.4453 | discharge/export
120 | -1.4362 | 0.405 | -0.3649 | 0.3038 | 1.0688 | discharge/export
150 | -1.5229 | 0.323 | -0.4516 | 0.2218 | 1.4804 | discharge/export
180 | -1.5503 | 0.2124 | -0.479 | 0.1112 | 1.5503 | discharge/export
210 | -1.5025 | 0.0486 | -0.4312 | -0.0526 | 1.2769 | discharge/export
240 | -1.3016 | -0.1693 | -0.2303 | -0.2705 | 0.79742 | discharge/export
270 | -1.2104 | -0.1967 | -0.1391 | -0.2979 | 0.1967 | discharge/export
300 | -1.123 | -0.1683 | -0.0517 | -0.2695 | -0.41575 | discharge/export
330 | -1.0357 | -0.084 | 0.0356 | -0.1852 | -0.85494 | charge/import
(close) | -1.0116 | 0.0774 | 0.0597 | -0.0238
Interpretation (all computed live):
P width (MW) |  | 0.5387
import-reach (charge) |  | 0.0597
export-reach (dischg) |  | 0.479
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P16_07h30
TR9 rolling FOR — period 16 = 07:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -1.2792 | B_Q (MVAr) = | 0.1185
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -1.2052 | 0.08 | 0.074 | -0.0385 | -1.2052 | charge/import
30 | -1.2235 | 0.3954 | 0.0557 | 0.2769 | -0.86188 | charge/import
60 | -1.277 | 0.4457 | 0.0022 | 0.3272 | -0.25251 | charge/import
90 | -1.4036 | 0.4766 | -0.1244 | 0.3581 | 0.4766 | discharge/export
120 | -1.5561 | 0.4362 | -0.2769 | 0.3177 | 1.1558 | discharge/export
150 | -1.6376 | 0.3511 | -0.3584 | 0.2326 | 1.5938 | discharge/export
180 | -1.6686 | 0.2446 | -0.3894 | 0.1261 | 1.6686 | discharge/export
210 | -1.6226 | 0.0932 | -0.3434 | -0.0253 | 1.3586 | discharge/export
240 | -1.4062 | -0.1378 | -0.127 | -0.2563 | 0.82244 | discharge/export
270 | -1.3223 | -0.1625 | -0.0431 | -0.281 | 0.1625 | discharge/export
300 | -1.2709 | -0.1475 | 0.0083 | -0.266 | -0.50771 | charge/import
330 | -1.2211 | -0.1 | 0.0581 | -0.2185 | -1.0075 | charge/import
(close) | -1.2052 | 0.08 | 0.074 | -0.0385
Interpretation (all computed live):
P width (MW) |  | 0.4634
import-reach (charge) |  | 0.074
export-reach (dischg) |  | 0.3894
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P17_08h00
TR9 rolling FOR — period 17 = 08:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -1.399 | B_Q (MVAr) = | 0.1494
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -1.3987 | 0.1209 | 0.0003 | -0.0285 | -1.3987 | charge/import
30 | -1.4173 | 0.4488 | -0.0183 | 0.2994 | -1.003 | discharge/export
60 | -1.4506 | 0.4805 | -0.0516 | 0.3311 | -0.30917 | discharge/export
90 | -1.545 | 0.5011 | -0.146 | 0.3517 | 0.5011 | discharge/export
120 | -1.6891 | 0.4647 | -0.2901 | 0.3153 | 1.247 | discharge/export
150 | -1.7717 | 0.3742 | -0.3727 | 0.2248 | 1.7214 | discharge/export
180 | -1.8061 | 0.2599 | -0.4071 | 0.1105 | 1.8061 | discharge/export
210 | -1.7656 | 0.1399 | -0.3666 | -0.0095 | 1.4591 | discharge/export
240 | -1.5289 | -0.1046 | -0.1299 | -0.254 | 0.85504 | discharge/export
270 | -1.4644 | -0.1261 | -0.0654 | -0.2755 | 0.1261 | discharge/export
300 | -1.4323 | -0.1192 | -0.0333 | -0.2686 | -0.61292 | discharge/export
330 | -1.413 | -0.0995 | -0.014 | -0.2489 | -1.1739 | discharge/export
(close) | -1.3987 | 0.1209 | 0.0003 | -0.0285
Interpretation (all computed live):
P width (MW) |  | 0.4074
import-reach (charge) |  | 0.0003
export-reach (dischg) |  | 0.4071
verdict |  | one-sided → discharge/export only (no import headroom)
what stops it |  | blocked at 0°: Vmax there = 1.09998 pu → over-voltage limit is active
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P18_08h30
TR9 rolling FOR — period 18 = 08:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -1.5392 | B_Q (MVAr) = | 0.1733
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -1.6019 | 0.1667 | -0.0627 | -0.0066 | -1.6019 | discharge/export
30 | -1.617 | 0.4768 | -0.0778 | 0.3035 | -1.162 | discharge/export
60 | -1.639 | 0.4979 | -0.0998 | 0.3246 | -0.38831 | discharge/export
90 | -1.7135 | 0.5122 | -0.1743 | 0.3389 | 0.5122 | discharge/export
120 | -1.8528 | 0.4776 | -0.3136 | 0.3043 | 1.34 | discharge/export
150 | -1.9365 | 0.3859 | -0.3973 | 0.2126 | 1.87 | discharge/export
180 | -1.9716 | 0.2697 | -0.4324 | 0.0964 | 1.9716 | discharge/export
210 | -1.9374 | 0.1698 | -0.3982 | -0.0035 | 1.5929 | discharge/export
240 | -1.7004 | -0.0779 | -0.1612 | -0.2512 | 0.91766 | discharge/export
270 | -1.6485 | -0.0947 | -0.1093 | -0.268 | 0.0947 | discharge/export
300 | -1.6178 | -0.0892 | -0.0786 | -0.2625 | -0.73165 | discharge/export
330 | -1.6107 | -0.0826 | -0.0715 | -0.2559 | -1.3536 | discharge/export
(close) | -1.6019 | 0.1667 | -0.0627 | -0.0066
Interpretation (all computed live):
P width (MW) |  | 0.3697
import-reach (charge) |  | 0
export-reach (dischg) |  | 0.4324
verdict |  | one-sided → discharge/export only (no import headroom)
what stops it |  | blocked at 0°: Vmax there = 1.09997 pu → over-voltage limit is active
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P19_09h00
TR9 rolling FOR — period 19 = 09:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -1.7076 | B_Q (MVAr) = | 0.1842
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -1.7447 | 0.1942 | -0.0371 | 0.01 | -1.7447 | discharge/export
30 | -1.7591 | 0.5038 | -0.0515 | 0.3196 | -1.2715 | discharge/export
60 | -1.7727 | 0.5159 | -0.0651 | 0.3317 | -0.43957 | discharge/export
90 | -1.8356 | 0.5267 | -0.128 | 0.3425 | 0.5267 | discharge/export
120 | -1.9667 | 0.4951 | -0.2591 | 0.3109 | 1.4121 | discharge/export
150 | -2.052 | 0.4044 | -0.3444 | 0.2202 | 1.9793 | discharge/export
180 | -2.0897 | 0.2824 | -0.3821 | 0.0982 | 2.0897 | discharge/export
210 | -2.0581 | 0.1871 | -0.3505 | 0.0029 | 1.6888 | discharge/export
240 | -1.8299 | -0.0492 | -0.1223 | -0.2334 | 0.95756 | discharge/export
270 | -1.7843 | -0.0641 | -0.0767 | -0.2483 | 0.0641 | discharge/export
300 | -1.7551 | -0.06 | -0.0475 | -0.2442 | -0.82559 | discharge/export
330 | -1.7529 | -0.0579 | -0.0453 | -0.2421 | -1.4891 | discharge/export
(close) | -1.7447 | 0.1942 | -0.0371 | 0.01
Interpretation (all computed live):
P width (MW) |  | 0.345
import-reach (charge) |  | 0
export-reach (dischg) |  | 0.3821
verdict |  | one-sided → discharge/export only (no import headroom)
what stops it |  | blocked at 0°: Vmax there = 1.09999 pu → over-voltage limit is active
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P20_09h30
TR9 rolling FOR — period 20 = 09:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -1.8297 | B_Q (MVAr) = | 0.1985
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -1.9368 | 0.2171 | -0.1071 | 0.0186 | -1.9368 | discharge/export
30 | -1.9515 | 0.5111 | -0.1218 | 0.3126 | -1.4345 | discharge/export
60 | -1.9592 | 0.5183 | -0.1295 | 0.3198 | -0.53074 | discharge/export
90 | -2.0155 | 0.5266 | -0.1858 | 0.3281 | 0.5266 | discharge/export
120 | -2.1263 | 0.5025 | -0.2966 | 0.304 | 1.4983 | discharge/export
150 | -2.2239 | 0.3984 | -0.3942 | 0.1999 | 2.1252 | discharge/export
180 | -2.2601 | 0.2789 | -0.4304 | 0.0804 | 2.2601 | discharge/export
210 | -2.2297 | 0.1958 | -0.4 | -0.0027 | 1.8331 | discharge/export
240 | -2.0115 | -0.0287 | -0.1818 | -0.2272 | 1.0306 | discharge/export
270 | -1.9615 | -0.0428 | -0.1318 | -0.2413 | 0.0428 | discharge/export
300 | -1.9459 | -0.0404 | -0.1162 | -0.2389 | -0.93796 | discharge/export
330 | -1.9454 | -0.0399 | -0.1157 | -0.2384 | -1.6648 | discharge/export
(close) | -1.9368 | 0.2171 | -0.1071 | 0.0186
Interpretation (all computed live):
P width (MW) |  | 0.3233
import-reach (charge) |  | 0
export-reach (dischg) |  | 0.4304
verdict |  | one-sided → discharge/export only (no import headroom)
what stops it |  | blocked at 0°: Vmax there = 1.10000 pu → over-voltage limit is active
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P21_10h00
TR9 rolling FOR — period 21 = 10:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -2.0084 | B_Q (MVAr) = | 0.1978
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -2.0919 | 0.2454 | -0.0835 | 0.0476 | -2.0919 | discharge/export
30 | -2.1075 | 0.516 | -0.0991 | 0.3182 | -1.5671 | discharge/export
60 | -2.1131 | 0.5211 | -0.1047 | 0.3233 | -0.60526 | discharge/export
90 | -2.1619 | 0.5272 | -0.1535 | 0.3294 | 0.5272 | discharge/export
120 | -2.2578 | 0.5069 | -0.2494 | 0.3091 | 1.5679 | discharge/export
150 | -2.3591 | 0.3995 | -0.3507 | 0.2017 | 2.2428 | discharge/export
180 | -2.3956 | 0.2806 | -0.3872 | 0.0828 | 2.3956 | discharge/export
210 | -2.3739 | 0.2154 | -0.3655 | 0.0176 | 1.9482 | discharge/export
240 | -2.1623 | -0.0034 | -0.1539 | -0.2012 | 1.0841 | discharge/export
270 | -2.1143 | -0.0163 | -0.1059 | -0.2141 | 0.0163 | discharge/export
300 | -2.1012 | -0.0147 | -0.0928 | -0.2125 | -1.0379 | discharge/export
330 | -2.1008 | -0.0144 | -0.0924 | -0.2122 | -1.8121 | discharge/export
(close) | -2.0919 | 0.2454 | -0.0835 | 0.0476
Interpretation (all computed live):
P width (MW) |  | 0.3037
import-reach (charge) |  | 0
export-reach (dischg) |  | 0.3872
verdict |  | one-sided → discharge/export only (no import headroom)
what stops it |  | blocked at 0°: Vmax there = 1.10000 pu → over-voltage limit is active
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P22_10h30
TR9 rolling FOR — period 22 = 10:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -2.1535 | B_Q (MVAr) = | 0.1977
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -2.182 | 0.2528 | -0.0285 | 0.0551 | -2.182 | discharge/export
30 | -2.1974 | 0.5193 | -0.0439 | 0.3216 | -1.6434 | discharge/export
60 | -2.202 | 0.5236 | -0.0485 | 0.3259 | -0.64755 | discharge/export
90 | -2.2462 | 0.5282 | -0.0927 | 0.3305 | 0.5282 | discharge/export
120 | -2.3434 | 0.5073 | -0.1899 | 0.3096 | 1.611 | discharge/export
150 | -2.4451 | 0.3995 | -0.2916 | 0.2018 | 2.3173 | discharge/export
180 | -2.4799 | 0.2818 | -0.3264 | 0.0841 | 2.4799 | discharge/export
210 | -2.4623 | 0.227 | -0.3088 | 0.0293 | 2.0189 | discharge/export
240 | -2.2563 | 0.0086 | -0.1028 | -0.1891 | 1.1207 | discharge/export
270 | -2.2 | -0.0067 | -0.0465 | -0.2044 | 0.0067 | discharge/export
300 | -2.1916 | -0.0057 | -0.0381 | -0.2034 | -1.0909 | discharge/export
330 | -2.1913 | -0.0055 | -0.0378 | -0.2032 | -1.895 | discharge/export
(close) | -2.182 | 0.2528 | -0.0285 | 0.0551
Interpretation (all computed live):
P width (MW) |  | 0.2979
import-reach (charge) |  | 0
export-reach (dischg) |  | 0.3264
verdict |  | one-sided → discharge/export only (no import headroom)
what stops it |  | blocked at 0°: Vmax there = 1.10000 pu → over-voltage limit is active
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P23_11h00
TR9 rolling FOR — period 23 = 11:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -2.2382 | B_Q (MVAr) = | 0.1988
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -2.1943 | 0.2633 | 0.0439 | 0.0645 | -2.1943 | charge/import
30 | -2.2089 | 0.5277 | 0.0293 | 0.3289 | -1.6491 | charge/import
60 | -2.2122 | 0.5306 | 0.026 | 0.3318 | -0.64659 | charge/import
90 | -2.2554 | 0.535 | -0.0172 | 0.3362 | 0.535 | discharge/export
120 | -2.3519 | 0.5147 | -0.1137 | 0.3159 | 1.6217 | discharge/export
150 | -2.455 | 0.4074 | -0.2168 | 0.2086 | 2.3298 | discharge/export
180 | -2.4908 | 0.2878 | -0.2526 | 0.089 | 2.4908 | discharge/export
210 | -2.4703 | 0.2276 | -0.2321 | 0.0288 | 2.0255 | discharge/export
240 | -2.2595 | 0.0087 | -0.0213 | -0.1901 | 1.1222 | discharge/export
270 | -2.2095 | -0.0063 | 0.0287 | -0.2051 | 0.0063 | charge/import
300 | -2.2034 | -0.0055 | 0.0348 | -0.2043 | -1.0969 | charge/import
330 | -2.2034 | -0.0055 | 0.0348 | -0.2043 | -1.9055 | charge/import
(close) | -2.1943 | 0.2633 | 0.0439 | 0.0645
Interpretation (all computed live):
P width (MW) |  | 0.2965
import-reach (charge) |  | 0.0439
export-reach (dischg) |  | 0.2526
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P24_11h30
TR9 rolling FOR — period 24 = 11:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -2.2476 | B_Q (MVAr) = | 0.2056
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -2.2023 | 0.2622 | 0.0453 | 0.0566 | -2.2023 | charge/import
30 | -2.2181 | 0.5283 | 0.0295 | 0.3227 | -1.6568 | charge/import
60 | -2.2227 | 0.5326 | 0.0249 | 0.327 | -0.6501 | charge/import
90 | -2.2673 | 0.5374 | -0.0197 | 0.3318 | 0.5374 | discharge/export
120 | -2.3534 | 0.5184 | -0.1058 | 0.3128 | 1.6256 | discharge/export
150 | -2.4545 | 0.4106 | -0.2069 | 0.205 | 2.331 | discharge/export
180 | -2.492 | 0.2903 | -0.2444 | 0.0847 | 2.492 | discharge/export
210 | -2.4748 | 0.2379 | -0.2272 | 0.0323 | 2.0243 | discharge/export
240 | -2.269 | 0.0201 | -0.0214 | -0.1855 | 1.1171 | discharge/export
270 | -2.2187 | 0.0051 | 0.0289 | -0.2005 | -0.0051 | charge/import
300 | -2.2114 | 0.0055 | 0.0362 | -0.2001 | -1.1105 | charge/import
330 | -2.2113 | 0.0055 | 0.0363 | -0.2001 | -1.9178 | charge/import
(close) | -2.2023 | 0.2622 | 0.0453 | 0.0566
Interpretation (all computed live):
P width (MW) |  | 0.2897
import-reach (charge) |  | 0.0453
export-reach (dischg) |  | 0.2444
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P25_12h00
TR9 rolling FOR — period 25 = 12:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -2.2582 | B_Q (MVAr) = | 0.2073
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -2.259 | 0.2471 | -0.0008 | 0.0398 | -2.259 | discharge/export
30 | -2.274 | 0.515 | -0.0158 | 0.3077 | -1.7118 | discharge/export
60 | -2.2778 | 0.5183 | -0.0196 | 0.311 | -0.69004 | discharge/export
90 | -2.3207 | 0.5227 | -0.0625 | 0.3154 | 0.5227 | discharge/export
120 | -2.4081 | 0.5033 | -0.1499 | 0.296 | 1.6399 | discharge/export
150 | -2.5088 | 0.396 | -0.2506 | 0.1887 | 2.3707 | discharge/export
180 | -2.5456 | 0.2774 | -0.2874 | 0.0701 | 2.5456 | discharge/export
210 | -2.5269 | 0.2235 | -0.2687 | 0.0162 | 2.0766 | discharge/export
240 | -2.3268 | 0.0122 | -0.0686 | -0.1951 | 1.1528 | discharge/export
270 | -2.2763 | -0.0009 | -0.0181 | -0.2082 | 0.0009 | discharge/export
300 | -2.2673 | -0.0003 | -0.0091 | -0.2076 | -1.1334 | discharge/export
330 | -2.2673 | -0.0003 | -0.0091 | -0.2076 | -1.9634 | discharge/export
(close) | -2.259 | 0.2471 | -0.0008 | 0.0398
Interpretation (all computed live):
P width (MW) |  | 0.2866
import-reach (charge) |  | 0
export-reach (dischg) |  | 0.2874
verdict |  | one-sided → discharge/export only (no import headroom)
what stops it |  | blocked at 0°: Vmax there = 1.10000 pu → over-voltage limit is active
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P26_12h30
TR9 rolling FOR — period 26 = 12:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -2.3117 | B_Q (MVAr) = | 0.1926
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -2.1733 | 0.2449 | 0.1384 | 0.0523 | -2.1733 | charge/import
30 | -2.1883 | 0.515 | 0.1234 | 0.3224 | -1.6376 | charge/import
60 | -2.1907 | 0.5172 | 0.121 | 0.3246 | -0.64744 | charge/import
90 | -2.2332 | 0.5215 | 0.0785 | 0.3289 | 0.5215 | charge/import
120 | -2.3327 | 0.5003 | -0.021 | 0.3077 | 1.5996 | discharge/export
150 | -2.4318 | 0.3941 | -0.1201 | 0.2015 | 2.3031 | discharge/export
180 | -2.4667 | 0.2775 | -0.155 | 0.0849 | 2.4667 | discharge/export
210 | -2.444 | 0.2162 | -0.1323 | 0.0236 | 2.0085 | discharge/export
240 | -2.2511 | 0.0095 | 0.0606 | -0.1831 | 1.1173 | charge/import
270 | -2.1928 | -0.0052 | 0.1189 | -0.1978 | 0.0052 | charge/import
300 | -2.1821 | -0.0042 | 0.1296 | -0.1968 | -1.0874 | charge/import
330 | -2.182 | -0.0042 | 0.1297 | -0.1968 | -1.8876 | charge/import
(close) | -2.1733 | 0.2449 | 0.1384 | 0.0523
Interpretation (all computed live):
P width (MW) |  | 0.2934
import-reach (charge) |  | 0.1384
export-reach (dischg) |  | 0.155
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P27_13h00
TR9 rolling FOR — period 27 = 13:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -2.2251 | B_Q (MVAr) = | 0.1918
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -2.1207 | 0.2264 | 0.1044 | 0.0346 | -2.1207 | charge/import
30 | -2.1353 | 0.5012 | 0.0898 | 0.3094 | -1.5986 | charge/import
60 | -2.1383 | 0.5038 | 0.0868 | 0.312 | -0.63285 | charge/import
90 | -2.1803 | 0.5079 | 0.0448 | 0.3161 | 0.5079 | charge/import
120 | -2.2892 | 0.4848 | -0.0641 | 0.293 | 1.5644 | discharge/export
150 | -2.3816 | 0.3865 | -0.1565 | 0.1947 | 2.2558 | discharge/export
180 | -2.4185 | 0.2631 | -0.1934 | 0.0713 | 2.4185 | discharge/export
210 | -2.3969 | 0.2048 | -0.1718 | 0.013 | 1.9734 | discharge/export
240 | -2.1877 | -0.0142 | 0.0374 | -0.206 | 1.1061 | charge/import
270 | -2.1373 | -0.0279 | 0.0878 | -0.2197 | 0.0279 | charge/import
300 | -2.1287 | -0.027 | 0.0964 | -0.2188 | -1.041 | charge/import
330 | -2.1287 | -0.027 | 0.0964 | -0.2188 | -1.83 | charge/import
(close) | -2.1207 | 0.2264 | 0.1044 | 0.0346
Interpretation (all computed live):
P width (MW) |  | 0.2978
import-reach (charge) |  | 0.1044
export-reach (dischg) |  | 0.1934
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P28_13h30
TR9 rolling FOR — period 28 = 13:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -2.172 | B_Q (MVAr) = | 0.1783
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -1.996 | 0.2162 | 0.176 | 0.0379 | -1.996 | charge/import
30 | -2.0099 | 0.4984 | 0.1621 | 0.3201 | -1.4914 | charge/import
60 | -2.0122 | 0.5005 | 0.1598 | 0.3222 | -0.57265 | charge/import
90 | -2.053 | 0.5043 | 0.119 | 0.326 | 0.5043 | charge/import
120 | -2.1648 | 0.4801 | 0.0072 | 0.3018 | 1.4982 | charge/import
150 | -2.2626 | 0.376 | -0.0906 | 0.1977 | 2.1475 | discharge/export
180 | -2.2979 | 0.2581 | -0.1259 | 0.0798 | 2.2979 | discharge/export
210 | -2.2698 | 0.1839 | -0.0978 | 0.0056 | 1.8738 | discharge/export
240 | -2.0626 | -0.03 | 0.1094 | -0.2083 | 1.0573 | charge/import
270 | -2.012 | -0.0437 | 0.16 | -0.222 | 0.0437 | charge/import
300 | -2.0039 | -0.0431 | 0.1681 | -0.2214 | -0.96462 | charge/import
330 | -2.0039 | -0.0431 | 0.1681 | -0.2214 | -1.7139 | charge/import
(close) | -1.996 | 0.2162 | 0.176 | 0.0379
Interpretation (all computed live):
P width (MW) |  | 0.3019
import-reach (charge) |  | 0.176
export-reach (dischg) |  | 0.1259
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P29_14h00
TR9 rolling FOR — period 29 = 14:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -2.0454 | B_Q (MVAr) = | 0.1752
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -1.844 | 0.2122 | 0.2014 | 0.037 | -1.844 | charge/import
30 | -1.8575 | 0.4926 | 0.1879 | 0.3174 | -1.3623 | charge/import
60 | -1.8588 | 0.4935 | 0.1866 | 0.3183 | -0.50202 | charge/import
90 | -1.8987 | 0.4971 | 0.1467 | 0.3219 | 0.4971 | charge/import
120 | -2.0199 | 0.47 | 0.0255 | 0.2948 | 1.417 | charge/import
150 | -2.1153 | 0.3678 | -0.0699 | 0.1926 | 2.0158 | discharge/export
180 | -2.15 | 0.2543 | -0.1046 | 0.0791 | 2.15 | discharge/export
210 | -2.1227 | 0.1726 | -0.0773 | -0.0026 | 1.752 | discharge/export
240 | -1.9133 | -0.0475 | 0.1321 | -0.2227 | 0.99779 | charge/import
270 | -1.8614 | -0.0625 | 0.184 | -0.2377 | 0.0625 | charge/import
300 | -1.8522 | -0.0618 | 0.1932 | -0.237 | -0.87258 | charge/import
330 | -1.8522 | -0.0618 | 0.1932 | -0.237 | -1.5732 | charge/import
(close) | -1.844 | 0.2122 | 0.2014 | 0.037
Interpretation (all computed live):
P width (MW) |  | 0.306
import-reach (charge) |  | 0.2014
export-reach (dischg) |  | 0.1046
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P30_14h30
TR9 rolling FOR — period 30 = 14:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -1.8919 | B_Q (MVAr) = | 0.1684
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -1.6777 | 0.1838 | 0.2142 | 0.0154 | -1.6777 | charge/import
30 | -1.6899 | 0.4896 | 0.202 | 0.3212 | -1.2187 | charge/import
60 | -1.6899 | 0.4896 | 0.202 | 0.3212 | -0.42094 | charge/import
90 | -1.7287 | 0.4928 | 0.1632 | 0.3244 | 0.4928 | charge/import
120 | -1.864 | 0.46 | 0.0279 | 0.2916 | 1.3304 | charge/import
150 | -1.953 | 0.3694 | -0.0611 | 0.201 | 1.876 | discharge/export
180 | -1.9896 | 0.2548 | -0.0977 | 0.0864 | 1.9896 | discharge/export
210 | -1.9571 | 0.1479 | -0.0652 | -0.0205 | 1.6209 | discharge/export
240 | -1.7497 | -0.0681 | 0.1422 | -0.2365 | 0.93383 | charge/import
270 | -1.6934 | -0.0848 | 0.1985 | -0.2532 | 0.0848 | charge/import
300 | -1.6852 | -0.0842 | 0.2067 | -0.2526 | -0.76968 | charge/import
330 | -1.6852 | -0.0842 | 0.2067 | -0.2526 | -1.4173 | charge/import
(close) | -1.6777 | 0.1838 | 0.2142 | 0.0154
Interpretation (all computed live):
P width (MW) |  | 0.3119
import-reach (charge) |  | 0.2142
export-reach (dischg) |  | 0.0977
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P31_15h00
TR9 rolling FOR — period 31 = 15:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -1.723 | B_Q (MVAr) = | 0.1648
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -1.4844 | 0.1808 | 0.2386 | 0.016 | -1.4844 | charge/import
30 | -1.4959 | 0.4814 | 0.2271 | 0.3166 | -1.0548 | charge/import
60 | -1.4963 | 0.4817 | 0.2267 | 0.3169 | -0.33099 | charge/import
90 | -1.5354 | 0.4848 | 0.1876 | 0.32 | 0.4848 | charge/import
120 | -1.6804 | 0.448 | 0.0426 | 0.2832 | 1.2282 | charge/import
150 | -1.765 | 0.3612 | -0.042 | 0.1964 | 1.7091 | discharge/export
180 | -1.8031 | 0.2416 | -0.0801 | 0.0768 | 1.8031 | discharge/export
210 | -1.7685 | 0.1351 | -0.0455 | -0.0297 | 1.464 | discharge/export
240 | -1.5546 | -0.0878 | 0.1684 | -0.2526 | 0.85334 | charge/import
270 | -1.5025 | -0.1055 | 0.2205 | -0.2703 | 0.1055 | charge/import
300 | -1.4915 | -0.1046 | 0.2315 | -0.2694 | -0.65516 | charge/import
330 | -1.4915 | -0.1046 | 0.2315 | -0.2694 | -1.2394 | charge/import
(close) | -1.4844 | 0.1808 | 0.2386 | 0.016
Interpretation (all computed live):
P width (MW) |  | 0.3187
import-reach (charge) |  | 0.2386
export-reach (dischg) |  | 0.0801
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P32_15h30
TR9 rolling FOR — period 32 = 15:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -1.5298 | B_Q (MVAr) = | 0.1571
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -1.1769 | 0.1653 | 0.3529 | 0.0082 | -1.1769 | charge/import
30 | -1.1865 | 0.4888 | 0.3433 | 0.3317 | -0.78314 | charge/import
60 | -1.1879 | 0.4902 | 0.3419 | 0.3331 | -0.16942 | charge/import
90 | -1.2237 | 0.4926 | 0.3061 | 0.3355 | 0.4926 | charge/import
120 | -1.3791 | 0.4509 | 0.1507 | 0.2938 | 1.08 | charge/import
150 | -1.4749 | 0.3564 | 0.0549 | 0.1993 | 1.4555 | charge/import
180 | -1.5085 | 0.2518 | 0.0213 | 0.0947 | 1.5085 | charge/import
210 | -1.4708 | 0.1257 | 0.059 | -0.0314 | 1.2109 | charge/import
240 | -1.258 | -0.0976 | 0.2718 | -0.2547 | 0.71352 | charge/import
270 | -1.1985 | -0.1173 | 0.3313 | -0.2744 | 0.1173 | charge/import
300 | -1.1847 | -0.1157 | 0.3451 | -0.2728 | -0.49215 | charge/import
330 | -1.1839 | -0.1149 | 0.3459 | -0.272 | -0.96784 | charge/import
(close) | -1.1769 | 0.1653 | 0.3529 | 0.0082
Interpretation (all computed live):
P width (MW) |  | 0.3316
import-reach (charge) |  | 0.3529
export-reach (dischg) |  | 0
verdict |  | one-sided → charge/import only (no export headroom)
what stops it |  | blocked at 180°: Vmax there = 1.10000 pu → over-voltage limit is active
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P33_16h00
TR9 rolling FOR — period 33 = 16:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -1.2201 | B_Q (MVAr) = | 0.1659
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -0.8247 | 0.1535 | 0.3954 | -0.0124 | -0.8247 | charge/import
30 | -0.8315 | 0.4966 | 0.3886 | 0.3307 | -0.4718 | charge/import
60 | -0.8321 | 0.497 | 0.388 | 0.3311 | 0.014365 | charge/import
90 | -0.8674 | 0.4994 | 0.3527 | 0.3335 | 0.4994 | charge/import
120 | -1.025 | 0.4571 | 0.1951 | 0.2912 | 0.90836 | charge/import
150 | -1.1364 | 0.3487 | 0.0837 | 0.1828 | 1.1585 | charge/import
180 | -1.1669 | 0.248 | 0.0532 | 0.0821 | 1.1669 | charge/import
210 | -1.1232 | 0.1016 | 0.0969 | -0.0643 | 0.92192 | charge/import
240 | -0.9214 | -0.1091 | 0.2987 | -0.275 | 0.55518 | charge/import
270 | -0.8388 | -0.1355 | 0.3813 | -0.3014 | 0.1355 | charge/import
300 | -0.8312 | -0.1344 | 0.3889 | -0.3003 | -0.29921 | charge/import
330 | -0.831 | -0.1342 | 0.3891 | -0.3001 | -0.65257 | charge/import
(close) | -0.8247 | 0.1535 | 0.3954 | -0.0124
Interpretation (all computed live):
P width (MW) |  | 0.3422
import-reach (charge) |  | 0.3954
export-reach (dischg) |  | 0
verdict |  | one-sided → charge/import only (no export headroom)
what stops it |  | blocked at 180°: Vmax there = 1.10000 pu → over-voltage limit is active
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P34_16h30
TR9 rolling FOR — period 34 = 16:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -0.8661 | B_Q (MVAr) = | 0.1739
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -0.5049 | 0.1584 | 0.3612 | -0.0155 | -0.5049 | charge/import
30 | -0.5099 | 0.5014 | 0.3562 | 0.3275 | -0.19089 | charge/import
60 | -0.5105 | 0.5017 | 0.3556 | 0.3278 | 0.17923 | charge/import
90 | -0.5472 | 0.5047 | 0.3189 | 0.3308 | 0.5047 | charge/import
120 | -0.7064 | 0.462 | 0.1597 | 0.2881 | 0.7533 | charge/import
150 | -0.8217 | 0.3481 | 0.0444 | 0.1742 | 0.88566 | charge/import
180 | -0.8542 | 0.2351 | 0.0119 | 0.0612 | 0.8542 | charge/import
210 | -0.8116 | 0.0893 | 0.0545 | -0.0846 | 0.65822 | charge/import
240 | -0.62 | -0.1129 | 0.2461 | -0.2868 | 0.40777 | charge/import
270 | -0.5312 | -0.1404 | 0.3349 | -0.3143 | 0.1404 | charge/import
300 | -0.5142 | -0.1376 | 0.3519 | -0.3115 | -0.13793 | charge/import
330 | -0.5106 | -0.1352 | 0.3555 | -0.3091 | -0.37459 | charge/import
(close) | -0.5049 | 0.1584 | 0.3612 | -0.0155
Interpretation (all computed live):
P width (MW) |  | 0.3493
import-reach (charge) |  | 0.3612
export-reach (dischg) |  | 0
verdict |  | one-sided → charge/import only (no export headroom)
what stops it |  | blocked at 180°: Vmax there = 1.10000 pu → over-voltage limit is active
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P35_17h00
TR9 rolling FOR — period 35 = 17:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -0.5473 | B_Q (MVAr) = | 0.1799
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | -0.0567 | 0.3397 | 0.4906 | 0.1598 | -0.0567 | charge/import
30 | -0.0586 | 0.5311 | 0.4887 | 0.3512 | 0.2148 | charge/import
60 | -0.0594 | 0.5316 | 0.4879 | 0.3517 | 0.43068 | charge/import
90 | -0.0971 | 0.5349 | 0.4502 | 0.355 | 0.5349 | charge/import
120 | -0.2589 | 0.4914 | 0.2884 | 0.3115 | 0.55501 | charge/import
150 | -0.3779 | 0.3727 | 0.1694 | 0.1928 | 0.51362 | charge/import
180 | -0.4133 | 0.2432 | 0.134 | 0.0633 | 0.4133 | charge/import
210 | -0.371 | 0.0904 | 0.1763 | -0.0895 | 0.2761 | charge/import
240 | -0.2098 | -0.079 | 0.3375 | -0.2589 | 0.17332 | charge/import
270 | -0.0972 | -0.112 | 0.4501 | -0.2919 | 0.112 | charge/import
300 | -0.0636 | -0.109 | 0.4837 | -0.2889 | 0.062597 | charge/import
330 | -0.0618 | -0.1076 | 0.4855 | -0.2875 | 0.00027963 | charge/import
(close) | -0.0567 | 0.3397 | 0.4906 | 0.1598
Interpretation (all computed live):
P width (MW) |  | 0.3566
import-reach (charge) |  | 0.4906
export-reach (dischg) |  | 0
verdict |  | one-sided → charge/import only (no export headroom)
what stops it |  | blocked at 180°: Vmax there = 1.10000 pu → over-voltage limit is active
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P36_17h30
TR9 rolling FOR — period 36 = 17:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | -0.0998 | B_Q (MVAr) = | 0.2113
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 0.1821 | 0.3378 | 0.2819 | 0.1265 | 0.1821 | charge/import
30 | 0.1815 | 0.5167 | 0.2813 | 0.3054 | 0.41553 | charge/import
60 | 0.178 | 0.52 | 0.2778 | 0.3087 | 0.53933 | charge/import
90 | 0.1358 | 0.5242 | 0.2356 | 0.3129 | 0.5242 | charge/import
120 | -0.0274 | 0.4804 | 0.0724 | 0.2691 | 0.42974 | charge/import
150 | -0.1478 | 0.36 | -0.048 | 0.1487 | 0.308 | discharge/export
180 | -0.1842 | 0.2274 | -0.0844 | 0.0161 | 0.1842 | discharge/export
210 | -0.1421 | 0.0632 | -0.0423 | -0.1481 | 0.091462 | discharge/export
240 | 0.0036 | -0.0886 | 0.1034 | -0.2999 | 0.07493 | charge/import
270 | 0.1298 | -0.1217 | 0.2296 | -0.333 | 0.1217 | charge/import
300 | 0.1745 | -0.1167 | 0.2743 | -0.328 | 0.18832 | charge/import
330 | 0.1775 | -0.114 | 0.2773 | -0.3253 | 0.21072 | charge/import
(close) | 0.1821 | 0.3378 | 0.2819 | 0.1265
Interpretation (all computed live):
P width (MW) |  | 0.3663
import-reach (charge) |  | 0.2819
export-reach (dischg) |  | 0.0844
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P37_18h00
TR9 rolling FOR — period 37 = 18:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 0.1318 | B_Q (MVAr) = | 0.2013
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 0.4123 | 0.5079 | 0.2805 | 0.3066 | 0.4123 | charge/import
30 | 0.4122 | 0.508 | 0.2804 | 0.3067 | 0.61098 | charge/import
60 | 0.4095 | 0.5104 | 0.2777 | 0.3091 | 0.64677 | charge/import
90 | 0.3661 | 0.5151 | 0.2343 | 0.3138 | 0.5151 | charge/import
120 | 0.2008 | 0.4706 | 0.069 | 0.2693 | 0.30715 | charge/import
150 | 0.0794 | 0.3493 | -0.0524 | 0.148 | 0.10589 | discharge/export
180 | 0.0381 | 0.2059 | -0.0937 | 0.0046 | -0.0381 | discharge/export
210 | 0.0822 | 0.0393 | -0.0496 | -0.162 | -0.090837 | discharge/export
240 | 0.2127 | -0.0934 | 0.0809 | -0.2947 | -0.025463 | charge/import
270 | 0.3546 | -0.1291 | 0.2228 | -0.3304 | 0.1291 | charge/import
300 | 0.4038 | -0.1237 | 0.272 | -0.325 | 0.30903 | charge/import
330 | 0.4066 | -0.1211 | 0.2748 | -0.3224 | 0.41268 | charge/import
(close) | 0.4123 | 0.5079 | 0.2805 | 0.3066
Interpretation (all computed live):
P width (MW) |  | 0.3742
import-reach (charge) |  | 0.2805
export-reach (dischg) |  | 0.0937
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P38_18h30
TR9 rolling FOR — period 38 = 18:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 0.3603 | B_Q (MVAr) = | 0.193
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 0.67 | 0.5068 | 0.3097 | 0.3138 | 0.67 | charge/import
30 | 0.6697 | 0.5077 | 0.3094 | 0.3147 | 0.83383 | charge/import
60 | 0.6673 | 0.5097 | 0.307 | 0.3167 | 0.77506 | charge/import
90 | 0.6154 | 0.5168 | 0.2551 | 0.3238 | 0.5168 | charge/import
120 | 0.4493 | 0.4721 | 0.089 | 0.2791 | 0.1842 | charge/import
150 | 0.3275 | 0.3505 | -0.0328 | 0.1575 | -0.10837 | discharge/export
180 | 0.2869 | 0.2075 | -0.0734 | 0.0145 | -0.2869 | discharge/export
210 | 0.3342 | 0.033 | -0.0261 | -0.16 | -0.30593 | discharge/export
240 | 0.4555 | -0.0887 | 0.0952 | -0.2817 | -0.15093 | charge/import
270 | 0.6028 | -0.1269 | 0.2425 | -0.3199 | 0.1269 | charge/import
300 | 0.6616 | -0.1185 | 0.3013 | -0.3115 | 0.43342 | charge/import
330 | 0.6643 | -0.1165 | 0.304 | -0.3095 | 0.63355 | charge/import
(close) | 0.67 | 0.5068 | 0.3097 | 0.3138
Interpretation (all computed live):
P width (MW) |  | 0.3831
import-reach (charge) |  | 0.3097
export-reach (dischg) |  | 0.0734
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P39_19h00
TR9 rolling FOR — period 39 = 19:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 0.6091 | B_Q (MVAr) = | 0.195
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 1.0837 | 0.5184 | 0.4746 | 0.3234 | 1.0837 | charge/import
30 | 1.0802 | 0.5341 | 0.4711 | 0.3391 | 1.2025 | charge/import
60 | 1.0701 | 0.5418 | 0.461 | 0.3468 | 1.0043 | charge/import
90 | 1.0194 | 0.5503 | 0.4103 | 0.3553 | 0.5503 | charge/import
120 | 0.8503 | 0.5048 | 0.2412 | 0.3098 | 0.01202 | charge/import
150 | 0.7266 | 0.3814 | 0.1175 | 0.1864 | -0.43855 | charge/import
180 | 0.6837 | 0.23 | 0.0746 | 0.035 | -0.6837 | charge/import
210 | 0.73 | 0.0639 | 0.1209 | -0.1311 | -0.66415 | charge/import
240 | 0.8427 | -0.05 | 0.2336 | -0.245 | -0.37805 | charge/import
270 | 0.9999 | -0.0909 | 0.3908 | -0.2859 | 0.0909 | charge/import
300 | 1.0698 | -0.0801 | 0.4607 | -0.2751 | 0.60427 | charge/import
330 | 1.0746 | -0.0764 | 0.4655 | -0.2714 | 0.96883 | charge/import
(close) | 1.0837 | 0.5184 | 0.4746 | 0.3234
Interpretation (all computed live):
P width (MW) |  | 0.4
import-reach (charge) |  | 0.4746
export-reach (dischg) |  | 0
verdict |  | one-sided → charge/import only (no export headroom)
what stops it |  | blocked at 180°: Vmax there = 1.10000 pu → over-voltage limit is active
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P40_19h30
TR9 rolling FOR — period 40 = 19:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 1.0097 | B_Q (MVAr) = | 0.2297
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 1.2639 | 0.5004 | 0.2542 | 0.2707 | 1.2639 | charge/import
30 | 1.2549 | 0.5323 | 0.2452 | 0.3026 | 1.3529 | charge/import
60 | 1.2371 | 0.5468 | 0.2274 | 0.3171 | 1.0921 | charge/import
90 | 1.1606 | 0.564 | 0.1509 | 0.3343 | 0.564 | charge/import
120 | 0.9969 | 0.5185 | -0.0128 | 0.2888 | -0.049416 | discharge/export
150 | 0.8725 | 0.3945 | -0.1372 | 0.1648 | -0.55836 | discharge/export
180 | 0.8294 | 0.2396 | -0.1803 | 0.0099 | -0.8294 | discharge/export
210 | 0.8731 | 0.0791 | -0.1366 | -0.1506 | -0.79568 | discharge/export
240 | 0.9858 | -0.0342 | -0.0239 | -0.2639 | -0.46328 | discharge/export
270 | 1.1454 | -0.076 | 0.1357 | -0.3057 | 0.076 | charge/import
300 | 1.2436 | -0.0575 | 0.2339 | -0.2872 | 0.6716 | charge/import
330 | 1.2543 | -0.0485 | 0.2446 | -0.2782 | 1.1105 | charge/import
(close) | 1.2639 | 0.5004 | 0.2542 | 0.2707
Interpretation (all computed live):
P width (MW) |  | 0.4345
import-reach (charge) |  | 0.2542
export-reach (dischg) |  | 0.1803
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P41_20h00
TR9 rolling FOR — period 41 = 20:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 1.1563 | B_Q (MVAr) = | 0.2442
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 1.3748 | 0.4771 | 0.2185 | 0.2329 | 1.3748 | charge/import
30 | 1.3601 | 0.5232 | 0.2038 | 0.279 | 1.4395 | charge/import
60 | 1.3297 | 0.552 | 0.1734 | 0.3078 | 1.1429 | charge/import
90 | 1.2333 | 0.5762 | 0.077 | 0.332 | 0.5762 | charge/import
120 | 1.0729 | 0.5314 | -0.0834 | 0.2872 | -0.076244 | discharge/export
150 | 0.9498 | 0.4087 | -0.2065 | 0.1645 | -0.6182 | discharge/export
180 | 0.9081 | 0.2568 | -0.2482 | 0.0126 | -0.9081 | discharge/export
210 | 0.9508 | 0.0894 | -0.2055 | -0.1548 | -0.86812 | discharge/export
240 | 1.0619 | -0.0219 | -0.0944 | -0.2661 | -0.51198 | discharge/export
270 | 1.2202 | -0.0633 | 0.0639 | -0.3075 | 0.0633 | charge/import
300 | 1.3419 | -0.037 | 0.1856 | -0.2812 | 0.70299 | charge/import
330 | 1.3645 | -0.0169 | 0.2082 | -0.2611 | 1.1901 | charge/import
(close) | 1.3748 | 0.4771 | 0.2185 | 0.2329
Interpretation (all computed live):
P width (MW) |  | 0.4667
import-reach (charge) |  | 0.2185
export-reach (dischg) |  | 0.2482
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P42_20h30
TR9 rolling FOR — period 42 = 20:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 1.2314 | B_Q (MVAr) = | 0.2568
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 1.4133 | 0.4157 | 0.1819 | 0.1589 | 1.4133 | charge/import
30 | 1.3938 | 0.5009 | 0.1624 | 0.2441 | 1.4575 | charge/import
60 | 1.3453 | 0.5473 | 0.1139 | 0.2905 | 1.1466 | charge/import
90 | 1.2363 | 0.5769 | 0.0049 | 0.3201 | 0.5769 | charge/import
120 | 1.0794 | 0.5323 | -0.152 | 0.2755 | -0.078715 | discharge/export
150 | 0.957 | 0.4107 | -0.2744 | 0.1539 | -0.62344 | discharge/export
180 | 0.9156 | 0.2432 | -0.3158 | -0.0136 | -0.9156 | discharge/export
210 | 0.9567 | 0.0893 | -0.2747 | -0.1675 | -0.87318 | discharge/export
240 | 1.0664 | -0.0203 | -0.165 | -0.2771 | -0.51562 | discharge/export
270 | 1.2251 | -0.0619 | -0.0063 | -0.3187 | 0.0619 | discharge/export
300 | 1.3649 | -0.0288 | 0.1335 | -0.2856 | 0.70739 | charge/import
330 | 1.402 | 0.0047 | 0.1706 | -0.2521 | 1.2118 | charge/import
(close) | 1.4133 | 0.4157 | 0.1819 | 0.1589
Interpretation (all computed live):
P width (MW) |  | 0.4977
import-reach (charge) |  | 0.1819
export-reach (dischg) |  | 0.3158
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P43_21h00
TR9 rolling FOR — period 43 = 21:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 1.2369 | B_Q (MVAr) = | 0.258
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 1.4057 | 0.3497 | 0.1688 | 0.0917 | 1.4057 | charge/import
30 | 1.3832 | 0.4702 | 0.1463 | 0.2122 | 1.433 | charge/import
60 | 1.3164 | 0.5356 | 0.0795 | 0.2776 | 1.122 | charge/import
90 | 1.1982 | 0.5685 | -0.0387 | 0.3105 | 0.5685 | discharge/export
120 | 1.038 | 0.524 | -0.1989 | 0.266 | -0.065203 | discharge/export
150 | 0.9199 | 0.4071 | -0.317 | 0.1491 | -0.59311 | discharge/export
180 | 0.8808 | 0.239 | -0.3561 | -0.019 | -0.8808 | discharge/export
210 | 0.9216 | 0.0757 | -0.3153 | -0.1823 | -0.83598 | discharge/export
240 | 1.0273 | -0.03 | -0.2096 | -0.288 | -0.48767 | discharge/export
270 | 1.1842 | -0.0711 | -0.0527 | -0.3291 | 0.0711 | discharge/export
300 | 1.3344 | -0.0338 | 0.0975 | -0.2918 | 0.69647 | charge/import
330 | 1.3914 | 0.0182 | 0.1545 | -0.2398 | 1.1959 | charge/import
(close) | 1.4057 | 0.3497 | 0.1688 | 0.0917
Interpretation (all computed live):
P width (MW) |  | 0.5249
import-reach (charge) |  | 0.1688
export-reach (dischg) |  | 0.3561
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P44_21h30
TR9 rolling FOR — period 44 = 21:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 1.1953 | B_Q (MVAr) = | 0.2491
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 1.3925 | 0.3036 | 0.1972 | 0.0545 | 1.3925 | charge/import
30 | 1.3693 | 0.4305 | 0.174 | 0.1814 | 1.4011 | charge/import
60 | 1.2753 | 0.5257 | 0.08 | 0.2766 | 1.0929 | charge/import
90 | 1.154 | 0.5592 | -0.0413 | 0.3101 | 0.5592 | discharge/export
120 | 0.9964 | 0.5154 | -0.1989 | 0.2663 | -0.051851 | discharge/export
150 | 0.8849 | 0.405 | -0.3104 | 0.1559 | -0.56385 | discharge/export
180 | 0.849 | 0.2002 | -0.3463 | -0.0489 | -0.849 | discharge/export
210 | 0.8868 | 0.0595 | -0.3085 | -0.1896 | -0.79774 | discharge/export
240 | 0.9862 | -0.04 | -0.2091 | -0.2891 | -0.45846 | discharge/export
270 | 1.1413 | -0.0803 | -0.054 | -0.3294 | 0.0803 | discharge/export
300 | 1.2985 | -0.0402 | 0.1032 | -0.2893 | 0.68406 | charge/import
330 | 1.3735 | 0.0307 | 0.1782 | -0.2184 | 1.1741 | charge/import
(close) | 1.3925 | 0.3036 | 0.1972 | 0.0545
Interpretation (all computed live):
P width (MW) |  | 0.5435
import-reach (charge) |  | 0.1972
export-reach (dischg) |  | 0.3463
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P45_22h00
TR9 rolling FOR — period 45 = 22:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 1.1524 | B_Q (MVAr) = | 0.2399
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 1.2932 | 0.2497 | 0.1408 | 0.0098 | 1.2932 | charge/import
30 | 1.2626 | 0.4 | 0.1102 | 0.1601 | 1.2934 | charge/import
60 | 1.162 | 0.5001 | 0.0096 | 0.2602 | 1.0141 | charge/import
90 | 1.0381 | 0.5346 | -0.1143 | 0.2947 | 0.5346 | discharge/export
120 | 0.885 | 0.4929 | -0.2674 | 0.253 | -0.015636 | discharge/export
150 | 0.7823 | 0.3925 | -0.3701 | 0.1526 | -0.48124 | discharge/export
180 | 0.7501 | 0.1396 | -0.4023 | -0.1003 | -0.7501 | discharge/export
210 | 0.7834 | 0.0236 | -0.369 | -0.2163 | -0.69024 | discharge/export
240 | 0.8757 | -0.0681 | -0.2767 | -0.308 | -0.37887 | discharge/export
270 | 1.0227 | -0.106 | -0.1297 | -0.3459 | 0.106 | discharge/export
300 | 1.1838 | -0.0642 | 0.0314 | -0.3041 | 0.6475 | charge/import
330 | 1.2716 | 0.0203 | 0.1192 | -0.2196 | 1.0911 | charge/import
(close) | 1.2932 | 0.2497 | 0.1408 | 0.0098
Interpretation (all computed live):
P width (MW) |  | 0.5431
import-reach (charge) |  | 0.1408
export-reach (dischg) |  | 0.4023
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P46_22h30
TR9 rolling FOR — period 46 = 22:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 1.0326 | B_Q (MVAr) = | 0.2143
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 1.1258 | 0.2028 | 0.0932 | -0.0115 | 1.1258 | charge/import
30 | 1.0941 | 0.3566 | 0.0615 | 0.1423 | 1.1258 | charge/import
60 | 0.9878 | 0.4625 | -0.0448 | 0.2482 | 0.89444 | discharge/export
90 | 0.8575 | 0.4969 | -0.1751 | 0.2826 | 0.4969 | discharge/export
120 | 0.7075 | 0.4575 | -0.3251 | 0.2432 | 0.042457 | discharge/export
150 | 0.6169 | 0.369 | -0.4157 | 0.1547 | -0.34975 | discharge/export
180 | 0.5881 | 0.1046 | -0.4445 | -0.1097 | -0.5881 | discharge/export
210 | 0.6201 | -0.0272 | -0.4125 | -0.2415 | -0.52342 | discharge/export
240 | 0.7037 | -0.1099 | -0.3289 | -0.3242 | -0.25667 | discharge/export
270 | 0.8423 | -0.1452 | -0.1903 | -0.3595 | 0.1452 | discharge/export
300 | 1.0042 | -0.1027 | -0.0284 | -0.317 | 0.59104 | discharge/export
330 | 1.0996 | -0.0095 | 0.067 | -0.2238 | 0.95703 | charge/import
(close) | 1.1258 | 0.2028 | 0.0932 | -0.0115
Interpretation (all computed live):
P width (MW) |  | 0.5377
import-reach (charge) |  | 0.0932
export-reach (dischg) |  | 0.4445
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P47_23h00
TR9 rolling FOR — period 47 = 23:00
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 0.85 | B_Q (MVAr) = | 0.1759
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 0.9354 | 0.137 | 0.0854 | -0.0389 | 0.9354 | charge/import
30 | 0.9002 | 0.3167 | 0.0502 | 0.1408 | 0.93795 | charge/import
60 | 0.7953 | 0.4198 | -0.0547 | 0.2439 | 0.76121 | discharge/export
90 | 0.6551 | 0.4551 | -0.1949 | 0.2792 | 0.4551 | discharge/export
120 | 0.5126 | 0.4181 | -0.3374 | 0.2422 | 0.10579 | discharge/export
150 | 0.428 | 0.3349 | -0.422 | 0.159 | -0.20321 | discharge/export
180 | 0.402 | 0.0745 | -0.448 | -0.1014 | -0.402 | discharge/export
210 | 0.4304 | -0.0745 | -0.4196 | -0.2504 | -0.33549 | discharge/export
240 | 0.513 | -0.1554 | -0.337 | -0.3313 | -0.12192 | discharge/export
270 | 0.6426 | -0.1878 | -0.2074 | -0.3637 | 0.1878 | discharge/export
300 | 0.8051 | -0.1449 | -0.0449 | -0.3208 | 0.52804 | discharge/export
330 | 0.9062 | -0.0451 | 0.0562 | -0.221 | 0.80734 | charge/import
(close) | 0.9354 | 0.137 | 0.0854 | -0.0389
Interpretation (all computed live):
P width (MW) |  | 0.5334
import-reach (charge) |  | 0.0854
export-reach (dischg) |  | 0.448
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.

## P48_23h30
TR9 rolling FOR — period 48 = 23:30
BASELINE B ≈ load − PV, batteries OFF — the all-idle PCC point (also carries losses). This is the UNCONTROLLABLE PV commitment; the battery deviates around it:
B_P (MW) = | 0.6488 | B_Q (MVAr) = | 0.1337
angle_deg | P_abs (MW) | Q_abs (MVAr) | dP = P − B_P | dQ = Q − B_Q | proj check | battery side
0 | 0.839 | 0.1445 | 0.1902 | 0.0108 | 0.839 | charge/import
30 | 0.8035 | 0.292 | 0.1547 | 0.1583 | 0.84185 | charge/import
60 | 0.6978 | 0.3966 | 0.049 | 0.2629 | 0.69237 | charge/import
90 | 0.5504 | 0.4339 | -0.0984 | 0.3002 | 0.4339 | discharge/export
120 | 0.415 | 0.3989 | -0.2338 | 0.2652 | 0.13796 | discharge/export
150 | 0.3359 | 0.322 | -0.3129 | 0.1883 | -0.1299 | discharge/export
180 | 0.3145 | 0.0186 | -0.3343 | -0.1151 | -0.3145 | discharge/export
210 | 0.3421 | -0.104 | -0.3067 | -0.2377 | -0.24427 | discharge/export
240 | 0.4205 | -0.1798 | -0.2283 | -0.3135 | -0.054539 | discharge/export
270 | 0.5405 | -0.2099 | -0.1083 | -0.3436 | 0.2099 | discharge/export
300 | 0.7035 | -0.1666 | 0.0547 | -0.3003 | 0.49603 | charge/import
330 | 0.8068 | -0.0642 | 0.158 | -0.1979 | 0.73081 | charge/import
(close) | 0.839 | 0.1445 | 0.1902 | 0.0108
Interpretation (all computed live):
P width (MW) |  | 0.5245
import-reach (charge) |  | 0.1902
export-reach (dischg) |  | 0.3343
verdict |  | two-sided → can charge (import) or discharge (export)
what stops it |  | both directions have headroom
Tip: change any light-blue P/Q or the pink baseline and the amber cells + both charts update automatically.