## 1. Overview
TR3 — Where does the PV energy go?
Prosumers vs. pure customers — every kWh traced from the raw model inputs
Purpose
This workbook accounts for every kWh of PV generated on transformer TR3 over one representative day, and it is fully auditable: nothing is hand-typed except the raw model outputs. Follow the data chain below — each step is a live formula, so changing any raw number updates everything.
The data chain (how each number is built)
Sheet 3 · Raw PV per load | The PV profile of every connection, 48 half-hours. Copied verbatim from TR3_load_PV_48periods.xlsx (sheet PV_generation_kW). Customers = 0.
Sheet 4 · Raw load per load | The load profile of every connection, 48 half-hours, tagged prosumer / customer. Copied from TR3_load_PV_48periods.xlsx (sheet Load_P_kW).
Sheet 5 · Raw batt charge | Charging power of every battery, 48 half-hours. Copied from the rolling dispatch TR3_analysis_data.xlsx (sheet Charge_kW).
Sheet 6 · Raw batt discharge | Discharging power of every battery. Copied from the same run (Discharge_kW).
Sheet 7 · PV allocation | Per half-hour: the five blue inputs are AGGREGATED from sheets 3–6 by SUM / SUMIF; the amber columns then split the PV by the priority rule.
Sheets 1 & 8 · Results | Daily totals (Σ×0.5 h) and shares. Every headline cell links to sheet 7.
The aggregation formulas (sheet 7, per half-hour)
PV (all)
prosumer load
customer load
battery charge
battery discharge
Headline results (all linked live to sheet 7)
Quantity | Value | Unit
Prosumers (PV + battery) | 49 | connections
Pure customers (load only) | 21 | connections
PV generated | 1316.4443 | kWh/day
PV → prosumers' own load (direct) | 223.6645 | kWh/day
PV → battery storage | 162.998 | kWh/day
PV → customers | 84.8832 | kWh/day
PV → export to grid | 844.8986 | kWh/day
PV share reaching customers | 6.448% | % of PV
Customer load covered by PV | 51.69% | % of customer load
Customer load covered by grid | 48.31% | % of customer load
Colour key & provenance
• LIGHT-BLUE cell = data belonging to a prosumer (its rooftop PV, load, or battery). WHITE = a pure customer (load only). On sheet 7: VIOLET = value aggregated live from the raw sheets (SUM/SUMIF); AMBER = allocation formula; GREEN = daily total (Σ × 0.5 h).
• Per-load PV & load profiles: results/tables/TR3_load_PV_48periods.xlsx (built from OpData.xls).
• Per-battery charge/discharge: TR3_analysis/01_DAILY_ROLLING_DISPATCH/TR3_analysis_data.xlsx (exact-QCP rolling dispatch, RunFOR_Rolling, CPLEX).
• Load classification (PV size > 0 = prosumer): sheet 'Customers' of the load/PV workbook.
• Method note: priority energy allocation per half-hour; downstream network + battery round-trip losses (~3–4% of PV) are not separated out in the per-period disposition.

## 2. Load classification
TR3 load classification — 70 connections
49 prosumers (PV + battery) · 21 pure customers (load only)
ID | Load name | Bus | Phase | PV size (kW) | Type
310 | Load_TR3_F1_1 | TR3_one38 | 2 | 0 | customer
312 | Load_TR3_F1_11 | TR3_one223 | 2 | 0 | customer
317 | Load_TR3_F1_16 | TR3_one280 | 1 | 0 | customer
318 | Load_TR3_F1_17 | TR3_one287 | 2 | 0 | customer
323 | Load_TR3_F1_21 | TR3_one321 | 3 | 0 | customer
324 | Load_TR3_F1_22 | TR3_one328 | 1 | 0 | customer
325 | Load_TR3_F1_23 | TR3_one345 | 1 | 0 | customer
333 | Load_TR3_F1_30 | TR3_one416 | 3 | 0 | customer
342 | Load_TR3_F1_39 | TR3_one537 | 1 | 0 | customer
347 | Load_TR3_F1_43 | TR3_one560 | 3 | 0 | customer
349 | Load_TR3_F1_45 | TR3_one585 | 1 | 0 | customer
350 | Load_TR3_F1_46 | TR3_one590 | 1 | 0 | customer
356 | Load_TR3_F1_7 | TR3_one133 | 1 | 0 | customer
362 | Load_TR3_F2_12 | TR3_two275 | 3 | 0 | customer
363 | Load_TR3_F2_13 | TR3_two283 | 2 | 0 | customer
365 | Load_TR3_F2_15 | TR3_two306 | 1 | 0 | customer
367 | Load_TR3_F2_17 | TR3_two312 | 3 | 0 | customer
369 | Load_TR3_F2_19 | TR3_two315 | 1 | 0 | customer
374 | Load_TR3_F2_4 | TR3_two217 | 1 | 0 | customer
377 | Load_TR3_F2_7 | TR3_two233 | 1 | 0 | customer
378 | Load_TR3_F2_8 | TR3_two238 | 3 | 0 | customer
311 | Load_TR3_F1_10 | TR3_one195 | 3 | 4 | prosumer
313 | Load_TR3_F1_12 | TR3_one235 | 1 | 4 | prosumer
314 | Load_TR3_F1_13 | TR3_one242 | 2 | 4 | prosumer
315 | Load_TR3_F1_14 | TR3_one252 | 3 | 3 | prosumer
316 | Load_TR3_F1_15 | TR3_one260 | 3 | 4 | prosumer
319 | Load_TR3_F1_18 | TR3_one299 | 2 | 4 | prosumer
320 | Load_TR3_F1_19 | TR3_one313 | 1 | 3 | prosumer
321 | Load_TR3_F1_2 | TR3_one42 | 2 | 3.5 | prosumer
322 | Load_TR3_F1_20 | TR3_one320 | 2 | 4 | prosumer
326 | Load_TR3_F1_24 | TR3_one346 | 3 | 4 | prosumer
327 | Load_TR3_F1_25 | TR3_one363 | 3 | 2 | prosumer
328 | Load_TR3_F1_26 | TR3_one366 | 2 | 2 | prosumer
329 | Load_TR3_F1_27 | TR3_one371 | 3 | 4 | prosumer
330 | Load_TR3_F1_28 | TR3_one375 | 3 | 4 | prosumer
331 | Load_TR3_F1_29 | TR3_one410 | 2 | 2 | prosumer
332 | Load_TR3_F1_3 | TR3_one50 | 1 | 2.5 | prosumer
334 | Load_TR3_F1_31 | TR3_one423 | 2 | 3.5 | prosumer
335 | Load_TR3_F1_32 | TR3_one446 | 2 | 4 | prosumer
336 | Load_TR3_F1_33 | TR3_one469 | 1 | 3.5 | prosumer
337 | Load_TR3_F1_34 | TR3_one477 | 1 | 1.5 | prosumer
338 | Load_TR3_F1_35 | TR3_one480 | 1 | 4 | prosumer
339 | Load_TR3_F1_36 | TR3_one482 | 2 | 4 | prosumer
340 | Load_TR3_F1_37 | TR3_one521 | 3 | 4 | prosumer
341 | Load_TR3_F1_38 | TR3_one528 | 3 | 4 | prosumer
343 | Load_TR3_F1_4 | TR3_one61 | 1 | 2.5 | prosumer
344 | Load_TR3_F1_40 | TR3_one544 | 1 | 4 | prosumer
345 | Load_TR3_F1_41 | TR3_one552 | 2 | 3.5 | prosumer
346 | Load_TR3_F1_42 | TR3_one559 | 3 | 4 | prosumer
348 | Load_TR3_F1_44 | TR3_one570 | 2 | 3 | prosumer
351 | Load_TR3_F1_47 | TR3_one605 | 1 | 4 | prosumer
352 | Load_TR3_F1_48 | TR3_one614 | 2 | 3 | prosumer
353 | Load_TR3_F1_49 | TR3_one617 | 1 | 4 | prosumer
354 | Load_TR3_F1_5 | TR3_one73 | 1 | 3.5 | prosumer
355 | Load_TR3_F1_6 | TR3_one76 | 1 | 2.5 | prosumer
357 | Load_TR3_F1_8 | TR3_one137 | 1 | 4 | prosumer
358 | Load_TR3_F1_9 | TR3_one176 | 1 | 2 | prosumer
359 | Load_TR3_F2_1 | TR3_two130 | 3 | 4 | prosumer
360 | Load_TR3_F2_10 | TR3_two249 | 1 | 4 | prosumer
361 | Load_TR3_F2_11 | TR3_two267 | 3 | 4 | prosumer
364 | Load_TR3_F2_14 | TR3_two292 | 2 | 4 | prosumer
366 | Load_TR3_F2_16 | TR3_two308 | 1 | 3 | prosumer
368 | Load_TR3_F2_18 | TR3_two313 | 3 | 2.5 | prosumer
370 | Load_TR3_F2_2 | TR3_two137 | 2 | 3.5 | prosumer
371 | Load_TR3_F2_20 | TR3_two316 | 1 | 3 | prosumer
372 | Load_TR3_F2_21 | TR3_two339 | 1 | 3.5 | prosumer
373 | Load_TR3_F2_3 | TR3_two149 | 2 | 3.5 | prosumer
375 | Load_TR3_F2_5 | TR3_two225 | 3 | 2 | prosumer
376 | Load_TR3_F2_6 | TR3_two229 | 1 | 1.5 | prosumer
379 | Load_TR3_F2_9 | TR3_two242 | 2 | 2 | prosumer

## 3. Raw PV per load
Raw PV per load
Verbatim copy of PV_generation_kW (TR3_load_PV_48periods.xlsx). One row per connection, 48 half-hours (kW).
Load name | Type | p1 | p2 | p3 | p4 | p5 | p6 | p7 | p8 | p9 | p10 | p11 | p12 | p13 | p14 | p15 | p16 | p17 | p18 | p19 | p20 | p21 | p22 | p23 | p24 | p25 | p26 | p27 | p28 | p29 | p30 | p31 | p32 | p33 | p34 | p35 | p36 | p37 | p38 | p39 | p40 | p41 | p42 | p43 | p44 | p45 | p46 | p47 | p48
Load_TR3_F1_1 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_10 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_11 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_12 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_13 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_14 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_15 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_16 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_17 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_18 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_19 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_2 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_20 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_21 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_22 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_23 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_24 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_25 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_26 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_27 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_28 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_29 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_3 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_30 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_31 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_32 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_33 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_34 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_35 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_36 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_37 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_38 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_39 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_4 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_40 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_41 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_42 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_43 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_44 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_45 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_46 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_47 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_48 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_49 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_5 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_6 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_7 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_8 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F1_9 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_1 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_10 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_11 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_12 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_13 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_14 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_15 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_16 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_17 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_18 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_19 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_2 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_20 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_21 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_3 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_4 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_5 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_6 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_7 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_8 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR3_F2_9 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 4. Raw load per load
Raw load per load
Verbatim copy of Load_P_kW (TR3_load_PV_48periods.xlsx), tagged by type. One row per connection, 48 half-hours (kW).
Load name | Type | p1 | p2 | p3 | p4 | p5 | p6 | p7 | p8 | p9 | p10 | p11 | p12 | p13 | p14 | p15 | p16 | p17 | p18 | p19 | p20 | p21 | p22 | p23 | p24 | p25 | p26 | p27 | p28 | p29 | p30 | p31 | p32 | p33 | p34 | p35 | p36 | p37 | p38 | p39 | p40 | p41 | p42 | p43 | p44 | p45 | p46 | p47 | p48
Load_TR3_F1_1 | customer | 0.9617 | 0.5561 | 0.8354 | 0.7362 | 0.1576 | 0.137 | 0.2422 | 0.2307 | 0.0639 | 0.2913 | 0.1906 | 0.4184 | 0.6373 | 0.3183 | 0.4199 | 0.1819 | 0.2082 | 0.4571 | 1.5202 | 0.2489 | 0.1637 | 0.2213 | 0.3085 | 0.3175 | 0.1993 | 0.4181 | 0.1968 | 0.5473 | 0.7599 | 0.4932 | 0.2217 | 0.7588 | 0.1884 | 0.2482 | 0.3904 | 0.5471 | 1.3444 | 0.7669 | 1.3423 | 0.2905 | 0.3876 | 0.766 | 0.264 | 0.8794 | 1.2691 | 0.4119 | 0.6214 | 0.1681
Load_TR3_F1_10 | prosumer | 0.1897 | 0.2611 | 0.0791 | 0.2595 | 0.1702 | 0.1543 | 0.2043 | 0.1818 | 0.1425 | 0.1147 | 0.2849 | 0.1092 | 0.2156 | 0.1754 | 0.1177 | 0.2523 | 3.5086 | 1.2015 | 0.9525 | 0.316 | 1.4874 | 1.4209 | 1.0839 | 0.4138 | 0.2612 | 0.0993 | 0.4685 | 0.1098 | 0.2649 | 0.1957 | 0.4001 | 0.2838 | 0.1625 | 0.2981 | 0.2266 | 0.3572 | 0.2695 | 0.4171 | 0.3557 | 0.6853 | 0.7839 | 0.6368 | 0.969 | 0.695 | 1.1144 | 0.9802 | 0.1801 | 0.9379
Load_TR3_F1_11 | customer | 0.1034 | 0.089 | 0.2085 | 0.2412 | 0.2768 | 0.046 | 0.1751 | 0.0747 | 0.1177 | 0.1321 | 0.046 | 0.2038 | 0.046 | 0.1894 | 0.0603 | 0.046 | 0.0494 | 0.0692 | 0.1751 | 0.0747 | 0.046 | 0.0747 | 0.1751 | 0.046 | 0.3215 | 0.1177 | 0.046 | 0.2106 | 0.0601 | 0.1308 | 0.4847 | 0.245 | 0.1679 | 0.0921 | 2.1325 | 2.5812 | 1.7829 | 0.052 | 0.1044 | 0.6324 | 0.0603 | 0.0532 | 0.6161 | 0.4601 | 0.6164 | 0.7547 | 0.5523 | 1.4402
Load_TR3_F1_12 | prosumer | 0.046 | 0.1072 | 0.1908 | 0.0725 | 0.1989 | 0.046 | 0.2431 | 0.0814 | 0.0858 | 0.2387 | 0.0681 | 0.2563 | 0.046 | 0.1123 | 0.2121 | 0.046 | 0.196 | 0.1534 | 0.0898 | 0.991 | 0.5618 | 0.3996 | 0.1351 | 0.258 | 0.1792 | 0.103 | 0.5726 | 0.0536 | 0.1454 | 0.0995 | 0.046 | 0.1256 | 0.0813 | 1.1341 | 3.1862 | 2.1118 | 0.1759 | 0.1365 | 0.1237 | 0.2102 | 0.2442 | 0.4009 | 0.5292 | 0.3365 | 0.3203 | 0.6663 | 0.046 | 0.1759
Load_TR3_F1_13 | prosumer | 0.046 | 0.3098 | 0.0573 | 0.1178 | 0.1614 | 0.0629 | 0.236 | 0.1311 | 0.48 | 0.2878 | 0.2131 | 0.2759 | 0.1452 | 0.046 | 0.2084 | 0.046 | 0.1808 | 0.1863 | 0.8571 | 0.7638 | 0.2577 | 0.2316 | 0.1854 | 0.0869 | 0.1549 | 0.1914 | 0.2097 | 0.1813 | 0.1463 | 0.1136 | 0.046 | 0.2935 | 0.1551 | 0.0742 | 0.2312 | 0.1077 | 0.1587 | 0.1454 | 0.32 | 0.3603 | 0.442 | 0.5171 | 0.5757 | 0.3551 | 0.276 | 0.0742 | 0.1632 | 0.1757
Load_TR3_F1_14 | prosumer | 0.3805 | 0.1247 | 0.048 | 0.166 | 0.048 | 0.166 | 0.048 | 0.0716 | 0.1424 | 0.048 | 0.166 | 0.048 | 0.166 | 0.048 | 1.5799 | 0.0716 | 0.1365 | 0.6076 | 0.644 | 1.8739 | 0.056 | 0.0765 | 0.2355 | 0.1938 | 0.1938 | 0.1423 | 1.3364 | 0.8488 | 0.2237 | 0.1355 | 0.1634 | 0.3957 | 0.0821 | 0.1011 | 0.1129 | 0.2935 | 2.6605 | 2.272 | 0.1542 | 0.0598 | 0.048 | 0.2334 | 0.1269 | 0.4062 | 0.3871 | 0.4897 | 0.2498 | 0.048
Load_TR3_F1_15 | prosumer | 0.048 | 0.2095 | 0.048 | 0.048 | 0.0718 | 0.1434 | 0.048 | 0.048 | 0.048 | 0.1672 | 0.048 | 0.1136 | 0.1016 | 0.048 | 0.0957 | 0.1195 | 0.048 | 0.1672 | 0.096 | 0.1672 | 0.0929 | 0.0581 | 0.171 | 0.9263 | 0.048 | 0.3516 | 0.148 | 0.2672 | 0.0612 | 0.1023 | 0.3294 | 0.2348 | 0.3727 | 0.2383 | 0.0931 | 0.3196 | 0.3716 | 0.4502 | 0.5657 | 0.2976 | 0.1987 | 0.942 | 1.1321 | 0.4801 | 0.4652 | 0.3495 | 0.048 | 0.1672
Load_TR3_F1_16 | customer | 0.052 | 0.052 | 0.052 | 0.052 | 0.0717 | 0.1769 | 0.052 | 0.1769 | 0.0717 | 0.052 | 0.1901 | 0.0586 | 0.0849 | 0.1638 | 0.052 | 0.052 | 0.0798 | 0.1887 | 0.0876 | 0.2011 | 0.9673 | 0.2479 | 0.1966 | 0.052 | 0.1835 | 0.0651 | 0.0651 | 0.1835 | 0.052 | 0.1966 | 0.052 | 0.1572 | 0.0914 | 0.1177 | 0.1309 | 0.0564 | 0.3696 | 1.1587 | 0.2483 | 0.3633 | 0.7898 | 0.4565 | 0.5198 | 0.5305 | 0.4802 | 0.4264 | 0.1608 | 0.1875
Load_TR3_F1_17 | customer | 0.6712 | 0.4177 | 0.05 | 0.05 | 0.1163 | 0.0583 | 0.108 | 0.0666 | 0.0997 | 0.0749 | 0.05 | 0.05 | 0.05 | 0.0956 | 0.079 | 0.05 | 2.8977 | 0.121 | 0.3161 | 0.2878 | 0.3551 | 0.2553 | 0.0989 | 0.1729 | 0.6402 | 2.6501 | 3.4538 | 0.1012 | 0.0523 | 0.1741 | 0.1074 | 0.05 | 0.29 | 0.1555 | 0.3803 | 0.6844 | 0.836 | 0.7187 | 2.0877 | 0.7713 | 1.3992 | 0.593 | 0.6949 | 0.7518 | 0.5373 | 0.3644 | 0.5584 | 0.2376
Load_TR3_F1_18 | prosumer | 0.1036 | 0.1706 | 0.0976 | 0.0586 | 0.2602 | 0.053 | 0.1323 | 0.1865 | 0.053 | 0.174 | 0.1448 | 0.053 | 0.1223 | 0.587 | 1.4668 | 0.2019 | 1.5513 | 0.6897 | 0.3013 | 0.3667 | 0.2005 | 0.1182 | 0.3666 | 0.3576 | 0.1422 | 0.1766 | 0.053 | 0.1422 | 0.1766 | 0.1422 | 0.053 | 0.2658 | 0.053 | 0.1373 | 0.1716 | 0.2485 | 0.4158 | 0.3752 | 0.3559 | 0.4472 | 0.4233 | 0.5942 | 0.442 | 1.4198 | 1.6793 | 0.4103 | 0.2411 | 0.171
Load_TR3_F1_19 | prosumer | 0.3398 | 0.053 | 0.1617 | 0.2429 | 0.0866 | 0.0866 | 0.1951 | 0.1562 | 0.177 | 0.0908 | 0.2076 | 0.1643 | 0.1646 | 0.2153 | 0.5527 | 0.6306 | 0.4116 | 0.232 | 0.1718 | 0.1016 | 0.202 | 0.2074 | 0.1173 | 0.2429 | 0.1727 | 0.1962 | 0.3358 | 0.1472 | 0.458 | 1.2857 | 0.2749 | 0.4339 | 1.0597 | 0.8525 | 0.4597 | 0.5032 | 0.3017 | 0.1286 | 0.2313 | 0.5028 | 0.5858 | 0.7609 | 0.6387 | 0.7756 | 0.6367 | 0.6774 | 0.6668 | 0.1338
Load_TR3_F1_2 | prosumer | 0.033 | 0.033 | 0.033 | 0.0689 | 0.0689 | 0.033 | 0.033 | 0.033 | 0.0969 | 0.041 | 0.061 | 0.0769 | 0.0809 | 0.057 | 0.033 | 0.057 | 0.2721 | 0.1381 | 0.21 | 0.0728 | 0.1324 | 0.089 | 3.11 | 2.2321 | 0.6365 | 0.1025 | 0.1166 | 0.0567 | 0.1186 | 0.058 | 0.053 | 0.135 | 0.2414 | 0.069 | 0.0889 | 0.033 | 0.033 | 0.1097 | 0.0815 | 0.042 | 0.0621 | 0.1009 | 0.033 | 0.041 | 0.0969 | 0.033 | 0.1049 | 0.033
Load_TR3_F1_20 | prosumer | 0.046 | 0.1994 | 0.046 | 0.1576 | 0.0878 | 0.046 | 0.1994 | 0.046 | 0.1366 | 0.1088 | 0.046 | 0.046 | 0.1994 | 0.046 | 0.1392 | 0.3114 | 0.1786 | 1.5454 | 1.2938 | 0.6964 | 0.1645 | 0.0809 | 0.046 | 0.1994 | 0.1681 | 0.8241 | 0.4977 | 0.3759 | 0.0502 | 0.106 | 0.1571 | 0.0544 | 0.2113 | 0.165 | 0.1274 | 0.2055 | 0.0753 | 0.1924 | 0.0746 | 0.2884 | 0.1402 | 0.2244 | 0.3742 | 0.2583 | 0.3784 | 0.2107 | 1.2444 | 0.2241
Load_TR3_F1_21 | customer | 0.1577 | 0.1187 | 0.1892 | 0.1377 | 0.1302 | 0.05 | 0.2417 | 0.1196 | 0.1635 | 0.1977 | 0.05 | 0.05 | 0.1645 | 0.0633 | 0.1888 | 1.5059 | 0.3268 | 0.3363 | 0.2011 | 0.268 | 0.053 | 0.2851 | 0.1226 | 0.1292 | 0.9557 | 2.688 | 2.6528 | 0.3785 | 0.0887 | 0.2531 | 0.1081 | 0.1752 | 0.2222 | 0.7812 | 0.5604 | 0.4968 | 0.073 | 0.2243 | 0.1794 | 0.3821 | 0.4503 | 0.6376 | 1.169 | 0.9949 | 0.8171 | 0.8221 | 0.7545 | 0.7299
Load_TR3_F1_22 | customer | 0.1019 | 0.1584 | 0.0898 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.0739 | 0.0742 | 1.0916 | 1.9493 | 0.1718 | 0.1099 | 0.2555 | 0.2679 | 0.0623 | 0.0499 | 0.049 | 2.1216 | 0.5747 | 0.0567 | 0.0684 | 0.2778 | 0.1119 | 0.0671 | 0.2659 | 1.12 | 0.9137 | 0.1035 | 0.0582 | 0.0572 | 1.4034 | 1.0557 | 1.1871 | 0.8472 | 0.2592 | 0.2158 | 0.1981 | 0.4691 | 0.3156 | 0.233 | 0.049
Load_TR3_F1_23 | customer | 0.5914 | 0.5487 | 0.047 | 0.1283 | 0.047 | 0.0644 | 0.1109 | 0.047 | 0.1051 | 0.0702 | 0.047 | 0.144 | 0.047 | 0.0644 | 0.1109 | 0.047 | 0.1283 | 0.047 | 0.0612 | 0.3289 | 0.2523 | 0.0988 | 0.9447 | 0.115 | 1.4616 | 0.1225 | 0.047 | 0.076 | 0.2276 | 0.1126 | 0.1425 | 0.123 | 0.1414 | 0.1353 | 0.0919 | 0.3063 | 0.7747 | 0.461 | 0.2416 | 0.1753 | 0.047 | 0.1283 | 0.2942 | 0.8006 | 0.4576 | 0.4026 | 0.278 | 0.1283
Load_TR3_F1_24 | prosumer | 0.0976 | 0.0782 | 0.0937 | 0.051 | 0.051 | 0.051 | 0.1209 | 0.051 | 0.051 | 0.051 | 0.0937 | 0.0782 | 0.051 | 0.1209 | 0.051 | 0.0774 | 0.0994 | 0.0939 | 0.9849 | 0.0552 | 0.0667 | 0.3635 | 1.4397 | 0.2315 | 0.4509 | 1.862 | 0.961 | 0.4497 | 0.4021 | 0.5185 | 0.6261 | 0.3146 | 0.2796 | 0.3427 | 0.439 | 0.9075 | 0.5325 | 0.5705 | 0.1838 | 0.5676 | 0.4355 | 0.6852 | 0.702 | 0.6203 | 0.7449 | 0.4691 | 0.5668 | 0.1821
Load_TR3_F1_25 | prosumer | 0.054 | 0.1719 | 0.0786 | 0.0822 | 0.0892 | 0.054 | 0.054 | 0.1173 | 0.054 | 0.054 | 0.1173 | 0.054 | 0.0857 | 0.0857 | 0.054 | 0.1173 | 0.3058 | 0.3028 | 0.0669 | 0.3347 | 0.204 | 0.054 | 0.054 | 0.1138 | 0.0575 | 0.054 | 0.0997 | 0.0716 | 0.1033 | 0.0681 | 0.1173 | 0.1193 | 0.2397 | 2.8577 | 0.434 | 0.2038 | 0.2724 | 0.2786 | 0.4477 | 0.4133 | 0.4717 | 0.9095 | 1.2033 | 0.4327 | 0.4417 | 0.3476 | 0.0822 | 0.0892
Load_TR3_F1_26 | prosumer | 0.5994 | 0.5442 | 0.5475 | 0.6563 | 0.3339 | 0.096 | 0.045 | 0.1867 | 0.1313 | 0.1673 | 0.0643 | 0.0579 | 0.1738 | 0.0977 | 0.2202 | 0.0929 | 0.1606 | 0.1094 | 0.0828 | 0.3248 | 0.1287 | 0.045 | 0.0617 | 1.0719 | 0.2045 | 0.1611 | 0.1518 | 0.2799 | 0.0555 | 0.287 | 0.1089 | 0.1786 | 0.524 | 0.1265 | 0.1867 | 0.1393 | 0.1055 | 0.1713 | 0.1949 | 1.2712 | 0.3241 | 0.4527 | 0.5515 | 0.5493 | 0.3648 | 0.3606 | 0.1025 | 0.0738
Load_TR3_F1_27 | prosumer | 0.0719 | 0.042 | 0.042 | 0.2062 | 0.042 | 0.0868 | 0.1614 | 0.042 | 0.042 | 0.2062 | 0.042 | 0.0793 | 0.1689 | 0.042 | 0.042 | 0.1212 | 0.2172 | 0.0441 | 0.9284 | 0.2993 | 1.5256 | 2.1318 | 2.6132 | 0.7326 | 0.2395 | 0.5331 | 4.1265 | 2.5312 | 0.3727 | 0.3885 | 3.9087 | 2.8208 | 0.555 | 0.5504 | 1.3131 | 0.6176 | 0.101 | 0.2062 | 0.1007 | 0.3896 | 0.3672 | 0.3629 | 0.1615 | 0.4036 | 0.3691 | 0.3012 | 0.4581 | 0.1092
Load_TR3_F1_28 | prosumer | 0.1444 | 0.2298 | 0.1611 | 0.153 | 0.0963 | 0.3036 | 0.094 | 0.183 | 0.1906 | 0.2472 | 0.1842 | 0.1934 | 0.1515 | 0.2126 | 0.3054 | 0.2342 | 0.3648 | 0.0842 | 0.0958 | 0.2224 | 0.2155 | 0.1476 | 0.2902 | 0.0704 | 0.1315 | 0.253 | 0.1565 | 0.9093 | 0.4148 | 0.7124 | 0.1774 | 0.1669 | 0.63 | 0.1632 | 0.3355 | 0.5556 | 0.124 | 0.2595 | 0.2849 | 0.4331 | 0.5291 | 0.421 | 0.4536 | 0.419 | 0.4381 | 0.2754 | 0.2013 | 0.1494
Load_TR3_F1_29 | prosumer | 0.1651 | 0.047 | 0.2207 | 0.1215 | 0.0825 | 0.0913 | 0.1924 | 0.0833 | 0.2053 | 0.1235 | 0.1268 | 0.2198 | 0.1223 | 0.1006 | 0.2983 | 0.1835 | 0.8476 | 0.138 | 0.1268 | 0.047 | 0.5935 | 0.2266 | 0.2853 | 0.1769 | 0.1268 | 0.2154 | 0.0825 | 0.0913 | 0.2154 | 0.1268 | 0.047 | 0.047 | 0.273 | 0.0692 | 0.1896 | 0.1526 | 0.047 | 0.1268 | 0.1695 | 0.138 | 0.1096 | 0.3694 | 0.2127 | 0.3691 | 0.0592 | 0.1817 | 1.5382 | 1.4055
Load_TR3_F1_3 | prosumer | 0.1604 | 0.055 | 0.055 | 0.1118 | 0.1766 | 0.055 | 0.2334 | 0.055 | 0.6563 | 0.9147 | 0.4722 | 0.055 | 0.1847 | 0.2353 | 0.055 | 0.2334 | 0.055 | 0.1036 | 0.5109 | 1.4866 | 1.7703 | 2.1891 | 2.5585 | 1.9797 | 0.1361 | 0.055 | 0.055 | 0.168 | 0.8155 | 0.055 | 0.1199 | 1.6688 | 0.4948 | 0.7275 | 0.2765 | 0.2253 | 0.0717 | 0.4107 | 0.6492 | 0.8626 | 0.9268 | 2.4162 | 2.2719 | 1.1693 | 0.9561 | 1.0328 | 0.1604 | 0.128
Load_TR3_F1_30 | customer | 0.5998 | 0.2279 | 0.056 | 0.056 | 0.0794 | 0.2044 | 0.056 | 0.2201 | 0.0638 | 0.0794 | 0.2044 | 0.056 | 0.1263 | 0.1576 | 0.056 | 0.1956 | 0.2547 | 0.181 | 0.2263 | 0.2576 | 0.2134 | 0.4063 | 0.3751 | 0.3846 | 0.6016 | 0.5128 | 0.5043 | 0.2677 | 1.107 | 1.817 | 2.348 | 0.1705 | 0.1825 | 0.4845 | 0.056 | 0.1282 | 0.3764 | 0.1224 | 1.6757 | 1.4086 | 1.375 | 0.4526 | 0.2551 | 0.4675 | 0.2619 | 0.2431 | 0.0873 | 0.1966
Load_TR3_F1_31 | prosumer | 0.1314 | 0.055 | 0.0868 | 0.1633 | 0.055 | 0.055 | 0.1951 | 0.055 | 0.1187 | 0.1314 | 0.0677 | 0.1824 | 0.055 | 0.2395 | 1.9225 | 0.9754 | 1.3233 | 1.8482 | 1.2958 | 0.2631 | 0.2753 | 0.4026 | 0.1484 | 0.2069 | 0.5373 | 0.5677 | 0.5401 | 0.2986 | 0.4586 | 0.2953 | 0.3023 | 0.4501 | 0.2202 | 0.3556 | 1.3429 | 0.1535 | 0.2067 | 0.0968 | 0.2085 | 0.2217 | 0.3476 | 0.528 | 0.3666 | 0.3974 | 1.0337 | 0.3053 | 0.5058 | 0.171
Load_TR3_F1_32 | prosumer | 0.1485 | 0.1704 | 0.2205 | 0.1769 | 0.048 | 0.2205 | 0.1769 | 0.1342 | 0.2502 | 0.0609 | 0.2205 | 0.106 | 0.2443 | 0.095 | 0.1769 | 0.2205 | 0.4403 | 0.2516 | 0.2474 | 0.048 | 0.1769 | 0.2205 | 0.1769 | 0.095 | 0.1734 | 0.0544 | 0.241 | 0.1499 | 0.1382 | 0.2199 | 0.1709 | 0.1793 | 0.3705 | 0.141 | 0.4137 | 0.4205 | 0.4351 | 0.3988 | 0.5446 | 0.599 | 0.5831 | 0.8045 | 0.6223 | 0.8015 | 0.9001 | 0.7618 | 0.58 | 0.9914
Load_TR3_F1_33 | prosumer | 0.048 | 0.091 | 0.1628 | 0.1259 | 0.2058 | 0.1259 | 0.048 | 0.2664 | 0.0653 | 0.1546 | 0.1771 | 0.1259 | 0.2058 | 0.1259 | 0.1197 | 0.1684 | 0.1076 | 0.1098 | 0.2147 | 0.1671 | 0.2203 | 0.1114 | 0.0913 | 0.0826 | 0.2707 | 0.061 | 0.1259 | 0.2058 | 0.2365 | 0.3792 | 0.3302 | 0.0567 | 0.3386 | 0.2015 | 0.2571 | 0.1848 | 0.3652 | 0.2416 | 0.1521 | 0.546 | 0.3229 | 0.048 | 0.2837 | 0.048 | 0.0956 | 0.2361 | 0.048 | 0.2334
Load_TR3_F1_34 | prosumer | 0.1491 | 0.1391 | 0.083 | 0.034 | 0.1911 | 0.1461 | 0.034 | 0.1881 | 0.103 | 0.08 | 0.1881 | 0.1491 | 0.097 | 0.1251 | 0.2994 | 0.4737 | 0.2383 | 0.5974 | 0.041 | 0.0743 | 0.2068 | 0.09 | 0.0608 | 0.2764 | 0.034 | 0.1491 | 0.1706 | 0.5376 | 0.4566 | 0.3491 | 0.3623 | 0.359 | 0.4337 | 0.1878 | 0.882 | 1.9299 | 0.4614 | 0.2341 | 1.177 | 0.7608 | 0.6809 | 0.7768 | 0.9805 | 0.7012 | 0.7603 | 0.8927 | 0.9862 | 0.6767
Load_TR3_F1_35 | prosumer | 0.1499 | 0.05 | 0.05 | 0.1049 | 0.095 | 0.05 | 0.1349 | 0.065 | 0.05 | 0.05 | 0.055 | 0.1449 | 0.05 | 0.05 | 0.05 | 0.0616 | 0.0868 | 0.1096 | 0.1595 | 0.0636 | 0.1499 | 0.05 | 0.1499 | 0.05 | 0.095 | 0.1049 | 0.05 | 0.1991 | 0.125 | 0.2259 | 0.328 | 0.1593 | 0.2107 | 0.2746 | 0.1589 | 0.1365 | 0.1903 | 0.2749 | 0.2307 | 1.6831 | 0.2909 | 0.3066 | 0.2822 | 0.3704 | 0.3082 | 0.9488 | 0.8168 | 0.2389
Load_TR3_F1_36 | prosumer | 0.053 | 0.053 | 0.1606 | 0.053 | 0.1452 | 0.0684 | 0.053 | 0.1529 | 0.0607 | 0.053 | 0.1606 | 0.053 | 0.0991 | 0.1145 | 0.053 | 0.1606 | 0.053 | 0.0537 | 0.1634 | 0.2302 | 0.3063 | 0.1736 | 0.5629 | 0.9979 | 0.0675 | 0.1057 | 0.1407 | 0.0878 | 0.972 | 0.1265 | 0.1479 | 0.0761 | 0.1375 | 0.053 | 0.053 | 0.1879 | 0.3499 | 1.1288 | 0.5981 | 0.2402 | 0.053 | 0.053 | 0.1606 | 0.053 | 0.1606 | 0.053 | 0.0607 | 0.1529
Load_TR3_F1_37 | prosumer | 0.1478 | 0.1059 | 0.05 | 0.05 | 0.2037 | 0.05 | 0.1269 | 0.1269 | 0.05 | 0.2037 | 0.05 | 0.2037 | 0.05 | 0.1199 | 0.1338 | 0.0543 | 0.2443 | 0.1614 | 0.223 | 0.3209 | 0.1951 | 0.3382 | 0.229 | 1.3619 | 0.265 | 0.1515 | 0.2037 | 0.05 | 0.1467 | 0.3094 | 1.259 | 0.2287 | 0.0984 | 0.1677 | 0.2486 | 0.1656 | 0.2381 | 0.1488 | 0.162 | 0.3544 | 1.2102 | 0.2354 | 0.7016 | 0.4429 | 0.3211 | 0.1987 | 0.2223 | 0.5724
Load_TR3_F1_38 | prosumer | 0.1096 | 0.052 | 0.168 | 0.1108 | 0.0958 | 0.1399 | 0.0951 | 0.1197 | 0.048 | 0.1197 | 0.1831 | 0.0998 | 0.1739 | 0.109 | 0.048 | 0.2349 | 0.048 | 0.1213 | 0.1616 | 0.048 | 0.1563 | 0.1265 | 0.1077 | 0.1594 | 0.0637 | 0.1161 | 0.0951 | 0.1157 | 0.2234 | 0.172 | 0.048 | 0.1632 | 0.1197 | 0.1527 | 0.3295 | 0.2339 | 0.4542 | 0.508 | 0.3408 | 0.5425 | 0.5785 | 0.506 | 0.1318 | 0.0759 | 0.2965 | 0.3419 | 0.3942 | 0.1793
Load_TR3_F1_39 | customer | 0.2264 | 0.052 | 0.1512 | 0.052 | 0.0768 | 0.2115 | 0.052 | 0.2316 | 0.0567 | 0.1512 | 0.0709 | 0.1182 | 0.1512 | 0.052 | 0.1958 | 0.2672 | 0.1541 | 0.1591 | 0.1549 | 0.0867 | 0.2699 | 0.1512 | 0.1371 | 0.0768 | 0.1264 | 0.1371 | 0.0619 | 0.1933 | 0.0851 | 0.052 | 0.1264 | 0.0768 | 0.057 | 0.2533 | 0.073 | 0.1064 | 0.2033 | 0.052 | 0.1413 | 0.1045 | 0.2027 | 1.3042 | 0.487 | 0.516 | 0.6302 | 0.6205 | 0.607 | 0.2511
Load_TR3_F1_4 | prosumer | 0.081 | 0.2796 | 0.049 | 0.2026 | 0.1579 | 0.049 | 0.1356 | 0.201 | 0.073 | 0.1979 | 0.1626 | 0.1323 | 0.2282 | 0.049 | 0.225 | 0.049 | 0.049 | 0.2283 | 0.1322 | 0.049 | 0.1259 | 0.2346 | 0.049 | 0.2491 | 0.1114 | 0.1627 | 0.1979 | 0.049 | 0.2779 | 0.0827 | 0.1308 | 0.2298 | 0.049 | 0.049 | 0.1308 | 0.2298 | 0.1521 | 0.209 | 0.065 | 0.0906 | 0.27 | 0.049 | 0.3116 | 0.049 | 0.177 | 0.097 | 0.081 | 0.193
Load_TR3_F1_40 | prosumer | 0.3348 | 1.2986 | 0.4244 | 0.1076 | 0.1289 | 0.1935 | 0.043 | 0.1836 | 0.1209 | 0.0688 | 0.207 | 0.1076 | 0.2149 | 0.043 | 0.1074 | 0.336 | 0.1331 | 0.3342 | 0.2144 | 0.1326 | 0.1076 | 0.1055 | 0.156 | 0.1159 | 0.4096 | 0.1471 | 0.0597 | 0.197 | 0.2085 | 0.2727 | 0.0821 | 0.1076 | 0.1211 | 0.1367 | 0.1076 | 0.2149 | 0.0574 | 0.2651 | 0.1015 | 0.3181 | 0.5059 | 0.4299 | 0.4875 | 0.3207 | 0.6321 | 0.4502 | 0.4628 | 0.2833
Load_TR3_F1_41 | prosumer | 0.054 | 0.054 | 0.2292 | 0.054 | 0.2053 | 0.0779 | 0.054 | 0.2292 | 0.054 | 0.1735 | 0.1098 | 0.054 | 0.2292 | 0.054 | 0.2556 | 0.342 | 0.2153 | 0.331 | 0.2925 | 0.2425 | 0.3985 | 0.1117 | 0.1667 | 0.1686 | 0.054 | 0.1416 | 0.1416 | 0.0575 | 0.1894 | 0.0938 | 0.0949 | 0.3019 | 0.147 | 0.298 | 0.1404 | 0.137 | 0.2954 | 0.116 | 0.3385 | 0.3565 | 0.399 | 0.5824 | 0.6396 | 0.5397 | 0.6129 | 0.3975 | 0.4286 | 0.0938
Load_TR3_F1_42 | prosumer | 0.06 | 0.2428 | 0.152 | 0.1902 | 0.1849 | 0.2099 | 0.06 | 0.3348 | 0.06 | 0.1904 | 0.2044 | 0.06 | 0.3348 | 0.06 | 0.2889 | 0.1059 | 0.1386 | 0.2562 | 0.06 | 0.0863 | 0.276 | 0.0925 | 0.152 | 0.1126 | 0.06 | 0.2046 | 0.1902 | 0.4171 | 0.2076 | 0.2398 | 0.1257 | 0.1186 | 0.1908 | 0.178 | 0.1774 | 0.2963 | 0.3515 | 0.2009 | 0.6494 | 0.6687 | 1.3503 | 1.3382 | 0.7974 | 1.0016 | 1.3009 | 1.0223 | 0.875 | 0.5216
Load_TR3_F1_43 | customer | 0.1833 | 0.1591 | 0.037 | 0.1394 | 0.203 | 0.0541 | 0.2076 | 0.037 | 0.1569 | 0.2078 | 0.0617 | 0.1774 | 0.1694 | 0.1132 | 0.2529 | 0.049 | 0.2049 | 0.1613 | 0.1043 | 0.2446 | 0.1608 | 0.2745 | 0.3399 | 0.9871 | 0.2916 | 0.2177 | 0.1819 | 0.1932 | 0.3153 | 1.7103 | 0.8103 | 0.2615 | 1.2081 | 0.832 | 0.3076 | 0.2111 | 0.2316 | 0.4517 | 0.3119 | 0.5211 | 0.8261 | 1.4494 | 0.44 | 0.3287 | 0.1474 | 0.4401 | 0.2688 | 0.296
Load_TR3_F1_44 | prosumer | 0.041 | 0.112 | 0.041 | 0.112 | 0.041 | 0.112 | 0.041 | 0.041 | 0.041 | 0.041 | 0.0804 | 0.0725 | 1.3923 | 0.2898 | 0.0483 | 0.0923 | 0.0648 | 0.041 | 0.112 | 0.041 | 0.041 | 0.112 | 0.041 | 0.041 | 0.042 | 0.1034 | 0.211 | 0.3642 | 0.2427 | 0.3485 | 0.2646 | 0.3924 | 0.4183 | 0.2181 | 0.2788 | 0.3901 | 1.3275 | 1.8435 | 0.731 | 0.2526 | 0.3799 | 0.37 | 0.3221 | 0.3614 | 0.1936 | 0.041 | 0.112 | 0.041
Load_TR3_F1_45 | customer | 0.052 | 0.1186 | 0.1613 | 0.052 | 0.2279 | 0.052 | 0.1186 | 0.1613 | 0.052 | 0.052 | 0.1121 | 0.1012 | 0.1678 | 0.1121 | 0.2773 | 0.3113 | 0.5342 | 0.3918 | 0.3089 | 0.244 | 0.052 | 0.052 | 0.0668 | 0.1038 | 0.1613 | 0.1186 | 0.1613 | 0.052 | 0.0927 | 0.1325 | 0.114 | 0.1658 | 0.1066 | 0.1186 | 0.1613 | 0.1186 | 0.1558 | 0.0575 | 0.052 | 0.2169 | 0.0629 | 0.3832 | 0.495 | 0.4527 | 0.2498 | 0.2131 | 0.0668 | 0.0705
Load_TR3_F1_46 | customer | 0.041 | 0.1877 | 0.2482 | 0.041 | 0.2542 | 0.1817 | 0.0655 | 0.1529 | 0.1817 | 0.1633 | 0.1178 | 0.3181 | 0.041 | 0.2701 | 0.1658 | 0.0766 | 0.4036 | 0.3181 | 0.1043 | 0.7129 | 1.8022 | 0.8775 | 0.4 | 0.2339 | 0.3309 | 0.041 | 0.1958 | 0.1633 | 0.0973 | 0.1395 | 0.1912 | 0.2447 | 0.041 | 0.2697 | 0.1103 | 0.1349 | 0.3267 | 0.2801 | 0.3054 | 0.2802 | 0.4678 | 0.6157 | 0.3544 | 0.2483 | 0.133 | 0.3226 | 0.1133 | 0.2058
Load_TR3_F1_47 | prosumer | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.0552 | 0.128 | 0.18 | 0.1399 | 0.2018 | 0.1592 | 0.053 | 0.1495 | 0.2362 | 0.1711 | 0.093 | 1.3663 | 0.1785 | 0.247 | 0.0998 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.0938 | 0.1275 | 0.1115 | 0.4656 | 0.2979 | 0.1001 | 0.053 | 0.053 | 0.4857 | 0.4521 | 0.7126 | 0.1609
Load_TR3_F1_48 | prosumer | 0.059 | 0.1475 | 0.1203 | 0.0794 | 0.1884 | 0.059 | 0.059 | 0.2088 | 0.059 | 0.0862 | 0.1816 | 0.059 | 0.059 | 0.2088 | 0.059 | 0.202 | 0.1988 | 0.4981 | 0.2341 | 0.3119 | 0.5542 | 0.4725 | 0.2271 | 0.3887 | 1.5262 | 0.3133 | 0.4614 | 0.4639 | 0.1002 | 0.1913 | 0.5063 | 0.7487 | 0.6873 | 0.8188 | 0.3371 | 0.3087 | 0.4588 | 1.7736 | 0.3947 | 0.4837 | 1.674 | 0.5374 | 0.6608 | 0.9905 | 1.746 | 1.6349 | 0.7602 | 0.0726
Load_TR3_F1_49 | prosumer | 0.1105 | 0.1409 | 0.036 | 0.0658 | 0.1702 | 0.036 | 0.2 | 0.036 | 0.036 | 0.2 | 0.036 | 0.036 | 0.2 | 0.036 | 0.0435 | 0.215 | 0.0435 | 0.0485 | 0.2045 | 0.036 | 0.0509 | 0.1851 | 0.036 | 0.0807 | 0.1552 | 0.036 | 0.036 | 0.2026 | 0.3019 | 1.207 | 0.0909 | 0.1262 | 0.143 | 0.0627 | 0.2383 | 0.0615 | 0.04 | 0.1454 | 0.2401 | 0.271 | 0.4008 | 0.395 | 0.5714 | 0.5932 | 0.4223 | 0.4381 | 0.3057 | 0.305
Load_TR3_F1_5 | prosumer | 0.4989 | 0.6213 | 0.2679 | 0.1765 | 0.1866 | 0.2721 | 0.1794 | 0.255 | 0.1536 | 0.1723 | 0.1689 | 0.2836 | 0.1251 | 0.1437 | 0.2589 | 0.2321 | 0.058 | 0.2118 | 0.2247 | 0.2344 | 0.1437 | 0.2025 | 1.8257 | 2.081 | 0.6405 | 0.4047 | 0.3807 | 0.6716 | 0.1033 | 0.2851 | 0.2021 | 0.0723 | 0.4035 | 0.0694 | 0.2408 | 0.2465 | 0.091 | 0.3428 | 0.5995 | 0.9054 | 0.5255 | 0.9658 | 0.8125 | 0.7217 | 0.8593 | 0.9206 | 0.822 | 0.236
Load_TR3_F1_6 | prosumer | 0.1521 | 0.041 | 0.2431 | 0.041 | 0.041 | 0.2134 | 0.0707 | 0.0528 | 0.1754 | 0.0969 | 0.0904 | 0.1937 | 0.041 | 0.2431 | 0.041 | 0.1188 | 0.1653 | 0.1129 | 1.9727 | 0.4666 | 0.3996 | 0.4737 | 0.1089 | 0.041 | 0.041 | 0.041 | 0.1712 | 0.057 | 0.1264 | 0.2626 | 0.2035 | 0.1306 | 0.0975 | 0.2341 | 0.1441 | 0.1965 | 0.2996 | 0.4575 | 0.2759 | 0.4943 | 0.041 | 0.1357 | 0.4136 | 0.3023 | 0.5755 | 0.6764 | 0.4409 | 0.4726
Load_TR3_F1_7 | customer | 0.055 | 0.3199 | 0.0617 | 0.1259 | 0.3515 | 0.2803 | 0.3727 | 1.3461 | 0.0505 | 0.1046 | 0.037 | 0.037 | 0.1181 | 0.037 | 0.1181 | 0.1474 | 0.3387 | 0.1699 | 1.7919 | 0.9711 | 0.3198 | 0.0902 | 0.1181 | 0.037 | 0.082 | 0.1112 | 0.2524 | 0.0828 | 1.4081 | 0.3186 | 0.3844 | 0.037 | 0.4687 | 0.2444 | 0.2364 | 0.1854 | 0.1782 | 0.1437 | 0.2281 | 0.398 | 0.6401 | 0.7186 | 0.4868 | 0.7422 | 1.3567 | 2.1454 | 0.845 | 0.6389
Load_TR3_F1_8 | prosumer | 0.043 | 0.043 | 0.3915 | 0.2192 | 0.2246 | 0.1182 | 0.043 | 0.043 | 0.1182 | 0.043 | 0.0848 | 0.0764 | 0.043 | 0.1182 | 0.043 | 0.0973 | 0.0639 | 0.1566 | 0.9703 | 0.2427 | 0.1873 | 0.2673 | 0.3341 | 1.0896 | 0.4457 | 0.6726 | 1.4895 | 2.0191 | 3.3654 | 1.9333 | 0.0764 | 0.0485 | 0.2104 | 0.1393 | 0.2109 | 0.7416 | 1.9543 | 0.3796 | 0.1343 | 1.1383 | 0.2346 | 0.2736 | 0.3935 | 0.4165 | 0.3473 | 0.1182 | 0.043 | 0.043
Load_TR3_F1_9 | prosumer | 0.1489 | 0.0821 | 0.042 | 0.189 | 0.042 | 0.042 | 0.1222 | 0.1088 | 0.0687 | 0.1623 | 0.042 | 0.1489 | 0.0821 | 0.1394 | 0.1757 | 0.1111 | 0.1686 | 0.1389 | 0.042 | 0.189 | 0.042 | 0.1088 | 0.1222 | 0.042 | 0.042 | 0.1824 | 0.0554 | 0.1715 | 0.1362 | 0.042 | 1.7143 | 0.0621 | 0.1373 | 0.3129 | 0.4083 | 0.3813 | 0.4322 | 1.658 | 0.1556 | 0.0754 | 0.2226 | 0.5597 | 0.4283 | 0.5077 | 0.6936 | 1.3586 | 0.3208 | 0.169
Load_TR3_F2_1 | prosumer | 0.049 | 0.2227 | 0.049 | 0.049 | 0.2227 | 0.049 | 0.049 | 0.1911 | 0.0806 | 0.0885 | 0.1832 | 0.049 | 0.1516 | 0.1201 | 0.049 | 0.2227 | 0.049 | 0.0569 | 0.1641 | 0.1847 | 0.6622 | 0.4922 | 1.9595 | 3.0177 | 1.6081 | 0.049 | 0.2762 | 0.1911 | 0.0502 | 0.0711 | 0.2448 | 0.0556 | 0.2926 | 0.3847 | 0.3656 | 0.3989 | 0.4312 | 0.2791 | 0.242 | 1.3524 | 1.2675 | 0.4609 | 0.7192 | 0.4998 | 0.4661 | 0.3006 | 0.3043 | 0.4833
Load_TR3_F2_10 | prosumer | 0.0787 | 0.1963 | 0.1371 | 0.1848 | 0.1772 | 0.0615 | 0.2537 | 0.0969 | 0.05 | 0.1589 | 0.2031 | 0.05 | 0.2115 | 0.1504 | 0.0739 | 0.2881 | 0.05 | 0.2126 | 0.3631 | 0.2712 | 0.3035 | 0.2371 | 0.1525 | 0.1784 | 0.1609 | 0.2485 | 0.3003 | 0.881 | 0.1837 | 0.3193 | 0.2766 | 0.4681 | 0.2953 | 1.064 | 0.3438 | 0.2757 | 0.3545 | 0.2322 | 0.158 | 0.4381 | 0.332 | 0.3963 | 0.4858 | 0.4946 | 0.6232 | 0.8757 | 0.5518 | 0.7945
Load_TR3_F2_11 | prosumer | 0.1379 | 0.0791 | 0.057 | 0.1599 | 0.057 | 0.0791 | 0.1379 | 0.057 | 0.057 | 0.1599 | 0.057 | 0.057 | 0.1526 | 0.0644 | 0.057 | 0.1599 | 0.057 | 0.3124 | 2.2585 | 2.9768 | 0.9672 | 0.057 | 0.057 | 0.1935 | 0.057 | 0.057 | 0.1879 | 0.1329 | 0.0902 | 0.3141 | 0.0864 | 0.057 | 2.458 | 2.8762 | 0.6529 | 0.199 | 0.067 | 0.0627 | 0.2911 | 0.3588 | 0.4137 | 0.57 | 0.6139 | 0.5288 | 0.7143 | 0.7374 | 0.704 | 0.1232
Load_TR3_F2_12 | customer | 0.156 | 0.2423 | 0.059 | 0.1837 | 0.0867 | 0.1677 | 0.1682 | 0.1725 | 0.1358 | 0.2044 | 0.0659 | 0.123 | 0.1576 | 0.2215 | 0.1422 | 0.4851 | 0.0798 | 0.0654 | 0.2429 | 0.149 | 0.769 | 1.4466 | 0.187 | 0.1947 | 0.1133 | 0.1698 | 0.4289 | 0.16 | 0.1515 | 1.0742 | 0.5369 | 0.4872 | 0.6143 | 0.5038 | 0.5101 | 2.214 | 1.4007 | 0.3184 | 0.7006 | 0.6332 | 1.5705 | 0.3868 | 0.9106 | 0.5368 | 0.8006 | 0.3586 | 0.2631 | 0.1352
Load_TR3_F2_13 | customer | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.1403 | 0.0683 | 0.1676 | 0.095 | 0.0603 | 0.2496 | 0.5504 | 1.1195 | 0.4361 | 0.3277 | 0.2575 | 0.4459 | 0.3291 | 0.4991 | 1.1131 | 0.1818 | 1.0446 | 0.2906 | 0.5625 | 0.6073 | 0.7326 | 0.7114 | 0.4819 | 0.8153 | 0.2891 | 0.055 | 0.055 | 0.055
Load_TR3_F2_14 | prosumer | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.101 | 0.1178 | 0.1178 | 0.1949 | 0.2174 | 0.1874 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053
Load_TR3_F2_15 | customer | 0.1099 | 0.0949 | 0.2178 | 0.0765 | 0.1132 | 0.1349 | 0.1716 | 0.101 | 0.1349 | 0.2206 | 0.052 | 0.1278 | 0.2277 | 0.052 | 0.1274 | 0.1424 | 0.1604 | 0.1952 | 0.0742 | 0.1194 | 0.1349 | 0.1349 | 0.1377 | 0.1952 | 0.0842 | 0.2709 | 0.9023 | 0.2073 | 0.4138 | 0.0636 | 0.1377 | 0.2027 | 0.0671 | 0.183 | 0.1726 | 0.1194 | 0.1985 | 0.0897 | 0.198 | 0.1575 | 0.052 | 0.1377 | 0.165 | 0.1905 | 0.052 | 0.2178 | 0.1377 | 0.2027
Load_TR3_F2_16 | prosumer | 0.6389 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1474 | 0.0742 | 0.0919 | 0.1201 | 0.3111 | 0.05 | 0.2771 | 0.0695 | 0.0523 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0522 | 0.3299 | 0.2366 | 0.3456 | 0.0616 | 0.0519 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2573 | 0.2749 | 0.3586 | 0.05 | 0.05 | 0.05 | 0.05
Load_TR3_F2_17 | customer | 0.127 | 0.05 | 0.05 | 0.1578 | 0.05 | 0.1424 | 0.0654 | 0.05 | 0.1578 | 0.05 | 0.1424 | 0.2642 | 0.05 | 0.1578 | 0.05 | 0.0808 | 0.127 | 0.3171 | 0.2135 | 0.32 | 0.1935 | 0.5932 | 0.974 | 0.0581 | 1.0127 | 0.3863 | 1.8655 | 1.3416 | 1.436 | 1.7228 | 0.4947 | 0.1266 | 0.2609 | 1.6403 | 1.2782 | 0.2902 | 0.2698 | 0.2529 | 0.1935 | 0.1919 | 0.6105 | 0.515 | 0.6579 | 0.7414 | 0.05 | 0.05 | 0.05 | 0.1424
Load_TR3_F2_18 | prosumer | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.0546 | 0.0653 | 0.0968 | 0.1522 | 0.0629 | 0.3598 | 1.6063 | 0.2192 | 0.2314 | 0.1335 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.3376 | 0.4487 | 0.4591 | 0.4416 | 0.7366 | 0.345 | 0.298 | 0.3475 | 0.053 | 0.0627
Load_TR3_F2_19 | customer | 1.507 | 0.2281 | 0.1389 | 0.1572 | 0.318 | 0.1442 | 0.055 | 0.3078 | 0.0782 | 0.055 | 0.2477 | 0.2275 | 0.2229 | 0.055 | 0.1618 | 0.2241 | 0.1629 | 0.52 | 0.2801 | 0.7356 | 0.5802 | 0.2341 | 0.1758 | 0.2394 | 0.1442 | 0.1847 | 0.2904 | 0.055 | 0.3342 | 0.141 | 0.055 | 0.1779 | 0.2438 | 0.1183 | 0.2831 | 0.258 | 1.6771 | 1.4958 | 0.927 | 0.4027 | 0.3672 | 0.2547 | 0.4035 | 0.4954 | 1.7856 | 1.6459 | 0.3132 | 0.1442
Load_TR3_F2_2 | prosumer | 0.552 | 0.5336 | 0.0791 | 0.0852 | 0.047 | 0.1639 | 0.1108 | 0.1769 | 0.034 | 0.1249 | 0.1627 | 0.034 | 0.0535 | 0.2342 | 0.034 | 0.1108 | 0.1769 | 0.1162 | 0.1939 | 0.7136 | 1.6256 | 0.1821 | 0.1692 | 0.0511 | 0.1769 | 0.0894 | 0.0878 | 0.1444 | 0.1108 | 0.1769 | 0.034 | 0.0596 | 0.2216 | 0.0405 | 0.0766 | 0.211 | 0.034 | 0.2277 | 0.06 | 0.0917 | 0.196 | 0.0681 | 0.3383 | 0.2615 | 0.4739 | 0.7498 | 0.4101 | 0.5486
Load_TR3_F2_20 | prosumer | 0.6829 | 0.1487 | 0.1433 | 0.054 | 0.054 | 0.1433 | 0.054 | 0.0987 | 0.0987 | 0.054 | 0.1433 | 0.054 | 0.1242 | 0.0731 | 0.054 | 0.054 | 0.1709 | 0.054 | 0.054 | 0.1433 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 1.3204 | 1.0702 | 0.3336 | 0.5809 | 0.2345 | 0.504 | 0.5493 | 0.267 | 0.2337 | 0.1306 | 0.1097 | 0.3133 | 0.1131 | 0.0972 | 0.454 | 0.3174 | 0.4346 | 0.7294 | 0.5623 | 0.672 | 0.5912 | 0.5069 | 0.6457
Load_TR3_F2_21 | prosumer | 0.7337 | 0.4382 | 0.8315 | 0.6654 | 0.4899 | 0.5671 | 0.207 | 0.053 | 0.1706 | 0.302 | 0.1636 | 0.2451 | 0.1169 | 0.1636 | 0.246 | 0.1436 | 0.1359 | 0.067 | 0.5709 | 0.0806 | 0.197 | 0.3682 | 0.1509 | 0.2777 | 0.1251 | 0.2653 | 0.2073 | 0.165 | 0.2782 | 0.0824 | 1.5652 | 0.3238 | 0.7983 | 0.714 | 0.3466 | 0.3934 | 0.5162 | 0.1955 | 0.3509 | 0.6999 | 0.9316 | 0.6246 | 0.4953 | 0.4707 | 1.172 | 0.4837 | 0.7627 | 0.162
Load_TR3_F2_3 | prosumer | 0.102 | 0.1336 | 0.1508 | 0.05 | 0.2343 | 0.05 | 0.05 | 0.128 | 0.1563 | 0.05 | 0.1336 | 0.1378 | 0.063 | 0.2083 | 0.076 | 0.0673 | 0.1942 | 0.0728 | 0.128 | 0.2284 | 0.3522 | 0.3094 | 0.3283 | 0.1982 | 0.05 | 0.2127 | 0.0717 | 0.178 | 0.1063 | 0.05 | 0.2343 | 0.05 | 0.1563 | 0.05 | 0.1432 | 0.1411 | 0.05 | 0.204 | 0.0803 | 0.089 | 0.1953 | 0.05 | 0.05 | 0.377 | 0.2299 | 0.2557 | 0.3889 | 0.4533
Load_TR3_F2_4 | customer | 0.058 | 0.1998 | 0.0762 | 0.1901 | 0.0859 | 0.058 | 0.218 | 0.058 | 0.1139 | 0.0804 | 0.058 | 0.1998 | 0.0762 | 0.1139 | 0.1621 | 0.058 | 0.1589 | 0.1171 | 0.0853 | 0.1125 | 0.1362 | 0.0762 | 0.1551 | 0.1027 | 0.1261 | 0.1499 | 0.108 | 0.0898 | 0.1907 | 0.0853 | 0.0971 | 0.0971 | 0.1964 | 0.3697 | 0.1048 | 0.1815 | 0.1588 | 0.19 | 0.4683 | 0.4608 | 0.6936 | 0.8142 | 0.6415 | 0.5772 | 0.3928 | 0.5212 | 0.1499 | 0.1352
Load_TR3_F2_5 | prosumer | 0.1604 | 0.146 | 0.0993 | 0.2464 | 0.1486 | 0.2464 | 0.05 | 0.0893 | 0.1793 | 0.1764 | 0.1173 | 0.2214 | 0.1062 | 0.05 | 0.2609 | 0.05 | 1.0832 | 0.1787 | 0.1473 | 0.229 | 0.1154 | 0.1622 | 0.05 | 0.1486 | 0.2183 | 0.078 | 0.4863 | 0.1631 | 0.1437 | 1.6547 | 3.442 | 2.5557 | 0.4685 | 0.2429 | 0.2709 | 0.7899 | 0.4621 | 0.3407 | 0.2981 | 0.5661 | 0.3257 | 0.3186 | 0.4927 | 0.3999 | 0.4253 | 0.4266 | 0.05 | 0.05
Load_TR3_F2_6 | prosumer | 0.133 | 0.1726 | 0.1035 | 0.0899 | 0.2089 | 0.1444 | 0.049 | 0.1799 | 0.1735 | 0.1144 | 0.1435 | 0.1103 | 0.0831 | 0.1653 | 0.188 | 0.0926 | 0.1743 | 0.1471 | 0.2206 | 0.1971 | 0.3999 | 0.0776 | 0.1448 | 0.2017 | 0.4221 | 0.7898 | 0.1798 | 0.3244 | 0.0914 | 0.8639 | 0.494 | 0.2372 | 0.3199 | 0.0495 | 0.1368 | 0.2876 | 0.1581 | 1.5365 | 0.9181 | 0.1858 | 0.3383 | 0.3894 | 0.5756 | 0.768 | 1.7014 | 0.7933 | 0.263 | 0.0563
Load_TR3_F2_7 | customer | 0.1229 | 0.1048 | 0.2636 | 0.1733 | 0.0946 | 0.3423 | 0.051 | 0.1986 | 0.2383 | 0.0731 | 0.3254 | 0.0894 | 0.2783 | 0.051 | 0.305 | 0.5349 | 0.0803 | 0.4225 | 0.051 | 0.1342 | 0.3027 | 0.051 | 0.213 | 0.1731 | 0.1018 | 0.228 | 0.2307 | 0.1648 | 0.1763 | 0.1887 | 0.1656 | 0.1303 | 0.1848 | 0.252 | 0.08 | 0.1683 | 0.2396 | 0.051 | 0.2464 | 0.365 | 0.3026 | 0.5671 | 0.3052 | 0.5453 | 0.6002 | 0.7617 | 0.6653 | 0.1586
Load_TR3_F2_8 | customer | 0.1682 | 0.2022 | 0.054 | 0.2624 | 0.0859 | 0.5013 | 0.5032 | 0.229 | 0.154 | 0.1943 | 0.054 | 0.256 | 0.0923 | 0.054 | 0.2369 | 0.1114 | 0.1915 | 0.1568 | 0.0581 | 0.2657 | 0.0826 | 0.1178 | 0.2428 | 0.054 | 0.2425 | 0.109 | 0.0773 | 0.285 | 0.0595 | 0.2708 | 0.0939 | 0.143 | 0.2666 | 0.1469 | 0.3544 | 0.0599 | 0.3068 | 1.0344 | 0.3307 | 0.737 | 0.5354 | 0.5226 | 0.9581 | 1.6517 | 0.4325 | 0.4977 | 0.1752 | 0.1303
Load_TR3_F2_9 | prosumer | 0.7686 | 0.1095 | 0.2172 | 0.1095 | 0.033 | 0.1095 | 0.0581 | 0.1921 | 0.0925 | 0.2091 | 0.0581 | 0.1095 | 0.2172 | 0.0585 | 0.2514 | 0.0497 | 0.21 | 0.2476 | 0.0925 | 0.184 | 0.1512 | 0.1252 | 0.1335 | 0.1346 | 0.2214 | 0.3324 | 0.4193 | 0.1346 | 0.033 | 0.0879 | 0.379 | 0.0614 | 0.2287 | 0.5115 | 0.2686 | 0.2853 | 0.0986 | 0.0615 | 0.5209 | 1.4391 | 1.3432 | 0.4148 | 0.2032 | 0.4023 | 0.2672 | 0.5403 | 0.5171 | 0.168

## 5. Raw batt charge
Raw batt charge
Verbatim copy of Charge_kW (TR3_analysis_data.xlsx). One row per half-hour, one column per battery (kW).
period | hour | BES_TR3_one195_C | BES_TR3_one235_A | BES_TR3_one242_B | BES_TR3_one252_C | BES_TR3_one260_C | BES_TR3_one299_B | BES_TR3_one313_A | BES_TR3_one42_B | BES_TR3_one320_B | BES_TR3_one346_C | BES_TR3_one363_C | BES_TR3_one366_B | BES_TR3_one371_C | BES_TR3_one375_C | BES_TR3_one410_B | BES_TR3_one50_A | BES_TR3_one423_B | BES_TR3_one446_B | BES_TR3_one469_A | BES_TR3_one477_A | BES_TR3_one480_A | BES_TR3_one482_B | BES_TR3_one521_C | BES_TR3_one528_C | BES_TR3_one61_A | BES_TR3_one544_A | BES_TR3_one552_B | BES_TR3_one559_C | BES_TR3_one570_B | BES_TR3_one605_A | BES_TR3_one614_B | BES_TR3_one617_A | BES_TR3_one73_A | BES_TR3_one76_A | BES_TR3_one137_A | BES_TR3_one176_A | BES_TR3_two130_C | BES_TR3_two249_A | BES_TR3_two267_C | BES_TR3_two292_B | BES_TR3_two308_A | BES_TR3_two313_C | BES_TR3_two137_B | BES_TR3_two316_A | BES_TR3_two339_A | BES_TR3_two149_B | BES_TR3_two225_C | BES_TR3_two229_A | BES_TR3_two242_B
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4.5 | 0.118 | 0 | 0 | 0.126 | 0.065 | 0.059 | 0.084 | 0.163 | 0.124 | 0.182 | 0.062 | 0 | 0.026 | 0 | 0 | 0 | 0.072 | 0.172 | 0.049 | 0.007 | 0.183 | 0.18 | 0.029 | 0.113 | 0 | 0.164 | 0.03 | 0.042 | 0.133 | 0.18 | 0.088 | 0.033 | 0.031 | 0.048 | 0.19 | 0 | 0.144 | 0.074 | 0.073 | 0.18 | 0.124 | 0.092 | 0.079 | 0.12 | 0 | 0.154 | 0 | 0 | 0
11 | 5 | 0.176 | 0.393 | 0.248 | 0.18 | 0.413 | 0.317 | 0.138 | 0.343 | 0.415 | 0.368 | 0.113 | 0.166 | 0.419 | 0.277 | 0.104 | 0 | 0.336 | 0.241 | 0.227 | 0 | 0.406 | 0.301 | 0.411 | 0.278 | 0.126 | 0.254 | 0.294 | 0.257 | 0.266 | 0.408 | 0.164 | 0.425 | 0.235 | 0.198 | 0.377 | 0.189 | 0.278 | 0.258 | 0.404 | 0.408 | 0.296 | 0.235 | 0.241 | 0.203 | 0.24 | 0.27 | 0.113 | 0.029 | 0.173
12 | 5.5 | 0.633 | 0.486 | 0.466 | 0.508 | 0.628 | 0.689 | 0.392 | 0.572 | 0.696 | 0.664 | 0.317 | 0.313 | 0.663 | 0.548 | 0.151 | 0.409 | 0.467 | 0.636 | 0.523 | 0.129 | 0.597 | 0.689 | 0.538 | 0.642 | 0.331 | 0.634 | 0.595 | 0.682 | 0.484 | 0.687 | 0.497 | 0.706 | 0.366 | 0.27 | 0.665 | 0.222 | 0.693 | 0.692 | 0.685 | 0.689 | 0.506 | 0.411 | 0.615 | 0.502 | 0.404 | 0.511 | 0.15 | 0.168 | 0.261
13 | 6 | 0.832 | 1.002 | 0.903 | 0.62 | 0.946 | 0.926 | 0.621 | 0.836 | 0.849 | 0.997 | 0.438 | 0.35 | 0.879 | 0.896 | 0.402 | 0.47 | 0.862 | 0.804 | 0.711 | 0.296 | 0.998 | 0.949 | 0.998 | 0.874 | 0.427 | 0.833 | 0.688 | 0.713 | 0 | 0.92 | 0.727 | 0.848 | 0.792 | 0.614 | 1.005 | 0.442 | 0.896 | 0.836 | 0.895 | 0.995 | 0.736 | 0.602 | 0.863 | 0.662 | 0.8 | 0.854 | 0.418 | 0.31 | 0.307
14 | 6.5 | 1.182 | 1.245 | 1.312 | 0.97 | 1.31 | 0.771 | 0.803 | 1.131 | 1.312 | 1.237 | 0.593 | 0.581 | 1.316 | 1.145 | 0.578 | 0.613 | 0.949 | 1.263 | 1.062 | 0.384 | 1.308 | 1.243 | 1.238 | 1.249 | 0.8 | 1.315 | 1.134 | 1.298 | 0.729 | 1.178 | 0.809 | 1.322 | 1.044 | 0.605 | 1.24 | 0.539 | 1.238 | 1.207 | 1.293 | 1.305 | 0.968 | 0.796 | 0.954 | 0.945 | 1.024 | 0.98 | 0.629 | 0.344 | 0.62
15 | 7 | 1.548 | 1.454 | 1.458 | 0 | 1.57 | 0.199 | 0.697 | 1.425 | 1.527 | 1.615 | 0.779 | 0.613 | 1.624 | 1.361 | 0.535 | 0.986 | 0 | 1.489 | 1.338 | 0.325 | 1.616 | 1.613 | 1.532 | 1.618 | 0.816 | 1.559 | 1.202 | 1.377 | 1.201 | 1.526 | 1.19 | 1.623 | 1.199 | 1 | 1.623 | 0.657 | 1.617 | 1.592 | 1.609 | 1.565 | 1.199 | 0.988 | 1.424 | 1.195 | 1.212 | 1.382 | 0.572 | 0.437 | 0.582
16 | 7.5 | 1.722 | 1.871 | 1.929 | 1.409 | 1.112 | 1.773 | 0.85 | 1.272 | 1.403 | 0.909 | 0.87 | 0.894 | 1.145 | 1.74 | 0.804 | 1.001 | 0.752 | 1.754 | 1.559 | 0.267 | 0.979 | 1.168 | 1.52 | 1.523 | 1.185 | 1.639 | 1.386 | 1.869 | 1.389 | 0.885 | 1.279 | 1.223 | 1.496 | 1.115 | 1.536 | 0.876 | 1.456 | 1.687 | 1.207 | 0.642 | 1.431 | 1.181 | 1.617 | 1.427 | 1.584 | 1.66 | 0.937 | 0.648 | 0.938
17 | 8 | 0 | 0 | 0.78 | 1.562 | 0 | 0.713 | 1.287 | 0 | 0 | 0 | 0.826 | 0.972 | 0 | 1.03 | 0.285 | 1.36 | 0.658 | 0.613 | 1.057 | 0.611 | 0 | 0 | 0 | 0 | 1.366 | 1.571 | 1.056 | 0.676 | 1.633 | 0 | 1.499 | 0 | 1.923 | 1.25 | 0 | 0.964 | 0 | 0.281 | 0 | 0 | 1.161 | 1.362 | 1.45 | 1.527 | 1.845 | 0.622 | 0.049 | 0.675 | 0.922
18 | 8.5 | 1.335 | 0 | 0 | 1.295 | 0 | 1.048 | 1.671 | 0 | 0 | 0 | 0.966 | 1.159 | 0 | 0 | 1.13 | 1.482 | 0.371 | 0 | 0 | 0.354 | 0 | 0 | 0 | 0 | 1.357 | 0 | 0 | 0 | 0.754 | 0 | 0.102 | 0 | 0.883 | 1.319 | 0 | 1.129 | 0 | 0 | 0 | 0 | 0 | 0.138 | 0 | 0.328 | 0.859 | 0 | 1.09 | 0.804 | 1.021
19 | 9 | 0.914 | 0 | 0 | 0.292 | 0 | 0 | 0.391 | 0 | 0 | 0 | 1.157 | 1.301 | 0 | 0 | 1.258 | 1.219 | 1.127 | 0 | 0 | 0.997 | 0 | 0 | 0 | 0 | 0.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.237 | 0.818 | 1.292
20 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.158 | 0 | 0 | 1.389 | 0.367 | 1.2 | 0 | 0 | 1.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.254 | 0.915 | 1.149
21 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.461 | 0 | 0 | 0 | 0.061 | 0 | 0 | 0 | 0.971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.418 | 0.778 | 0
22 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79 | 0
23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.615 | 0 | 0 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.616 | 0 | 0
34 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.679 | 0 | 0
35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.499 | 0 | 0
36 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 18 | 0 | 0.747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 18.5 | 0 | 0.494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 19 | 0 | 0.245 | 0 | 0.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.234 | 0.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 19.5 | 0 | 0 | 0 | 0.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 6. Raw batt discharge
Raw batt discharge
Verbatim copy of Discharge_kW (TR3_analysis_data.xlsx). One row per half-hour, one column per battery (kW).
period | hour | BES_TR3_one195_C | BES_TR3_one235_A | BES_TR3_one242_B | BES_TR3_one252_C | BES_TR3_one260_C | BES_TR3_one299_B | BES_TR3_one313_A | BES_TR3_one42_B | BES_TR3_one320_B | BES_TR3_one346_C | BES_TR3_one363_C | BES_TR3_one366_B | BES_TR3_one371_C | BES_TR3_one375_C | BES_TR3_one410_B | BES_TR3_one50_A | BES_TR3_one423_B | BES_TR3_one446_B | BES_TR3_one469_A | BES_TR3_one477_A | BES_TR3_one480_A | BES_TR3_one482_B | BES_TR3_one521_C | BES_TR3_one528_C | BES_TR3_one61_A | BES_TR3_one544_A | BES_TR3_one552_B | BES_TR3_one559_C | BES_TR3_one570_B | BES_TR3_one605_A | BES_TR3_one614_B | BES_TR3_one617_A | BES_TR3_one73_A | BES_TR3_one76_A | BES_TR3_one137_A | BES_TR3_one176_A | BES_TR3_two130_C | BES_TR3_two249_A | BES_TR3_two267_C | BES_TR3_two292_B | BES_TR3_two308_A | BES_TR3_two313_C | BES_TR3_two137_B | BES_TR3_two316_A | BES_TR3_two339_A | BES_TR3_two149_B | BES_TR3_two225_C | BES_TR3_two229_A | BES_TR3_two242_B
1 | 0 | 0.19 | 0.046 | 0.046 | 0.38 | 0.048 | 0.104 | 0.34 | 0.033 | 0.046 | 0.098 | 0.054 | 0.599 | 0.072 | 0.144 | 0.165 | 0.16 | 0.131 | 0.149 | 0.048 | 0.149 | 0.15 | 0.053 | 0.148 | 0.11 | 0.081 | 0.335 | 0.054 | 0.06 | 0.041 | 0.053 | 0.059 | 0.111 | 0.499 | 0.152 | 0.043 | 0.149 | 0.049 | 0.079 | 0.138 | 0.053 | 0.639 | 0.053 | 0.552 | 0.683 | 0.734 | 0.102 | 0.16 | 0.133 | 0.769
2 | 0.5 | 0.261 | 0.107 | 0.31 | 0.125 | 0.21 | 0.171 | 0.053 | 0.033 | 0.199 | 0.078 | 0.172 | 0.544 | 0.042 | 0.23 | 0.047 | 0.055 | 0.055 | 0.17 | 0.091 | 0.139 | 0.05 | 0.053 | 0.106 | 0.052 | 0.28 | 1.299 | 0.054 | 0.243 | 0.112 | 0.053 | 0.148 | 0.141 | 0.621 | 0.041 | 0.043 | 0.082 | 0.223 | 0.196 | 0.079 | 0.053 | 0.05 | 0.053 | 0.534 | 0.149 | 0.438 | 0.134 | 0.146 | 0.173 | 0.109
3 | 1 | 0.079 | 0.191 | 0.057 | 0.048 | 0.048 | 0.098 | 0.162 | 0.033 | 0.046 | 0.094 | 0.079 | 0.548 | 0.042 | 0.161 | 0.221 | 0.055 | 0.087 | 0.22 | 0.163 | 0.083 | 0.05 | 0.161 | 0.05 | 0.168 | 0.049 | 0.424 | 0.229 | 0.152 | 0.041 | 0.053 | 0.12 | 0.036 | 0.268 | 0.243 | 0.391 | 0.042 | 0.049 | 0.137 | 0.057 | 0.053 | 0.05 | 0.053 | 0.079 | 0.143 | 0.831 | 0.151 | 0.099 | 0.104 | 0.217
4 | 1.5 | 0.259 | 0.073 | 0.118 | 0.166 | 0.048 | 0.059 | 0.243 | 0.069 | 0.158 | 0.051 | 0.082 | 0.656 | 0.206 | 0.153 | 0.122 | 0.112 | 0.163 | 0.177 | 0.126 | 0.034 | 0.105 | 0.053 | 0.05 | 0.111 | 0.203 | 0.108 | 0.054 | 0.19 | 0.112 | 0.053 | 0.079 | 0.066 | 0.176 | 0.041 | 0.219 | 0.189 | 0.049 | 0.185 | 0.16 | 0.053 | 0.05 | 0.053 | 0.085 | 0.054 | 0.387 | 0.05 | 0.246 | 0.09 | 0.109
5 | 2 | 0.17 | 0.199 | 0.161 | 0.048 | 0.072 | 0.26 | 0.087 | 0.069 | 0.088 | 0.051 | 0.089 | 0.043 | 0.042 | 0.096 | 0.082 | 0.177 | 0.055 | 0.048 | 0.206 | 0.191 | 0.095 | 0.145 | 0.204 | 0.096 | 0.158 | 0.129 | 0.205 | 0.185 | 0.041 | 0.053 | 0.188 | 0.17 | 0.187 | 0.041 | 0.225 | 0.042 | 0.223 | 0.177 | 0.057 | 0.053 | 0.05 | 0.053 | 0.047 | 0.054 | 0 | 0.234 | 0.149 | 0.209 | 0.033
6 | 2.5 | 0.154 | 0.046 | 0.063 | 0.166 | 0.143 | 0.053 | 0.087 | 0.033 | 0.046 | 0.051 | 0.054 | 0 | 0.087 | 0.304 | 0.091 | 0.055 | 0.055 | 0.22 | 0.126 | 0.146 | 0.05 | 0.068 | 0.05 | 0.14 | 0.049 | 0.096 | 0.078 | 0.21 | 0.112 | 0.053 | 0.059 | 0.036 | 0.272 | 0.213 | 0.118 | 0.042 | 0.049 | 0.061 | 0.079 | 0.053 | 0.05 | 0.053 | 0.164 | 0.143 | 0 | 0.05 | 0.246 | 0.144 | 0.109
7 | 3 | 0.204 | 0.243 | 0.236 | 0.048 | 0.048 | 0.132 | 0.195 | 0.033 | 0.199 | 0.121 | 0.054 | 0 | 0.161 | 0.094 | 0.192 | 0.233 | 0.195 | 0.177 | 0.048 | 0.034 | 0.135 | 0.053 | 0.127 | 0.095 | 0.136 | 0 | 0.054 | 0.06 | 0.041 | 0.053 | 0.059 | 0.2 | 0.179 | 0.071 | 0.043 | 0.122 | 0.049 | 0.254 | 0.138 | 0.053 | 0.05 | 0.053 | 0.111 | 0.054 | 0 | 0.05 | 0.05 | 0.049 | 0.058
8 | 3.5 | 0.178 | 0.078 | 0.128 | 0.069 | 0.045 | 0.183 | 0.154 | 0.03 | 0.043 | 0.048 | 0.116 | 0 | 0.039 | 0.18 | 0.082 | 0.053 | 0.052 | 0.131 | 0.263 | 0.187 | 0.062 | 0.149 | 0.123 | 0.116 | 0.199 | 0 | 0.226 | 0.331 | 0.038 | 0.05 | 0.206 | 0.033 | 0.188 | 0.051 | 0.04 | 0.107 | 0.188 | 0.093 | 0.054 | 0.05 | 0.047 | 0.051 | 0.174 | 0.096 | 0 | 0.125 | 0.088 | 0.179 | 0.19
9 | 4 | 0.093 | 0.036 | 0.43 | 0.105 | 0 | 0.003 | 0.14 | 0.053 | 0.087 | 0.001 | 0.029 | 0 | 0 | 0.141 | 0.18 | 0.625 | 0.075 | 0.2 | 0.022 | 0.084 | 0.0003 | 0.011 | 0.0003 | 0 | 0.042 | 0 | 0.01 | 0.01 | 0.004 | 0.003 | 0.022 | 0 | 0 | 0.144 | 0.068 | 0.044 | 0.031 | 0.0003 | 0.007 | 0.003 | 0.013 | 0.022 | 0 | 0.061 | 0 | 0.113 | 0.154 | 0.155 | 0.068
10 | 4.5 | 0 | 0.006 | 0.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015 | 0.007 | 0.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0.027 | 0.093
11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.096 | 0 | 0 | 0 | 0.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 7 | 0 | 0 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 8 | 1.244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.216 | 0 | 0
31 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.102 | 0 | 0
32 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.381 | 0 | 0 | 0.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.336 | 0 | 0
33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 17 | 0 | 1.647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 17.5 | 0 | 0.886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.177 | 0 | 0
37 | 18 | 0 | 0 | 0 | 1.968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.635 | 0 | 0 | 0 | 0 | 0 | 1.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
38 | 18.5 | 0 | 0 | 0 | 1.799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016 | 0 | 0 | 0 | 0 | 0 | 0.498 | 0 | 0 | 0 | 0 | 0 | 0 | 1.37 | 0 | 1.301 | 0 | 0 | 0.063 | 0 | 1.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025 | 1.3 | 0
39 | 19 | 0 | 0 | 0 | 0 | 0.197 | 0 | 0 | 0 | 0 | 0 | 0.264 | 0.011 | 0 | 0 | 0 | 0.419 | 0 | 0.176 | 0 | 1.039 | 0 | 0.23 | 0 | 0 | 0 | 0 | 0.016 | 0.281 | 0.455 | 0 | 0.118 | 0 | 0.277 | 0.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.107 | 0 | 0 | 0.029 | 0 | 0.114 | 0.78 | 0.337
40 | 19.5 | 0.578 | 0.103 | 0.253 | 0 | 0.19 | 0.34 | 0.422 | 0 | 0.181 | 0.46 | 0.36 | 1.218 | 0.282 | 0.326 | 0.084 | 0.796 | 0.128 | 0.492 | 0.452 | 0.721 | 1.576 | 0.133 | 0.247 | 0.435 | 0.024 | 0.211 | 0.263 | 0.562 | 0.172 | 0.358 | 0.403 | 0.164 | 0.812 | 0.427 | 1.031 | 0.022 | 1.245 | 0.331 | 0.252 | 0 | 0 | 0.382 | 0 | 0.374 | 0.606 | 0 | 0.512 | 0.146 | 1.386
41 | 20 | 0.764 | 0.224 | 0.422 | 0.033 | 0.179 | 0.404 | 0.571 | 0.045 | 0.12 | 0.416 | 0.462 | 0.314 | 0.347 | 0.509 | 0.1 | 0.914 | 0.33 | 0.563 | 0.306 | 0.673 | 0.271 | 0.033 | 1.19 | 0.559 | 0.258 | 0.486 | 0.382 | 1.331 | 0.365 | 0.278 | 1.659 | 0.381 | 0.508 | 0.029 | 0.215 | 0.213 | 1.248 | 0.312 | 0.394 | 0.033 | 0.035 | 0.447 | 0.179 | 0.303 | 0.914 | 0.178 | 0.316 | 0.331 | 1.333
42 | 20.5 | 0.637 | 0.401 | 0.517 | 0.233 | 0.942 | 0.594 | 0.761 | 0.101 | 0.224 | 0.685 | 0.91 | 0.453 | 0.363 | 0.421 | 0.369 | 2.416 | 0.528 | 0.805 | 0.048 | 0.777 | 0.307 | 0.053 | 0.235 | 0.506 | 0.049 | 0.43 | 0.582 | 1.338 | 0.37 | 0.1 | 0.537 | 0.395 | 0.966 | 0.136 | 0.274 | 0.56 | 0.461 | 0.396 | 0.57 | 0.053 | 0.257 | 0.442 | 0.068 | 0.435 | 0.625 | 0.05 | 0.319 | 0.389 | 0.415
43 | 21 | 0.969 | 0.529 | 0.576 | 0.127 | 1.132 | 0.442 | 0.639 | 0.033 | 0.374 | 0.702 | 1.203 | 0.552 | 0.162 | 0.454 | 0.213 | 2.272 | 0.367 | 0.622 | 0.284 | 0.98 | 0.282 | 0.161 | 0.702 | 0.132 | 0.312 | 0.488 | 0.64 | 0.797 | 0.322 | 0.053 | 0.661 | 0.571 | 0.813 | 0.414 | 0.393 | 0.428 | 0.719 | 0.486 | 0.614 | 0.053 | 0.275 | 0.737 | 0.338 | 0.729 | 0.495 | 0.05 | 0.493 | 0.576 | 0.203
44 | 21.5 | 0.695 | 0.336 | 0.355 | 0.406 | 0.48 | 1.42 | 0.776 | 0.041 | 0.258 | 0.62 | 0.433 | 0.549 | 0.404 | 0.419 | 0.369 | 0.338 | 0.397 | 0.802 | 0.048 | 0.701 | 0.37 | 0.053 | 0.443 | 0.076 | 0.049 | 0.321 | 0.54 | 1.002 | 0.361 | 0.053 | 0.991 | 0.593 | 0.722 | 0.302 | 0.417 | 0.508 | 0.5 | 0.495 | 0.529 | 0.053 | 0.359 | 0.345 | 0.261 | 0.562 | 0.471 | 0.377 | 0.4 | 0.768 | 0.402
45 | 22 | 1.114 | 0.32 | 0.276 | 0.387 | 0.465 | 1.679 | 0.637 | 0.097 | 0.378 | 0.745 | 0.442 | 0.365 | 0.369 | 0.438 | 0.059 | 0 | 1.034 | 0.9 | 0.096 | 0.393 | 0.308 | 0.161 | 0.321 | 0.296 | 0.177 | 0.632 | 0.613 | 1.301 | 0.194 | 0.486 | 1.502 | 0.422 | 0.859 | 0.575 | 0.347 | 0.694 | 0.466 | 0.623 | 0.714 | 0.053 | 0.05 | 0.298 | 0.474 | 0.672 | 1.172 | 0.23 | 0.425 | 1.701 | 0.267
46 | 22.5 | 0.98 | 0.666 | 0.074 | 0.49 | 0.35 | 0.41 | 0.677 | 0.033 | 0.211 | 0.469 | 0.348 | 0.361 | 0.301 | 0.275 | 0.182 | 0 | 0.305 | 0.762 | 0.236 | 0 | 0.949 | 0.053 | 0.199 | 0.342 | 0.097 | 0.45 | 0.397 | 0.561 | 0.041 | 0.452 | 0 | 0.438 | 0.921 | 0.676 | 0.118 | 1.359 | 0.301 | 0.876 | 0.737 | 0.053 | 0.05 | 0.347 | 0.75 | 0.591 | 0.484 | 0.256 | 0.427 | 0.793 | 0.54
47 | 23 | 0.18 | 0.046 | 0.163 | 0.25 | 0.048 | 0.241 | 0.667 | 0.105 | 1.244 | 0.567 | 0.082 | 0.103 | 0.458 | 0.201 | 1.538 | 0 | 0.506 | 0.58 | 0.048 | 0 | 0.817 | 0.061 | 0.222 | 0.394 | 0.081 | 0.463 | 0.429 | 0 | 0.112 | 0.713 | 0 | 0.306 | 0.822 | 0.441 | 0.043 | 0.321 | 0.304 | 0.552 | 0.704 | 0.053 | 0.05 | 0.053 | 0.41 | 0.507 | 0.763 | 0.389 | 0.05 | 0.263 | 0.517
48 | 23.5 | 0.938 | 0.176 | 0.176 | 0.048 | 0.167 | 0.171 | 0.134 | 0.033 | 0.224 | 0.182 | 0.089 | 0.074 | 0.109 | 0.149 | 1.405 | 0 | 0.171 | 0.991 | 0.233 | 0 | 0.239 | 0.153 | 0.572 | 0.179 | 0.193 | 0.283 | 0.094 | 0 | 0.041 | 0.161 | 0 | 0.305 | 0.236 | 0.473 | 0.043 | 0.169 | 0.483 | 0.794 | 0.123 | 0.053 | 0.05 | 0.063 | 0.549 | 0.646 | 0.162 | 0.453 | 0.05 | 0.056 | 0.168

## 7. PV allocation (per period)
TR3 PV allocation — per half-hour
VIOLET = aggregated live from the raw sheets 3–6 (SUM / SUMIF). AMBER = priority split (MIN formulas): PV → prosumer load → battery → customer load → export.
period | hour (h) | PV (kW) | prosumer load (kW) | customer load (kW) | batt charge (kW) | batt discharge (kW) | batt net =chg−dis | PV→ prosumer | PV→ battery | PV→ customer | PV→ export | customer ←grid
1 | 0 | 0 | 9.242 | 6.1008 | 0 | 9.244 | -9.244 | 0 | 0 | 0 | 0 | 6.1008
2 | 0.5 | 0 | 8.8049 | 4.1829 | 0 | 8.807 | -8.807 | 0 | 0 | 0 | 0 | 4.1829
3 | 1 | 0 | 7.015 | 3.1018 | 0 | 7.015 | -7.015 | 0 | 0 | 0 | 0 | 3.1018
4 | 1.5 | 0 | 6.733 | 3.1167 | 0 | 6.455 | -6.455 | 0 | 0 | 0 | 0 | 3.1167
5 | 2 | 0 | 6.5173 | 2.9307 | 0 | 5.737 | -5.737 | 0 | 0 | 0 | 0 | 2.9307
6 | 2.5 | 0 | 5.5909 | 3.1114 | 0 | 4.827 | -4.827 | 0 | 0 | 0 | 0 | 3.1114
7 | 3 | 0 | 5.3406 | 3.1387 | 0 | 5.044 | -5.044 | 0 | 0 | 0 | 0 | 3.1387
8 | 3.5 | 0.1394 | 5.928 | 4.0854 | 0 | 5.313 | -5.313 | 0.1394 | 0 | 0 | 0 | 4.0854
9 | 4 | 2.0261 | 5.6999 | 2.3001 | 0.036 | 3.2899 | -3.2539 | 2.0261 | 0 | 0 | 0 | 2.3001
10 | 4.5 | 9.478 | 6.9676 | 2.5583 | 3.793 | 1.131 | 2.662 | 6.9676 | 2.5104 | 0 | 0 | 2.5583
11 | 5 | 18.7989 | 6.3844 | 2.227 | 12.611 | 0.111 | 12.5 | 6.3844 | 12.4145 | 0 | 0 | 2.227
12 | 5.5 | 30.2315 | 5.4489 | 3.1244 | 24.782 | 0 | 24.782 | 5.4489 | 24.782 | 0.0006 | 0 | 3.1238
13 | 6 | 42.7019 | 7.668 | 3.0125 | 35.642 | 0.606 | 35.036 | 7.668 | 35.0339 | 0 | 0 | 3.0125
14 | 6.5 | 55.3271 | 6.2176 | 2.4709 | 49.111 | 0 | 49.111 | 6.2176 | 49.1095 | 0 | 0 | 2.4709
15 | 7 | 67.8888 | 11.4151 | 3.2914 | 57.269 | 0.795 | 56.474 | 11.4151 | 56.4737 | 0 | 0 | 3.2914
16 | 7.5 | 80.4654 | 8.7084 | 5.7132 | 62.519 | 0 | 62.519 | 8.7084 | 62.519 | 5.7132 | 3.5248 | 0
17 | 8 | 92.2707 | 15.0558 | 8.5455 | 33.586 | 1.244 | 32.342 | 15.0558 | 32.342 | 8.5455 | 36.3274 | 0
18 | 8.5 | 103.3697 | 13.3213 | 4.6214 | 20.595 | 0 | 20.595 | 13.3213 | 20.595 | 4.6214 | 64.832 | 0
19 | 9 | 112.82 | 19.0656 | 6.2219 | 13.549 | 0.242 | 13.307 | 19.0656 | 13.307 | 6.2219 | 74.2255 | 0
20 | 9.5 | 120.8808 | 17.1438 | 6.0732 | 8.739 | 0.01 | 8.729 | 17.1438 | 8.729 | 6.0732 | 88.9348 | 0
21 | 10 | 127.955 | 16.8985 | 7.2628 | 2.701 | 0 | 2.701 | 16.8985 | 2.701 | 7.2628 | 101.0927 | 0
22 | 10.5 | 133.7951 | 14.2955 | 5.8192 | 1.904 | 0.137 | 1.767 | 14.2955 | 1.767 | 5.8192 | 111.9134 | 0
23 | 11 | 137.9386 | 22.2333 | 5.5863 | 0 | 0.591 | -0.591 | 22.2333 | 0 | 5.5863 | 110.119 | 0
24 | 11.5 | 139.7562 | 21.9888 | 3.817 | 0.329 | 0 | 0.329 | 21.9888 | 0.329 | 3.817 | 113.6214 | 0
25 | 12 | 140.2819 | 11.9531 | 9.3623 | 0.481 | 0 | 0.481 | 11.9531 | 0.481 | 9.3623 | 118.4855 | 0
26 | 12.5 | 139.2961 | 12.7509 | 9.5228 | 0 | 0 | 0 | 12.7509 | 0 | 9.5228 | 117.0224 | 0
27 | 13 | 135.9902 | 18.1356 | 12.3293 | 0 | 0.789 | -0.789 | 18.1356 | 0 | 12.3293 | 105.5253 | 0
28 | 13.5 | 130.9429 | 17.4091 | 5.9408 | 0.682 | 0 | 0.682 | 17.4091 | 0.682 | 5.9408 | 106.911 | 0
29 | 14 | 124.9191 | 14.0843 | 7.822 | 0.195 | 0.3 | -0.105 | 14.0843 | 0 | 7.822 | 103.0128 | 0
30 | 14.5 | 117.2862 | 15.6731 | 9.5163 | 0.333 | 0.216 | 0.117 | 15.6731 | 0.117 | 9.5163 | 91.9798 | 0
31 | 15 | 109.1737 | 20.6182 | 6.9962 | 0 | 3.707 | -3.707 | 20.6182 | 0 | 6.9962 | 81.5593 | 0
32 | 15.5 | 99.413 | 16.1785 | 4.5421 | 0.416 | 1.861 | -1.445 | 16.1785 | 0 | 4.5421 | 78.6924 | 0
33 | 16 | 88.4198 | 15.9448 | 6.4482 | 2.391 | 0.288 | 2.103 | 15.9448 | 2.103 | 6.4482 | 63.9238 | 0
34 | 16.5 | 75.1467 | 18.5203 | 8.3593 | 0.854 | 2.968 | -2.114 | 18.5203 | 0 | 8.3593 | 48.2671 | 0
35 | 17 | 62.7224 | 17.2124 | 8.6308 | 1.721 | 1.952 | -0.231 | 17.2124 | 0 | 8.6308 | 36.8792 | 0
36 | 17.5 | 49.9565 | 16.9107 | 9.0881 | 0.99 | 2.533 | -1.543 | 16.9107 | 0 | 9.0881 | 23.9577 | 0
37 | 18 | 37.6091 | 16.6135 | 12.0057 | 0.936 | 3.75 | -2.814 | 16.6135 | 0 | 12.0057 | 8.9899 | 0
38 | 18.5 | 25.7044 | 20.2104 | 9.6152 | 0.784 | 7.715 | -6.931 | 20.2104 | 0 | 5.494 | 0 | 4.1212
39 | 19 | 15.0087 | 14.9613 | 11.6008 | 0.63 | 4.896 | -4.266 | 14.9613 | 0 | 0.0474 | 0 | 11.5534
40 | 19.5 | 4.3684 | 23.6635 | 10.2867 | 0.021 | 19.46 | -19.439 | 4.3684 | 0 | 0 | 0 | 10.2867
41 | 20 | 0.8064 | 22.6836 | 12.4204 | 0 | 21.877 | -21.877 | 0.8064 | 0 | 0 | 0 | 12.4204
42 | 20.5 | 0 | 23.5018 | 11.727 | 0 | 23.503 | -23.503 | 0 | 0 | 0 | 0 | 11.727
43 | 21 | 0 | 25.5658 | 10.8158 | 0 | 25.569 | -25.569 | 0 | 0 | 0 | 0 | 10.8158
44 | 21.5 | 0 | 23 | 12.9244 | 0 | 22.17 | -22.17 | 0 | 0 | 0 | 0 | 12.9244
45 | 22 | 0 | 27.7968 | 11.8286 | 0 | 26.227 | -26.227 | 0 | 0 | 0 | 0 | 11.8286
46 | 22.5 | 0 | 24.4097 | 11.5904 | 0 | 20.388 | -20.388 | 0 | 0 | 0 | 0 | 11.5904
47 | 23 | 0 | 19.6472 | 6.956 | 0 | 16.867 | -16.867 | 0 | 0 | 0 | 0 | 6.956
48 | 23.5 | 0 | 13.6622 | 5.7031 | 0 | 12.261 | -12.261 | 0 | 0 | 0 | 0 | 5.7031
TOTAL | kWh/day | 1316.4443 | 352.3955 | 164.2229 | 168.8 | 139.948 | 28.8521 | 223.6645 | 162.998 | 84.8832 | 844.8986 | 79.3397
Each half-hour is 0.5 h, so daily energy (kWh) = Σ(power in kW) × 0.5.
Trace any input: e.g. cell C5 = SUM of column C on sheet 3 (PV of all 70 connections at 00:00). Click it to see the formula.

## 8. Results & charts
TR3 PV allocation — results
Where the day's PV goes |  |  | How the customers (21) are supplied
Destination | kWh/day | % of PV | Source | kWh/day | % of cust. load
PV → prosumers' own load | 223.6645 | 16.99% | From prosumer PV (day) | 84.8832 | 51.69%
PV → battery storage | 162.998 | 12.38% | From grid import (night) | 79.3397 | 48.31%
PV → customers | 84.8832 | 6.448% | TOTAL customer load | 164.2229 | 100%
PV → export to grid | 844.8986 | 64.18%
TOTAL (= PV) | 1316.4443 | 100%
Charts read live from sheet 7, which reads live from raw sheets 3–6.