## 1. Overview
TR5 — Where does the PV energy go?
Prosumers vs. pure customers — every kWh traced from the raw model inputs
Purpose
This workbook accounts for every kWh of PV generated on transformer TR5 over one representative day, and it is fully auditable: nothing is hand-typed except the raw model outputs. Follow the data chain below — each step is a live formula, so changing any raw number updates everything.
The data chain (how each number is built)
Sheet 3 · Raw PV per load | The PV profile of every connection, 48 half-hours. Copied verbatim from TR5_load_PV_48periods.xlsx (sheet PV_generation_kW). Customers = 0.
Sheet 4 · Raw load per load | The load profile of every connection, 48 half-hours, tagged prosumer / customer. Copied from TR5_load_PV_48periods.xlsx (sheet Load_P_kW).
Sheet 5 · Raw batt charge | Charging power of every battery, 48 half-hours. Copied from the rolling dispatch TR5_analysis_data.xlsx (sheet Charge_kW).
Sheet 6 · Raw batt discharge | Discharging power of every battery. Copied from the same run (Discharge_kW).
Sheet 7 · PV allocation | Per half-hour: the five blue inputs are AGGREGATED from sheets 3–6 by SUM / SUMIF; the amber columns then split the PV by the priority rule.
Sheets 1 & 8 · Results | Daily totals (Σ×0.5 h) and shares. Every headline cell links to sheet 7.
The aggregation formulas (sheet 7, per half-hour)
PV (all)
prosumer load
customer load
battery charge
battery discharge
Headline results (all linked live to sheet 7)
Quantity | Value | Unit
Prosumers (PV + battery) | 214 | connections
Pure customers (load only) | 203 | connections
PV generated | 5100.2134 | kWh/day
PV → prosumers' own load (direct) | 1049.137 | kWh/day
PV → battery storage | 709.867 | kWh/day
PV → customers | 725.1666 | kWh/day
PV → export to grid | 2616.0428 | kWh/day
PV share reaching customers | 14.22% | % of PV
Customer load covered by PV | 50.37% | % of customer load
Customer load covered by grid | 49.63% | % of customer load
Colour key & provenance
• LIGHT-BLUE cell = data belonging to a prosumer (its rooftop PV, load, or battery). WHITE = a pure customer (load only). On sheet 7: VIOLET = value aggregated live from the raw sheets (SUM/SUMIF); AMBER = allocation formula; GREEN = daily total (Σ × 0.5 h).
• Per-load PV & load profiles: results/tables/TR5_load_PV_48periods.xlsx (built from OpData.xls).
• Per-battery charge/discharge: TR5_analysis/01_DAILY_ROLLING_DISPATCH/TR5_analysis_data.xlsx (exact-QCP rolling dispatch, RunFOR_Rolling, CPLEX).
• Load classification (PV size > 0 = prosumer): sheet 'Customers' of the load/PV workbook.
• Method note: priority energy allocation per half-hour; downstream network + battery round-trip losses (~3–4% of PV) are not separated out in the per-period disposition.

## 2. Load classification
TR5 load classification — 417 connections
214 prosumers (PV + battery) · 203 pure customers (load only)
ID | Load name | Bus | Phase | PV size (kW) | Type
459 | Load_TR5_F1_11 | TR5_one223 | 2 | 0 | customer
460 | Load_TR5_F1_11_dup | TR5_one223_dup | 2 | 0 | customer
463 | Load_TR5_F1_13 | TR5_one242 | 2 | 0 | customer
467 | Load_TR5_F1_15 | TR5_one260 | 3 | 0 | customer
470 | Load_TR5_F1_16_dup | TR5_one280_dup | 1 | 0 | customer
472 | Load_TR5_F1_17_dup | TR5_one287_dup | 2 | 0 | customer
456 | Load_TR5_F1_1_dup | TR5_one38_dup | 2 | 0 | customer
480 | Load_TR5_F1_20_dup | TR5_one320_dup | 2 | 0 | customer
482 | Load_TR5_F1_21_dup | TR5_one321_dup | 3 | 0 | customer
484 | Load_TR5_F1_22_dup | TR5_one328_dup | 1 | 0 | customer
485 | Load_TR5_F1_23 | TR5_one345 | 1 | 0 | customer
488 | Load_TR5_F1_24_dup | TR5_one346_dup | 3 | 0 | customer
489 | Load_TR5_F1_25 | TR5_one363 | 3 | 0 | customer
490 | Load_TR5_F1_25_dup | TR5_one363_dup | 3 | 0 | customer
491 | Load_TR5_F1_26 | TR5_one366 | 2 | 0 | customer
493 | Load_TR5_F1_27 | TR5_one371 | 3 | 0 | customer
494 | Load_TR5_F1_27_dup | TR5_one371_dup | 3 | 0 | customer
478 | Load_TR5_F1_2_dup | TR5_one42_dup | 2 | 0 | customer
503 | Load_TR5_F1_31 | TR5_one423 | 2 | 0 | customer
505 | Load_TR5_F1_32 | TR5_one446 | 2 | 0 | customer
508 | Load_TR5_F1_33_dup | TR5_one469_dup | 1 | 0 | customer
513 | Load_TR5_F1_36 | TR5_one482 | 2 | 0 | customer
514 | Load_TR5_F1_36_dup | TR5_one482_dup | 2 | 0 | customer
515 | Load_TR5_F1_37 | TR5_one521 | 3 | 0 | customer
519 | Load_TR5_F1_39 | TR5_one537 | 1 | 0 | customer
520 | Load_TR5_F1_39_dup | TR5_one537_dup | 1 | 0 | customer
500 | Load_TR5_F1_3_dup | TR5_one50_dup | 1 | 0 | customer
521 | Load_TR5_F1_4 | TR5_one61 | 1 | 0 | customer
525 | Load_TR5_F1_41 | TR5_one552 | 2 | 0 | customer
526 | Load_TR5_F1_41_dup | TR5_one552_dup | 2 | 0 | customer
528 | Load_TR5_F1_42_dup | TR5_one559_dup | 3 | 0 | customer
529 | Load_TR5_F1_43 | TR5_one560 | 3 | 0 | customer
530 | Load_TR5_F1_43_dup | TR5_one560_dup | 3 | 0 | customer
531 | Load_TR5_F1_44 | TR5_one570 | 2 | 0 | customer
532 | Load_TR5_F1_44_dup | TR5_one570_dup | 2 | 0 | customer
533 | Load_TR5_F1_45 | TR5_one585 | 1 | 0 | customer
534 | Load_TR5_F1_45_dup | TR5_one585_dup | 1 | 0 | customer
540 | Load_TR5_F1_48_dup | TR5_one614_dup | 2 | 0 | customer
541 | Load_TR5_F1_49 | TR5_one617 | 1 | 0 | customer
546 | Load_TR5_F1_6_dup | TR5_one76_dup | 1 | 0 | customer
548 | Load_TR5_F1_7_dup | TR5_one133_dup | 1 | 0 | customer
550 | Load_TR5_F1_8_dup | TR5_one137_dup | 1 | 0 | customer
552 | Load_TR5_F1_9_dup | TR5_one176_dup | 1 | 0 | customer
553 | Load_TR5_F4_1 | TR5_four50 | 3 | 0 | customer
554 | Load_TR5_F4_10 | TR5_four149 | 2 | 0 | customer
556 | Load_TR5_F4_11 | TR5_four163 | 3 | 0 | customer
558 | Load_TR5_F4_13 | TR5_four174 | 3 | 0 | customer
564 | Load_TR5_F4_19 | TR5_four265 | 3 | 0 | customer
568 | Load_TR5_F4_22 | TR5_four289 | 2 | 0 | customer
569 | Load_TR5_F4_23 | TR5_four292 | 3 | 0 | customer
571 | Load_TR5_F4_25 | TR5_four317 | 2 | 0 | customer
576 | Load_TR5_F4_3 | TR5_four65 | 2 | 0 | customer
577 | Load_TR5_F4_30 | TR5_four368 | 3 | 0 | customer
578 | Load_TR5_F4_31 | TR5_four372 | 3 | 0 | customer
580 | Load_TR5_F4_33 | TR5_four384 | 2 | 0 | customer
584 | Load_TR5_F4_37 | TR5_four437 | 1 | 0 | customer
587 | Load_TR5_F4_4 | TR5_four67 | 1 | 0 | customer
588 | Load_TR5_F4_40 | TR5_four455 | 1 | 0 | customer
589 | Load_TR5_F4_41 | TR5_four459 | 2 | 0 | customer
590 | Load_TR5_F4_42 | TR5_four466 | 3 | 0 | customer
591 | Load_TR5_F4_43 | TR5_four467 | 3 | 0 | customer
592 | Load_TR5_F4_44 | TR5_four480 | 1 | 0 | customer
596 | Load_TR5_F4_48 | TR5_four558 | 3 | 0 | customer
599 | Load_TR5_F4_50 | TR5_four573 | 1 | 0 | customer
600 | Load_TR5_F4_51 | TR5_four586 | 2 | 0 | customer
601 | Load_TR5_F4_52 | TR5_four590 | 1 | 0 | customer
602 | Load_TR5_F4_53 | TR5_four593 | 3 | 0 | customer
603 | Load_TR5_F4_54 | TR5_four604 | 1 | 0 | customer
605 | Load_TR5_F4_56 | TR5_four664 | 1 | 0 | customer
609 | Load_TR5_F4_6 | TR5_four78 | 2 | 0 | customer
610 | Load_TR5_F4_60 | TR5_four727 | 2 | 0 | customer
611 | Load_TR5_F4_61 | TR5_four732 | 2 | 0 | customer
615 | Load_TR5_F4_65 | TR5_four818 | 2 | 0 | customer
616 | Load_TR5_F4_66 | TR5_four821 | 1 | 0 | customer
617 | Load_TR5_F4_67 | TR5_four829 | 2 | 0 | customer
618 | Load_TR5_F4_68 | TR5_four832 | 1 | 0 | customer
620 | Load_TR5_F4_7 | TR5_four98 | 3 | 0 | customer
621 | Load_TR5_F4_70 | TR5_four846 | 3 | 0 | customer
622 | Load_TR5_F4_71 | TR5_four853 | 3 | 0 | customer
625 | Load_TR5_F4_74 | TR5_four936 | 3 | 0 | customer
626 | Load_TR5_F4_75 | TR5_four950 | 2 | 0 | customer
627 | Load_TR5_F4_76 | TR5_four957 | 1 | 0 | customer
629 | Load_TR5_F4_78 | TR5_four963 | 3 | 0 | customer
630 | Load_TR5_F4_79 | TR5_four978 | 1 | 0 | customer
631 | Load_TR5_F4_8 | TR5_four104 | 1 | 0 | customer
632 | Load_TR5_F4_80 | TR5_four988 | 1 | 0 | customer
633 | Load_TR5_F4_81 | TR5_four1013 | 2 | 0 | customer
638 | Load_TR5_F4_86 | TR5_four1108 | 3 | 0 | customer
639 | Load_TR5_F4_87 | TR5_four1123 | 3 | 0 | customer
643 | Load_TR5_F4_90 | TR5_four1152 | 2 | 0 | customer
645 | Load_TR5_F4_92 | TR5_four1193 | 3 | 0 | customer
650 | Load_TR5_F4_97 | TR5_four1230 | 3 | 0 | customer
651 | Load_TR5_F4_98 | TR5_four1241 | 3 | 0 | customer
653 | Load_TR5_F5_1 | TR5_five58 | 3 | 0 | customer
655 | Load_TR5_F5_10 | TR5_five147 | 3 | 0 | customer
662 | Load_TR5_F5_13_dup | TR5_five168_dup | 1 | 0 | customer
664 | Load_TR5_F5_14_dup | TR5_five170_dup | 1 | 0 | customer
666 | Load_TR5_F5_15_dup | TR5_five177_dup | 1 | 0 | customer
667 | Load_TR5_F5_16 | TR5_five186 | 3 | 0 | customer
668 | Load_TR5_F5_16_dup | TR5_five186_dup | 3 | 0 | customer
671 | Load_TR5_F5_18 | TR5_five199 | 3 | 0 | customer
672 | Load_TR5_F5_18_dup | TR5_five199_dup | 3 | 0 | customer
675 | Load_TR5_F5_2 | TR5_five67 | 3 | 0 | customer
677 | Load_TR5_F5_20 | TR5_five223 | 1 | 0 | customer
679 | Load_TR5_F5_21 | TR5_five242 | 1 | 0 | customer
681 | Load_TR5_F5_22 | TR5_five243 | 2 | 0 | customer
686 | Load_TR5_F5_24_dup | TR5_five285_dup | 2 | 0 | customer
687 | Load_TR5_F5_25 | TR5_five303 | 2 | 0 | customer
688 | Load_TR5_F5_25_dup | TR5_five303_dup | 2 | 0 | customer
690 | Load_TR5_F5_26_dup | TR5_five309_dup | 3 | 0 | customer
692 | Load_TR5_F5_27_dup | TR5_five324_dup | 2 | 0 | customer
694 | Load_TR5_F5_28_dup | TR5_five345_dup | 1 | 0 | customer
696 | Load_TR5_F5_29_dup | TR5_five355_dup | 1 | 0 | customer
676 | Load_TR5_F5_2_dup | TR5_five67_dup | 3 | 0 | customer
697 | Load_TR5_F5_3 | TR5_five78 | 1 | 0 | customer
700 | Load_TR5_F5_30_dup | TR5_five394_dup | 3 | 0 | customer
703 | Load_TR5_F5_32 | TR5_five445 | 3 | 0 | customer
704 | Load_TR5_F5_32_dup | TR5_five445_dup | 3 | 0 | customer
705 | Load_TR5_F5_33 | TR5_five451 | 1 | 0 | customer
706 | Load_TR5_F5_33_dup | TR5_five451_dup | 1 | 0 | customer
710 | Load_TR5_F5_35_dup | TR5_five466_dup | 1 | 0 | customer
711 | Load_TR5_F5_36 | TR5_five472 | 1 | 0 | customer
715 | Load_TR5_F5_38 | TR5_five494 | 2 | 0 | customer
717 | Load_TR5_F5_39 | TR5_five499 | 2 | 0 | customer
718 | Load_TR5_F5_39_dup | TR5_five499_dup | 2 | 0 | customer
719 | Load_TR5_F5_4 | TR5_five92 | 1 | 0 | customer
722 | Load_TR5_F5_40_dup | TR5_five512_dup | 1 | 0 | customer
723 | Load_TR5_F5_41 | TR5_five513 | 2 | 0 | customer
725 | Load_TR5_F5_42 | TR5_five520 | 3 | 0 | customer
726 | Load_TR5_F5_42_dup | TR5_five520_dup | 3 | 0 | customer
730 | Load_TR5_F5_44_dup | TR5_five540_dup | 1 | 0 | customer
731 | Load_TR5_F5_45 | TR5_five545 | 2 | 0 | customer
733 | Load_TR5_F5_46 | TR5_five551 | 3 | 0 | customer
734 | Load_TR5_F5_46_dup | TR5_five551_dup | 3 | 0 | customer
735 | Load_TR5_F5_47 | TR5_five585 | 1 | 0 | customer
737 | Load_TR5_F5_48 | TR5_five588 | 1 | 0 | customer
739 | Load_TR5_F5_49 | TR5_five631 | 2 | 0 | customer
740 | Load_TR5_F5_49_dup | TR5_five631_dup | 2 | 0 | customer
720 | Load_TR5_F5_4_dup | TR5_five92_dup | 1 | 0 | customer
743 | Load_TR5_F5_50 | TR5_five649 | 1 | 0 | customer
744 | Load_TR5_F5_50_dup | TR5_five649_dup | 1 | 0 | customer
749 | Load_TR5_F5_53 | TR5_five685 | 2 | 0 | customer
751 | Load_TR5_F5_54 | TR5_five695 | 1 | 0 | customer
753 | Load_TR5_F5_55 | TR5_five704 | 1 | 0 | customer
757 | Load_TR5_F5_57 | TR5_five733 | 3 | 0 | customer
758 | Load_TR5_F5_57_dup | TR5_five733_dup | 3 | 0 | customer
760 | Load_TR5_F5_58_dup | TR5_five735_dup | 1 | 0 | customer
761 | Load_TR5_F5_59 | TR5_five748 | 2 | 0 | customer
763 | Load_TR5_F5_6 | TR5_five117 | 2 | 0 | customer
767 | Load_TR5_F5_61 | TR5_five778 | 2 | 0 | customer
771 | Load_TR5_F5_63 | TR5_five799 | 3 | 0 | customer
773 | Load_TR5_F5_64 | TR5_five801 | 3 | 0 | customer
775 | Load_TR5_F5_65 | TR5_five809 | 2 | 0 | customer
776 | Load_TR5_F5_65_dup | TR5_five809_dup | 2 | 0 | customer
777 | Load_TR5_F5_66 | TR5_five831 | 3 | 0 | customer
778 | Load_TR5_F5_66_dup | TR5_five831_dup | 3 | 0 | customer
779 | Load_TR5_F5_67 | TR5_five881 | 3 | 0 | customer
780 | Load_TR5_F5_67_dup | TR5_five881_dup | 3 | 0 | customer
781 | Load_TR5_F5_68 | TR5_five905 | 2 | 0 | customer
782 | Load_TR5_F5_68_dup | TR5_five905_dup | 2 | 0 | customer
784 | Load_TR5_F5_7_dup | TR5_five118_dup | 2 | 0 | customer
785 | Load_TR5_F5_8 | TR5_five123 | 2 | 0 | customer
786 | Load_TR5_F5_8_dup | TR5_five123_dup | 2 | 0 | customer
787 | Load_TR5_F5_9 | TR5_five129 | 3 | 0 | customer
788 | Load_TR5_F5_9_dup | TR5_five129_dup | 3 | 0 | customer
790 | Load_TR5_F6_10 | TR5_six154 | 3 | 0 | customer
793 | Load_TR5_F6_13 | TR5_six191 | 2 | 0 | customer
795 | Load_TR5_F6_15 | TR5_six232 | 3 | 0 | customer
799 | Load_TR5_F6_19 | TR5_six269 | 3 | 0 | customer
801 | Load_TR5_F6_20 | TR5_six289 | 3 | 0 | customer
804 | Load_TR5_F6_23 | TR5_six329 | 1 | 0 | customer
806 | Load_TR5_F6_25 | TR5_six349 | 1 | 0 | customer
808 | Load_TR5_F6_27 | TR5_six362 | 3 | 0 | customer
809 | Load_TR5_F6_28 | TR5_six365 | 3 | 0 | customer
810 | Load_TR5_F6_29 | TR5_six378 | 1 | 0 | customer
815 | Load_TR5_F6_33 | TR5_six410 | 1 | 0 | customer
818 | Load_TR5_F6_36 | TR5_six484 | 2 | 0 | customer
819 | Load_TR5_F6_37 | TR5_six501 | 1 | 0 | customer
822 | Load_TR5_F6_4 | TR5_six82 | 1 | 0 | customer
825 | Load_TR5_F6_42 | TR5_six571 | 3 | 0 | customer
826 | Load_TR5_F6_43 | TR5_six583 | 1 | 0 | customer
829 | Load_TR5_F6_46 | TR5_six625 | 1 | 0 | customer
834 | Load_TR5_F6_50 | TR5_six652 | 1 | 0 | customer
836 | Load_TR5_F6_52 | TR5_six667 | 1 | 0 | customer
837 | Load_TR5_F6_53 | TR5_six699 | 3 | 0 | customer
842 | Load_TR5_F6_58 | TR5_six758 | 2 | 0 | customer
843 | Load_TR5_F6_59 | TR5_six784 | 2 | 0 | customer
844 | Load_TR5_F6_6 | TR5_six90 | 2 | 0 | customer
846 | Load_TR5_F6_61 | TR5_six801 | 3 | 0 | customer
848 | Load_TR5_F6_63 | TR5_six844 | 3 | 0 | customer
851 | Load_TR5_F6_66 | TR5_six869 | 3 | 0 | customer
853 | Load_TR5_F6_68 | TR5_six894 | 2 | 0 | customer
855 | Load_TR5_F6_7 | TR5_six105 | 1 | 0 | customer
856 | Load_TR5_F6_70 | TR5_six914 | 1 | 0 | customer
859 | Load_TR5_F6_73 | TR5_six938 | 1 | 0 | customer
860 | Load_TR5_F6_74 | TR5_six945 | 3 | 0 | customer
863 | Load_TR5_F6_77 | TR5_six974 | 3 | 0 | customer
864 | Load_TR5_F6_78 | TR5_six979 | 1 | 0 | customer
865 | Load_TR5_F6_79 | TR5_six990 | 2 | 0 | customer
868 | Load_TR5_F6_81 | TR5_six1020 | 1 | 0 | customer
869 | Load_TR5_F6_82 | TR5_six1025 | 2 | 0 | customer
870 | Load_TR5_F6_83 | TR5_six1064 | 3 | 0 | customer
871 | Load_TR5_F6_9 | TR5_six128 | 2 | 0 | customer
455 | Load_TR5_F1_1 | TR5_one38 | 2 | 2.5 | prosumer
457 | Load_TR5_F1_10 | TR5_one195 | 3 | 4 | prosumer
458 | Load_TR5_F1_10_dup | TR5_one195_dup | 3 | 4 | prosumer
461 | Load_TR5_F1_12 | TR5_one235 | 1 | 2.5 | prosumer
462 | Load_TR5_F1_12_dup | TR5_one235_dup | 1 | 2 | prosumer
464 | Load_TR5_F1_13_dup | TR5_one242_dup | 2 | 1.5 | prosumer
465 | Load_TR5_F1_14 | TR5_one252 | 3 | 3 | prosumer
466 | Load_TR5_F1_14_dup | TR5_one252_dup | 3 | 2 | prosumer
468 | Load_TR5_F1_15_dup | TR5_one260_dup | 3 | 1 | prosumer
469 | Load_TR5_F1_16 | TR5_one280 | 1 | 4 | prosumer
471 | Load_TR5_F1_17 | TR5_one287 | 2 | 3.5 | prosumer
473 | Load_TR5_F1_18 | TR5_one299 | 2 | 3 | prosumer
474 | Load_TR5_F1_18_dup | TR5_one299_dup | 2 | 1.5 | prosumer
475 | Load_TR5_F1_19 | TR5_one313 | 1 | 4 | prosumer
476 | Load_TR5_F1_19_dup | TR5_one313_dup | 1 | 1.5 | prosumer
477 | Load_TR5_F1_2 | TR5_one42 | 2 | 4 | prosumer
479 | Load_TR5_F1_20 | TR5_one320 | 2 | 4 | prosumer
481 | Load_TR5_F1_21 | TR5_one321 | 3 | 2 | prosumer
483 | Load_TR5_F1_22 | TR5_one328 | 1 | 2.5 | prosumer
486 | Load_TR5_F1_23_dup | TR5_one345_dup | 1 | 3 | prosumer
487 | Load_TR5_F1_24 | TR5_one346 | 3 | 2.5 | prosumer
492 | Load_TR5_F1_26_dup | TR5_one366_dup | 2 | 2 | prosumer
495 | Load_TR5_F1_28 | TR5_one375 | 3 | 3 | prosumer
496 | Load_TR5_F1_28_dup | TR5_one375_dup | 3 | 3.5 | prosumer
497 | Load_TR5_F1_29 | TR5_one410 | 2 | 3.5 | prosumer
498 | Load_TR5_F1_29_dup | TR5_one410_dup | 2 | 1.5 | prosumer
499 | Load_TR5_F1_3 | TR5_one50 | 1 | 2.5 | prosumer
501 | Load_TR5_F1_30 | TR5_one416 | 3 | 2 | prosumer
502 | Load_TR5_F1_30_dup | TR5_one416_dup | 3 | 4 | prosumer
504 | Load_TR5_F1_31_dup | TR5_one423_dup | 2 | 3.5 | prosumer
506 | Load_TR5_F1_32_dup | TR5_one446_dup | 2 | 4 | prosumer
507 | Load_TR5_F1_33 | TR5_one469 | 1 | 3 | prosumer
509 | Load_TR5_F1_34 | TR5_one477 | 1 | 3.5 | prosumer
510 | Load_TR5_F1_34_dup | TR5_one477_dup | 1 | 4 | prosumer
511 | Load_TR5_F1_35 | TR5_one480 | 1 | 2 | prosumer
512 | Load_TR5_F1_35_dup | TR5_one480_dup | 1 | 4 | prosumer
516 | Load_TR5_F1_37_dup | TR5_one521_dup | 3 | 4 | prosumer
517 | Load_TR5_F1_38 | TR5_one528 | 3 | 4 | prosumer
518 | Load_TR5_F1_38_dup | TR5_one528_dup | 3 | 2.5 | prosumer
523 | Load_TR5_F1_40 | TR5_one544 | 1 | 4 | prosumer
524 | Load_TR5_F1_40_dup | TR5_one544_dup | 1 | 2.5 | prosumer
527 | Load_TR5_F1_42 | TR5_one559 | 3 | 2 | prosumer
535 | Load_TR5_F1_46 | TR5_one590 | 1 | 4 | prosumer
536 | Load_TR5_F1_46_dup | TR5_one590_dup | 1 | 3.5 | prosumer
537 | Load_TR5_F1_47 | TR5_one605 | 1 | 4 | prosumer
538 | Load_TR5_F1_47_dup | TR5_one605_dup | 1 | 3 | prosumer
539 | Load_TR5_F1_48 | TR5_one614 | 2 | 2 | prosumer
542 | Load_TR5_F1_49_dup | TR5_one617_dup | 1 | 2 | prosumer
522 | Load_TR5_F1_4_dup | TR5_one61_dup | 1 | 1.5 | prosumer
543 | Load_TR5_F1_5 | TR5_one73 | 1 | 2.5 | prosumer
544 | Load_TR5_F1_5_dup | TR5_one73_dup | 1 | 3.5 | prosumer
545 | Load_TR5_F1_6 | TR5_one76 | 1 | 2 | prosumer
547 | Load_TR5_F1_7 | TR5_one133 | 1 | 2 | prosumer
549 | Load_TR5_F1_8 | TR5_one137 | 1 | 3.5 | prosumer
551 | Load_TR5_F1_9 | TR5_one176 | 1 | 4 | prosumer
555 | Load_TR5_F4_100 | TR5_four1252 | 3 | 4 | prosumer
557 | Load_TR5_F4_12 | TR5_four171 | 1 | 4 | prosumer
559 | Load_TR5_F4_14 | TR5_four180 | 1 | 4 | prosumer
560 | Load_TR5_F4_15 | TR5_four184 | 2 | 3 | prosumer
561 | Load_TR5_F4_16 | TR5_four200 | 1 | 2.5 | prosumer
562 | Load_TR5_F4_17 | TR5_four239 | 1 | 2 | prosumer
563 | Load_TR5_F4_18 | TR5_four259 | 2 | 2.5 | prosumer
565 | Load_TR5_F4_2 | TR5_four54 | 3 | 4 | prosumer
566 | Load_TR5_F4_20 | TR5_four279 | 2 | 1.5 | prosumer
567 | Load_TR5_F4_21 | TR5_four288 | 2 | 1.5 | prosumer
570 | Load_TR5_F4_24 | TR5_four301 | 3 | 1.5 | prosumer
572 | Load_TR5_F4_26 | TR5_four326 | 1 | 4 | prosumer
573 | Load_TR5_F4_27 | TR5_four352 | 1 | 4 | prosumer
574 | Load_TR5_F4_28 | TR5_four354 | 2 | 2 | prosumer
575 | Load_TR5_F4_29 | TR5_four358 | 3 | 2.5 | prosumer
579 | Load_TR5_F4_32 | TR5_four381 | 1 | 1.5 | prosumer
581 | Load_TR5_F4_34 | TR5_four385 | 1 | 4 | prosumer
582 | Load_TR5_F4_35 | TR5_four396 | 2 | 2 | prosumer
583 | Load_TR5_F4_36 | TR5_four423 | 3 | 4 | prosumer
585 | Load_TR5_F4_38 | TR5_four446 | 2 | 1.5 | prosumer
586 | Load_TR5_F4_39 | TR5_four451 | 3 | 4 | prosumer
593 | Load_TR5_F4_45 | TR5_four532 | 1 | 2.5 | prosumer
594 | Load_TR5_F4_46 | TR5_four548 | 2 | 3 | prosumer
595 | Load_TR5_F4_47 | TR5_four553 | 2 | 4 | prosumer
597 | Load_TR5_F4_49 | TR5_four562 | 3 | 2 | prosumer
598 | Load_TR5_F4_5 | TR5_four70 | 2 | 2.5 | prosumer
604 | Load_TR5_F4_55 | TR5_four659 | 2 | 2 | prosumer
606 | Load_TR5_F4_57 | TR5_four675 | 3 | 4 | prosumer
607 | Load_TR5_F4_58 | TR5_four704 | 2 | 4 | prosumer
608 | Load_TR5_F4_59 | TR5_four710 | 3 | 3 | prosumer
612 | Load_TR5_F4_62 | TR5_four734 | 1 | 1.5 | prosumer
613 | Load_TR5_F4_63 | TR5_four763 | 1 | 3 | prosumer
614 | Load_TR5_F4_64 | TR5_four797 | 3 | 3 | prosumer
619 | Load_TR5_F4_69 | TR5_four840 | 1 | 2 | prosumer
623 | Load_TR5_F4_72 | TR5_four854 | 1 | 3.5 | prosumer
624 | Load_TR5_F4_73 | TR5_four926 | 2 | 1.5 | prosumer
628 | Load_TR5_F4_77 | TR5_four958 | 3 | 3 | prosumer
634 | Load_TR5_F4_82 | TR5_four1027 | 1 | 3.5 | prosumer
635 | Load_TR5_F4_83 | TR5_four1063 | 3 | 1.5 | prosumer
636 | Load_TR5_F4_84 | TR5_four1091 | 2 | 4 | prosumer
637 | Load_TR5_F4_85 | TR5_four1103 | 3 | 4 | prosumer
640 | Load_TR5_F4_88 | TR5_four1132 | 3 | 4 | prosumer
641 | Load_TR5_F4_89 | TR5_four1140 | 1 | 4 | prosumer
642 | Load_TR5_F4_9 | TR5_four126 | 1 | 1.5 | prosumer
644 | Load_TR5_F4_91 | TR5_four1187 | 1 | 4 | prosumer
646 | Load_TR5_F4_93 | TR5_four1207 | 2 | 3 | prosumer
647 | Load_TR5_F4_94 | TR5_four1216 | 3 | 3.5 | prosumer
648 | Load_TR5_F4_95 | TR5_four1220 | 3 | 3 | prosumer
649 | Load_TR5_F4_96 | TR5_four1226 | 1 | 2.5 | prosumer
652 | Load_TR5_F4_99 | TR5_four1244 | 2 | 4 | prosumer
656 | Load_TR5_F5_10_dup | TR5_five147_dup | 3 | 4 | prosumer
657 | Load_TR5_F5_11 | TR5_five149 | 1 | 1.5 | prosumer
658 | Load_TR5_F5_11_dup | TR5_five149_dup | 1 | 3.5 | prosumer
659 | Load_TR5_F5_12 | TR5_five160 | 3 | 4 | prosumer
660 | Load_TR5_F5_12_dup | TR5_five160_dup | 3 | 3.5 | prosumer
661 | Load_TR5_F5_13 | TR5_five168 | 1 | 3 | prosumer
663 | Load_TR5_F5_14 | TR5_five170 | 1 | 3 | prosumer
665 | Load_TR5_F5_15 | TR5_five177 | 1 | 2.5 | prosumer
669 | Load_TR5_F5_17 | TR5_five194 | 3 | 4 | prosumer
670 | Load_TR5_F5_17_dup | TR5_five194_dup | 3 | 2.5 | prosumer
673 | Load_TR5_F5_19 | TR5_five220 | 3 | 2.5 | prosumer
674 | Load_TR5_F5_19_dup | TR5_five220_dup | 3 | 3 | prosumer
654 | Load_TR5_F5_1_dup | TR5_five58_dup | 3 | 2 | prosumer
678 | Load_TR5_F5_20_dup | TR5_five223_dup | 1 | 3.5 | prosumer
680 | Load_TR5_F5_21_dup | TR5_five242_dup | 1 | 2 | prosumer
682 | Load_TR5_F5_22_dup | TR5_five243_dup | 2 | 3 | prosumer
683 | Load_TR5_F5_23 | TR5_five284 | 3 | 4 | prosumer
684 | Load_TR5_F5_23_dup | TR5_five284_dup | 3 | 1.5 | prosumer
685 | Load_TR5_F5_24 | TR5_five285 | 2 | 1.5 | prosumer
689 | Load_TR5_F5_26 | TR5_five309 | 3 | 4 | prosumer
691 | Load_TR5_F5_27 | TR5_five324 | 2 | 2.5 | prosumer
693 | Load_TR5_F5_28 | TR5_five345 | 1 | 3.5 | prosumer
695 | Load_TR5_F5_29 | TR5_five355 | 1 | 1.5 | prosumer
699 | Load_TR5_F5_30 | TR5_five394 | 3 | 4 | prosumer
701 | Load_TR5_F5_31 | TR5_five421 | 1 | 3 | prosumer
702 | Load_TR5_F5_31_dup | TR5_five421_dup | 1 | 3.5 | prosumer
707 | Load_TR5_F5_34 | TR5_five457 | 2 | 4 | prosumer
708 | Load_TR5_F5_34_dup | TR5_five457_dup | 2 | 3.5 | prosumer
709 | Load_TR5_F5_35 | TR5_five466 | 1 | 4 | prosumer
712 | Load_TR5_F5_36_dup | TR5_five472_dup | 1 | 4 | prosumer
713 | Load_TR5_F5_37 | TR5_five488 | 2 | 3 | prosumer
714 | Load_TR5_F5_37_dup | TR5_five488_dup | 2 | 3.5 | prosumer
716 | Load_TR5_F5_38_dup | TR5_five494_dup | 2 | 2 | prosumer
698 | Load_TR5_F5_3_dup | TR5_five78_dup | 1 | 3 | prosumer
721 | Load_TR5_F5_40 | TR5_five512 | 1 | 4 | prosumer
724 | Load_TR5_F5_41_dup | TR5_five513_dup | 2 | 2.5 | prosumer
727 | Load_TR5_F5_43 | TR5_five537 | 3 | 2 | prosumer
728 | Load_TR5_F5_43_dup | TR5_five537_dup | 3 | 4 | prosumer
729 | Load_TR5_F5_44 | TR5_five540 | 1 | 2 | prosumer
732 | Load_TR5_F5_45_dup | TR5_five545_dup | 2 | 1.5 | prosumer
736 | Load_TR5_F5_47_dup | TR5_five585_dup | 1 | 4 | prosumer
738 | Load_TR5_F5_48_dup | TR5_five588_dup | 1 | 2 | prosumer
741 | Load_TR5_F5_5 | TR5_five108 | 2 | 4 | prosumer
745 | Load_TR5_F5_51 | TR5_five663 | 3 | 3 | prosumer
746 | Load_TR5_F5_51_dup | TR5_five663_dup | 3 | 4 | prosumer
747 | Load_TR5_F5_52 | TR5_five670 | 3 | 2.5 | prosumer
748 | Load_TR5_F5_52_dup | TR5_five670_dup | 3 | 2.5 | prosumer
750 | Load_TR5_F5_53_dup | TR5_five685_dup | 2 | 3.5 | prosumer
752 | Load_TR5_F5_54_dup | TR5_five695_dup | 1 | 2 | prosumer
754 | Load_TR5_F5_55_dup | TR5_five704_dup | 1 | 2 | prosumer
755 | Load_TR5_F5_56 | TR5_five719 | 1 | 4 | prosumer
756 | Load_TR5_F5_56_dup | TR5_five719_dup | 1 | 3 | prosumer
759 | Load_TR5_F5_58 | TR5_five735 | 1 | 4 | prosumer
762 | Load_TR5_F5_59_dup | TR5_five748_dup | 2 | 2 | prosumer
742 | Load_TR5_F5_5_dup | TR5_five108_dup | 2 | 3 | prosumer
765 | Load_TR5_F5_60 | TR5_five750 | 2 | 2 | prosumer
766 | Load_TR5_F5_60_dup | TR5_five750_dup | 2 | 4 | prosumer
768 | Load_TR5_F5_61_dup | TR5_five778_dup | 2 | 3 | prosumer
769 | Load_TR5_F5_62 | TR5_five793 | 1 | 3 | prosumer
770 | Load_TR5_F5_62_dup | TR5_five793_dup | 1 | 2.5 | prosumer
772 | Load_TR5_F5_63_dup | TR5_five799_dup | 3 | 2.5 | prosumer
774 | Load_TR5_F5_64_dup | TR5_five801_dup | 3 | 3 | prosumer
764 | Load_TR5_F5_6_dup | TR5_five117_dup | 2 | 4 | prosumer
783 | Load_TR5_F5_7 | TR5_five118 | 2 | 2 | prosumer
789 | Load_TR5_F6_1 | TR5_six64 | 1 | 2.5 | prosumer
791 | Load_TR5_F6_11 | TR5_six173 | 3 | 3 | prosumer
792 | Load_TR5_F6_12 | TR5_six186 | 1 | 2.5 | prosumer
794 | Load_TR5_F6_14 | TR5_six203 | 1 | 2.5 | prosumer
796 | Load_TR5_F6_16 | TR5_six238 | 1 | 2.5 | prosumer
797 | Load_TR5_F6_17 | TR5_six249 | 2 | 2.5 | prosumer
798 | Load_TR5_F6_18 | TR5_six254 | 2 | 1.5 | prosumer
800 | Load_TR5_F6_2 | TR5_six68 | 3 | 3 | prosumer
802 | Load_TR5_F6_21 | TR5_six317 | 3 | 4 | prosumer
803 | Load_TR5_F6_22 | TR5_six326 | 1 | 1.5 | prosumer
805 | Load_TR5_F6_24 | TR5_six342 | 1 | 4 | prosumer
807 | Load_TR5_F6_26 | TR5_six350 | 2 | 2.5 | prosumer
811 | Load_TR5_F6_3 | TR5_six75 | 1 | 4 | prosumer
812 | Load_TR5_F6_30 | TR5_six385 | 2 | 3.5 | prosumer
813 | Load_TR5_F6_31 | TR5_six387 | 1 | 2.5 | prosumer
814 | Load_TR5_F6_32 | TR5_six392 | 3 | 4 | prosumer
816 | Load_TR5_F6_34 | TR5_six431 | 3 | 1.5 | prosumer
817 | Load_TR5_F6_35 | TR5_six441 | 1 | 2 | prosumer
820 | Load_TR5_F6_38 | TR5_six512 | 2 | 2.5 | prosumer
821 | Load_TR5_F6_39 | TR5_six518 | 2 | 4 | prosumer
823 | Load_TR5_F6_40 | TR5_six523 | 3 | 2 | prosumer
824 | Load_TR5_F6_41 | TR5_six534 | 2 | 2 | prosumer
827 | Load_TR5_F6_44 | TR5_six591 | 3 | 2 | prosumer
828 | Load_TR5_F6_45 | TR5_six595 | 2 | 1.5 | prosumer
830 | Load_TR5_F6_47 | TR5_six643 | 1 | 4 | prosumer
831 | Load_TR5_F6_48 | TR5_six646 | 2 | 4 | prosumer
832 | Load_TR5_F6_49 | TR5_six651 | 3 | 4 | prosumer
833 | Load_TR5_F6_5 | TR5_six87 | 1 | 3 | prosumer
835 | Load_TR5_F6_51 | TR5_six665 | 2 | 4 | prosumer
838 | Load_TR5_F6_54 | TR5_six718 | 3 | 3.5 | prosumer
839 | Load_TR5_F6_55 | TR5_six721 | 1 | 2.5 | prosumer
840 | Load_TR5_F6_56 | TR5_six723 | 2 | 2.5 | prosumer
841 | Load_TR5_F6_57 | TR5_six740 | 1 | 2.5 | prosumer
845 | Load_TR5_F6_60 | TR5_six799 | 2 | 4 | prosumer
847 | Load_TR5_F6_62 | TR5_six807 | 1 | 3 | prosumer
849 | Load_TR5_F6_64 | TR5_six852 | 2 | 3 | prosumer
850 | Load_TR5_F6_65 | TR5_six860 | 3 | 4 | prosumer
852 | Load_TR5_F6_67 | TR5_six885 | 1 | 3 | prosumer
854 | Load_TR5_F6_69 | TR5_six909 | 3 | 3 | prosumer
857 | Load_TR5_F6_71 | TR5_six921 | 2 | 2 | prosumer
858 | Load_TR5_F6_72 | TR5_six929 | 1 | 4 | prosumer
861 | Load_TR5_F6_75 | TR5_six952 | 1 | 2.5 | prosumer
862 | Load_TR5_F6_76 | TR5_six967 | 2 | 4 | prosumer
866 | Load_TR5_F6_8 | TR5_six111 | 3 | 4 | prosumer
867 | Load_TR5_F6_80 | TR5_six1006 | 3 | 3 | prosumer

## 3. Raw PV per load
Raw PV per load
Verbatim copy of PV_generation_kW (TR5_load_PV_48periods.xlsx). One row per connection, 48 half-hours (kW).
Load name | Type | p1 | p2 | p3 | p4 | p5 | p6 | p7 | p8 | p9 | p10 | p11 | p12 | p13 | p14 | p15 | p16 | p17 | p18 | p19 | p20 | p21 | p22 | p23 | p24 | p25 | p26 | p27 | p28 | p29 | p30 | p31 | p32 | p33 | p34 | p35 | p36 | p37 | p38 | p39 | p40 | p41 | p42 | p43 | p44 | p45 | p46 | p47 | p48
Load_TR5_F1_1 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_10 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_10_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_11 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_11_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_12 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_12_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_13 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_13_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_14 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_14_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_15 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_15_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0009 | 0.0124 | 0.0581 | 0.1153 | 0.1855 | 0.262 | 0.3394 | 0.4165 | 0.4937 | 0.5661 | 0.6342 | 0.6921 | 0.7416 | 0.785 | 0.8208 | 0.8462 | 0.8574 | 0.8606 | 0.8546 | 0.8343 | 0.8033 | 0.7664 | 0.7195 | 0.6698 | 0.6099 | 0.5425 | 0.461 | 0.3848 | 0.3065 | 0.2307 | 0.1577 | 0.0921 | 0.0268 | 0.0049 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_16 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_16_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_17 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_17_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_18 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_18_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_19 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_19_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_1_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_2 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_20 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_20_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_21 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_21_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_22 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_22_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_23 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_23_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_24 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_24_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_25 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_25_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_26 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_26_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_27 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_27_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_28 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_28_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_29 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_29_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_2_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_3 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_30 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_30_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_31 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_31_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_32 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_32_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_33 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_33_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_34 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_34_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_35 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_35_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_36 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_36_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_37 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_37_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_38 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_38_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_39 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_39_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_3_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_4 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_40 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_40_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_41 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_41_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_42 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_42_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_43 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_43_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_44 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_44_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_45 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_45_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_46 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_46_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_47 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_47_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_48 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_48_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_49 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_49_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_4_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_5 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_5_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_6 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_6_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_7 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_7_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_8 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_8_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_9 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F1_9_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_1 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_10 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_100 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_11 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_12 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_13 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_14 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_15 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_16 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_17 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_18 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_19 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_2 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_20 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_21 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_22 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_23 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_24 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_25 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_26 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_27 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_28 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_29 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_3 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_30 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_31 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_32 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_33 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_34 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_35 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_36 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_37 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_38 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_39 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_4 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_40 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_41 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_42 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_43 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_44 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_45 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_46 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_47 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_48 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_49 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_5 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_50 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_51 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_52 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_53 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_54 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_55 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_56 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_57 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_58 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_59 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_6 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_60 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_61 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_62 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_63 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_64 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_65 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_66 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_67 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_68 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_69 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_7 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_70 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_71 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_72 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_73 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_74 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_75 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_76 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_77 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_78 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_79 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_8 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_80 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_81 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_82 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_83 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_84 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_85 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_86 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_87 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_88 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_89 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_9 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_90 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_91 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_92 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_93 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_94 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_95 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_96 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_97 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_98 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F4_99 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_1 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_10 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_10_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_11 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_11_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_12 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_12_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_13 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_13_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_14 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_14_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_15 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_15_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_16 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_16_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_17 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_17_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_18 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_18_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_19 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_19_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_1_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_2 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_20 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_20_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_21 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_21_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_22 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_22_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_23 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_23_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_24 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_24_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_25 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_25_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_26 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_26_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_27 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_27_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_28 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_28_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_29 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_29_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_2_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_3 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_30 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_30_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_31 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_31_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_32 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_32_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_33 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_33_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_34 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_34_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_35 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_35_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_36 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_36_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_37 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_37_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_38 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_38_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_39 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_39_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_3_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_4 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_40 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_40_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_41 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_41_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_42 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_42_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_43 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_43_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_44 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_44_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_45 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_45_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_46 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_46_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_47 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_47_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_48 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_48_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_49 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_49_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_4_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_5 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_50 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_50_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_51 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_51_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_52 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_52_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_53 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_53_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_54 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_54_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_55 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_55_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_56 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_56_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_57 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_57_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_58 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_58_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_59 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_59_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_5_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_6 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_60 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_60_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_61 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_61_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_62 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_62_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_63 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_63_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_64 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_64_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_65 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_65_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_66 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_66_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_67 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_67_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_68 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_68_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_6_dup | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_7 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_7_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_8 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_8_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_9 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F5_9_dup | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_1 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_10 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_11 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_12 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_13 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_14 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_15 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_16 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_17 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_18 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_19 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_2 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_20 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_21 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_22 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_23 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_24 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_25 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_26 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_27 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_28 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_29 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_3 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_30 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_31 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_32 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_33 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_34 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_35 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_36 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_37 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_38 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_39 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_4 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_40 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_41 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_42 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_43 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_44 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_45 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013 | 0.0187 | 0.0872 | 0.173 | 0.2782 | 0.393 | 0.5092 | 0.6247 | 0.7405 | 0.8491 | 0.9512 | 1.0382 | 1.1124 | 1.1775 | 1.2312 | 1.2694 | 1.2861 | 1.2909 | 1.2819 | 1.2514 | 1.205 | 1.1496 | 1.0793 | 1.0047 | 0.9148 | 0.8137 | 0.6915 | 0.5772 | 0.4597 | 0.3461 | 0.2365 | 0.1381 | 0.0402 | 0.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_46 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_47 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_48 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_49 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_5 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_50 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_51 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_52 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_53 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_54 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0.0435 | 0.2035 | 0.4037 | 0.6491 | 0.9169 | 1.188 | 1.4577 | 1.7278 | 1.9813 | 2.2196 | 2.4225 | 2.5956 | 2.7475 | 2.8729 | 2.9619 | 3.0009 | 3.0122 | 2.991 | 2.92 | 2.8117 | 2.6823 | 2.5184 | 2.3442 | 2.1346 | 1.8986 | 1.6136 | 1.3468 | 1.0727 | 0.8076 | 0.5519 | 0.3223 | 0.0938 | 0.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_55 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_56 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_57 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_58 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_59 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_6 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_60 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_61 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_62 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_63 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_64 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_65 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_66 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_67 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_68 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_69 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_7 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_70 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_71 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017 | 0.0249 | 0.1163 | 0.2307 | 0.3709 | 0.524 | 0.6789 | 0.833 | 0.9873 | 1.1322 | 1.2683 | 1.3843 | 1.4832 | 1.57 | 1.6417 | 1.6925 | 1.7148 | 1.7212 | 1.7092 | 1.6686 | 1.6067 | 1.5328 | 1.4391 | 1.3396 | 1.2198 | 1.0849 | 0.922 | 0.7696 | 0.613 | 0.4615 | 0.3154 | 0.1842 | 0.0536 | 0.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_72 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_73 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_74 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_75 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022 | 0.0311 | 0.1454 | 0.2883 | 0.4637 | 0.6549 | 0.8486 | 1.0412 | 1.2341 | 1.4152 | 1.5854 | 1.7304 | 1.854 | 1.9625 | 2.0521 | 2.1156 | 2.1435 | 2.1516 | 2.1365 | 2.0857 | 2.0083 | 1.9159 | 1.7989 | 1.6745 | 1.5247 | 1.3561 | 1.1525 | 0.962 | 0.7662 | 0.5768 | 0.3942 | 0.2302 | 0.067 | 0.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_76 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_77 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_78 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_79 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_8 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034 | 0.0497 | 0.2326 | 0.4613 | 0.7419 | 1.0479 | 1.3577 | 1.666 | 1.9746 | 2.2643 | 2.5367 | 2.7686 | 2.9664 | 3.14 | 3.2833 | 3.385 | 3.4296 | 3.4425 | 3.4183 | 3.3372 | 3.2133 | 3.0655 | 2.8782 | 2.6791 | 2.4396 | 2.1698 | 1.8441 | 1.5392 | 1.2259 | 0.9229 | 0.6308 | 0.3683 | 0.1072 | 0.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_80 | prosumer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0.0373 | 0.1744 | 0.346 | 0.5564 | 0.7859 | 1.0183 | 1.2495 | 1.481 | 1.6982 | 1.9025 | 2.0764 | 2.2248 | 2.355 | 2.4625 | 2.5387 | 2.5722 | 2.5819 | 2.5637 | 2.5029 | 2.41 | 2.2991 | 2.1586 | 2.0093 | 1.8297 | 1.6274 | 1.3831 | 1.1544 | 0.9195 | 0.6922 | 0.4731 | 0.2762 | 0.0804 | 0.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_81 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_82 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_83 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_TR5_F6_9 | customer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 4. Raw load per load
Raw load per load
Verbatim copy of Load_P_kW (TR5_load_PV_48periods.xlsx), tagged by type. One row per connection, 48 half-hours (kW).
Load name | Type | p1 | p2 | p3 | p4 | p5 | p6 | p7 | p8 | p9 | p10 | p11 | p12 | p13 | p14 | p15 | p16 | p17 | p18 | p19 | p20 | p21 | p22 | p23 | p24 | p25 | p26 | p27 | p28 | p29 | p30 | p31 | p32 | p33 | p34 | p35 | p36 | p37 | p38 | p39 | p40 | p41 | p42 | p43 | p44 | p45 | p46 | p47 | p48
Load_TR5_F1_1 | prosumer | 0.2355 | 0.052 | 0.1604 | 0.1271 | 0.052 | 0.0937 | 0.1938 | 0.052 | 0.052 | 0.2355 | 0.052 | 0.052 | 0.2272 | 0.0603 | 0.245 | 1.0888 | 0.226 | 0.3653 | 0.3936 | 0.2921 | 0.473 | 0.434 | 0.2129 | 0.6047 | 0.2452 | 2.0194 | 0.5818 | 0.4188 | 0.3091 | 0.1 | 0.3997 | 0.1665 | 0.9459 | 2.1714 | 1.8219 | 0.2806 | 0.3835 | 0.5267 | 0.561 | 0.3291 | 0.0806 | 0.1354 | 0.1521 | 0.052 | 0.3605 | 0.5645 | 0.6776 | 0.6844
Load_TR5_F1_10 | prosumer | 0.758 | 0.6276 | 0.7769 | 0.2312 | 0.2664 | 0.1746 | 0.1344 | 0.2158 | 0.1482 | 0.2665 | 0.0707 | 0.1503 | 0.1745 | 0.1606 | 0.2358 | 0.1997 | 0.0908 | 0.1713 | 1.6537 | 0.3993 | 0.2852 | 0.2294 | 0.4271 | 0.3119 | 1.5015 | 0.266 | 1.319 | 0.4272 | 0.1881 | 0.2232 | 0.2116 | 0.103 | 0.1951 | 0.235 | 0.1281 | 0.1745 | 0.2287 | 0.355 | 0.2729 | 0.474 | 0.2731 | 0.3914 | 0.1678 | 0.052 | 0.6142 | 0.1519 | 0.1658 | 0.2155
Load_TR5_F1_10_dup | prosumer | 0.1706 | 0.1882 | 0.1154 | 0.1154 | 0.1759 | 0.048 | 0.3108 | 0.048 | 0.048 | 0.3108 | 0.048 | 0.1631 | 0.1956 | 0.048 | 0.048 | 0.048 | 0.1399 | 0.0909 | 1.7715 | 0.7763 | 0.1759 | 0.1461 | 0.1551 | 1.0046 | 0.7356 | 1.2214 | 0.1972 | 0.5909 | 1.2306 | 0.4185 | 0.2622 | 0.3783 | 0.1215 | 0.048 | 0.1706 | 0.1882 | 0.1928 | 0.5361 | 0.3973 | 0.4698 | 0.4529 | 0.5694 | 0.1338 | 0.2249 | 0.048 | 0.1828 | 0.0672 | 0.2425
Load_TR5_F1_11 | customer | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.0641 | 0.2546 | 0.294 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.0561 | 0.0649 | 0.0598 | 0.1873 | 0.2812 | 0.2812 | 0.4227 | 0.2999 | 0.3755 | 0.3572 | 1.0994 | 0.3182 | 0.4934 | 0.311 | 0.1325 | 0.325 | 0.0544 | 0.0649 | 0.0635 | 1.2496 | 1.2152 | 2.6869 | 2.8111 | 0.5266 | 0.3656 | 0.4151 | 0.051 | 0.2036 | 0.3702 | 0.051 | 0.051 | 0.051 | 0.051
Load_TR5_F1_11_dup | customer | 0.1972 | 0.051 | 0.0975 | 0.1507 | 0.051 | 0.051 | 0.1972 | 0.051 | 0.1706 | 0.0776 | 0.0709 | 0.1773 | 0.051 | 0.1174 | 0.1307 | 1.4152 | 0.8483 | 0.2132 | 0.0831 | 1.8108 | 0.0644 | 1.1724 | 0.4082 | 0.2748 | 0.2748 | 0.2515 | 0.0842 | 0.1108 | 0.1374 | 0.715 | 0.9264 | 0.2347 | 1.4662 | 0.9256 | 0.2762 | 0.5929 | 0.9281 | 2.2632 | 0.9636 | 0.815 | 0.3145 | 1.2264 | 0.7165 | 0.5151 | 0.2296 | 0.1212 | 0.1144 | 0.1507
Load_TR5_F1_12 | prosumer | 0.2899 | 0.0602 | 0.3614 | 0.039 | 0.1025 | 0.2661 | 0.092 | 0.289 | 0.1326 | 0.088 | 0.0989 | 0.2737 | 0.039 | 0.0836 | 0.2585 | 0.1185 | 0.4194 | 0.2456 | 0.7224 | 0.5236 | 0.2177 | 0.3442 | 0.4102 | 1.2541 | 0.8142 | 0.606 | 0.3093 | 0.5979 | 0.2799 | 0.4289 | 0.2918 | 0.1169 | 0.5903 | 0.2261 | 0.5713 | 0.9097 | 0.1434 | 0.3561 | 0.3366 | 0.4829 | 0.4011 | 0.4444 | 0.6638 | 0.4451 | 0.3604 | 0.2301 | 0.1863 | 0.1364
Load_TR5_F1_12_dup | prosumer | 0.122 | 0.048 | 0.122 | 0.048 | 0.048 | 0.0768 | 0.0932 | 0.048 | 0.122 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.316 | 0.225 | 0.0764 | 0.5118 | 1.306 | 0.3729 | 1.1359 | 0.1101 | 0.0691 | 0.1708 | 0.7349 | 0.5906 | 0.2529 | 0.1075 | 0.3266 | 0.1116 | 0.1028 | 0.1211 | 0.5659 | 1.3082 | 0.9414 | 1.8842 | 0.9342 | 1.1448 | 0.5917 | 0.5434 | 0.58 | 0.5728 | 1.1421 | 0.7017 | 0.5034 | 0.4419 | 0.3884 | 0.1056
Load_TR5_F1_13 | customer | 0.044 | 0.183 | 0.0749 | 0.044 | 0.1135 | 0.1444 | 0.0594 | 0.1985 | 0.044 | 0.0517 | 0.2062 | 0.044 | 0.044 | 0.2139 | 0.044 | 0.1095 | 0.1768 | 0.0826 | 0.05 | 0.1847 | 0.0749 | 0.044 | 0.0517 | 0.2062 | 0.044 | 0.1907 | 0.1572 | 0.1404 | 0.2636 | 0.1979 | 0.1494 | 0.2795 | 0.044 | 0.2139 | 0.0778 | 0.2509 | 0.4005 | 0.044 | 0.2279 | 0.1478 | 0.4657 | 0.4239 | 0.2572 | 0.512 | 0.3218 | 0.4828 | 0.044 | 0.044
Load_TR5_F1_13_dup | prosumer | 0.3803 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.5405 | 2.1166 | 0.1561 | 0.1397 | 0.1464 | 0.1316 | 0.1404 | 0.127 | 0.097 | 0.051 | 0.2688 | 0.0852 | 0.2907 | 0.272 | 0.0888 | 0.09 | 0.0577 | 0.161 | 0.1341 | 0.0767 | 0.1529 | 0.1429 | 0.2573 | 0.547 | 0.3214 | 0.3497 | 0.4519 | 0.5201 | 0.5684 | 0.6572 | 0.7238
Load_TR5_F1_14 | prosumer | 0.056 | 0.2911 | 0.056 | 0.056 | 0.1711 | 0.0899 | 0.1421 | 0.056 | 0.2289 | 0.1182 | 0.1373 | 0.2098 | 0.056 | 0.1421 | 0.1237 | 0.4634 | 1.0527 | 1.3246 | 0.207 | 0.1381 | 0.3002 | 0.1881 | 0.1465 | 0.2209 | 0.1485 | 0.1196 | 1.5255 | 0.056 | 0.1628 | 0.6044 | 0.3416 | 0.298 | 0.702 | 0.5982 | 0.8035 | 1.0931 | 0.056 | 0.2911 | 0.9082 | 0.5387 | 0.8105 | 0.5564 | 0.8802 | 0.7122 | 0.9926 | 0.8564 | 1.1063 | 1.2063
Load_TR5_F1_14_dup | prosumer | 0.1622 | 0.1946 | 0.056 | 0.2618 | 0.095 | 0.1524 | 0.2044 | 0.0863 | 0.2488 | 0.0776 | 0.1394 | 0.2174 | 0.056 | 0.056 | 0.4011 | 0.0788 | 0.1167 | 0.6113 | 0.105 | 0.5137 | 0.2682 | 0.2322 | 0.3002 | 0.3331 | 0.2001 | 0.056 | 0.0776 | 0.1123 | 0.2532 | 0.1036 | 0.1383 | 0.2185 | 0.0776 | 0.1123 | 0.2001 | 0.2588 | 0.8421 | 0.6877 | 0.5445 | 0.6727 | 1.1172 | 0.9799 | 0.1774 | 0.1795 | 0.0788 | 0.2521 | 0.082 | 0.2466
Load_TR5_F1_15 | customer | 0.0638 | 0.1059 | 0.047 | 0.068 | 0.1017 | 0.047 | 0.047 | 0.1143 | 0.0554 | 0.1227 | 0.047 | 0.047 | 0.047 | 0.2145 | 1.3606 | 0.9558 | 0.0998 | 0.0731 | 0.1271 | 0.2825 | 0.1962 | 0.047 | 0.1143 | 0.0554 | 0.0652 | 0.0874 | 0.2563 | 0.0701 | 0.247 | 0.3139 | 1.5973 | 3.0872 | 1.5225 | 0.2828 | 0.1511 | 0.2064 | 0.1545 | 0.2216 | 0.1766 | 0.4659 | 0.3416 | 0.3703 | 0.4644 | 0.4696 | 0.047 | 0.0849 | 0.1873 | 0.1099
Load_TR5_F1_15_dup | prosumer | 0.049 | 0.4001 | 0.0977 | 0.1618 | 0.2258 | 0.1752 | 0.2422 | 0.2395 | 0.186 | 0.2072 | 0.1536 | 0.3387 | 0.049 | 0.2019 | 0.2684 | 0.0765 | 0.3871 | 0.1261 | 0.1374 | 0.2666 | 0.1643 | 0.3274 | 0.4164 | 0.2363 | 0.1019 | 0.3359 | 0.1699 | 0.1615 | 0.3363 | 0.1053 | 0.2018 | 0.1296 | 0.2073 | 0.2904 | 0.1591 | 0.2258 | 0.049 | 0.272 | 0.2258 | 0.1591 | 0.3212 | 0.547 | 0.8375 | 0.7617 | 0.068 | 0.1618 | 0.2259 | 0.1316
Load_TR5_F1_16 | prosumer | 0.2787 | 0.12 | 0.1659 | 0.219 | 0.055 | 0.0966 | 0.2489 | 0.1221 | 0.1451 | 0.193 | 0.1295 | 0.055 | 0.0966 | 0.316 | 0.0827 | 0.2851 | 0.0997 | 0.3121 | 0.2368 | 0.1967 | 0.055 | 0.285 | 0.1881 | 0.1473 | 0.1891 | 0.055 | 0.3653 | 1.5517 | 4.9454 | 2.171 | 0.269 | 0.3513 | 0.0721 | 1.6363 | 0.3492 | 0.3989 | 0.2948 | 0.3162 | 0.4443 | 0.4226 | 0.5684 | 0.4075 | 0.2959 | 0.2862 | 0.0848 | 0.1936 | 0.0848 | 0.3278
Load_TR5_F1_16_dup | customer | 0.2977 | 0.1332 | 0.2092 | 0.2525 | 0.2777 | 0.3914 | 0.4614 | 0.2188 | 0.1436 | 0.1249 | 0.058 | 0.4037 | 0.058 | 0.222 | 0.2195 | 0.0782 | 0.236 | 0.1042 | 0.3553 | 1.2248 | 0.4627 | 1.5451 | 0.8049 | 1.8387 | 0.4864 | 0.1956 | 0.2829 | 0.3623 | 0.1597 | 0.1671 | 0.6532 | 1.0598 | 0.5776 | 1.3372 | 0.3361 | 0.147 | 0.1588 | 0.2544 | 0.1307 | 0.058 | 0.1848 | 0.2769 | 0.058 | 0.0766 | 0.1357 | 0.3075 | 0.1249 | 0.1992
Load_TR5_F1_17 | prosumer | 0.6999 | 0.5983 | 0.7018 | 0.3511 | 0.4858 | 0.3817 | 0.2463 | 0.5324 | 0.05 | 0.1809 | 0.1152 | 0.1465 | 0.2081 | 0.1548 | 0.1614 | 0.3163 | 0.0838 | 0.2279 | 0.2315 | 0.05 | 0.176 | 0.2774 | 0.1858 | 0.2518 | 0.251 | 0.3231 | 0.2335 | 0.1845 | 0.2749 | 0.0696 | 0.2108 | 0.1103 | 0.2388 | 0.1572 | 0.1724 | 0.2862 | 0.1738 | 0.3037 | 0.2819 | 0.5253 | 0.5226 | 0.6585 | 0.481 | 0.6689 | 0.35 | 0.05 | 0.3107 | 0.0574
Load_TR5_F1_17_dup | customer | 0.1521 | 0.0542 | 0.042 | 0.1643 | 0.042 | 0.1643 | 0.042 | 0.1643 | 0.042 | 0.1215 | 0.0848 | 0.0481 | 0.1582 | 0.042 | 0.1643 | 0.3444 | 0.3499 | 0.2969 | 0.0428 | 0.042 | 0.042 | 0.1643 | 0.042 | 0.0603 | 0.1459 | 0.042 | 0.1942 | 0.4478 | 0.0816 | 0.1521 | 0.042 | 0.042 | 0.1276 | 0.0787 | 0.042 | 0.0481 | 0.1582 | 0.042 | 0.1582 | 0.0481 | 0.042 | 0.1643 | 0.042 | 0.1629 | 0.4966 | 1.4533 | 0.5557 | 0.042
Load_TR5_F1_18 | prosumer | 0.1621 | 0.0673 | 0.1215 | 0.108 | 0.047 | 0.047 | 0.1215 | 0.108 | 0.047 | 0.047 | 0.1825 | 0.047 | 0.1825 | 0.047 | 0.1825 | 0.047 | 0.047 | 0.0673 | 0.1621 | 0.0657 | 0.0549 | 0.1617 | 0.1236 | 0.1415 | 0.3367 | 0.2887 | 0.1858 | 0.0538 | 0.1757 | 0.047 | 0.1825 | 0.047 | 0.0717 | 0.7899 | 0.0923 | 0.2917 | 0.3522 | 0.4037 | 0.1673 | 0.047 | 0.1418 | 0.0876 | 0.047 | 0.108 | 0.1215 | 0.0944 | 0.1351 | 0.047
Load_TR5_F1_18_dup | prosumer | 0.1558 | 0.1023 | 0.0777 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.098 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.0523 | 0.1452 | 1.4201 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.2916 | 0.051 | 0.1078 | 0.1499 | 0.2693 | 0.1619 | 0.1447 | 0.5952 | 0.99 | 2.5038 | 0.1978 | 0.4608 | 0.5622 | 0.4485 | 0.3295 | 0.3097 | 0.3377 | 0.1488 | 0.051
Load_TR5_F1_19 | prosumer | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.051 | 0.0892 | 0.4977 | 0.5632 | 0.1865 | 0.1086 | 0.08 | 0.0529 | 0.1615 | 0.432 | 0.2242 | 0.202 | 0.1946 | 0.2017 | 0.2064 | 0.2248 | 0.322 | 0.2242 | 0.222 | 0.1262 | 0.1422 | 0.1098 | 0.1739 | 0.3201 | 0.3601 | 0.6659 | 0.384 | 0.3027 | 0.2622 | 0.4023 | 0.748 | 0.2937
Load_TR5_F1_19_dup | prosumer | 0.1927 | 0.1374 | 0.045 | 0.1949 | 0.2408 | 0.0616 | 0.2534 | 0.1657 | 0.045 | 0.1498 | 0.045 | 0.2859 | 0.1498 | 0.045 | 0.06 | 0.3842 | 1.1953 | 1.2618 | 0.729 | 0.2867 | 0.2423 | 0.1706 | 0.1983 | 0.1431 | 0.1498 | 0.2118 | 0.1191 | 0.1498 | 0.2104 | 0.2253 | 0.045 | 0.2034 | 0.1583 | 0.1567 | 0.2708 | 0.1573 | 0.2034 | 0.1757 | 0.1242 | 0.1883 | 0.1498 | 0.1431 | 0.1878 | 0.1498 | 0.045 | 0.3158 | 0.1199 | 0.1274
Load_TR5_F1_1_dup | customer | 0.044 | 0.0971 | 0.0971 | 0.044 | 0.1931 | 0.3896 | 0.109 | 1.0063 | 0.044 | 0.044 | 0.044 | 0.1502 | 0.044 | 0.044 | 0.1502 | 0.052 | 0.3978 | 0.199 | 0.044 | 0.2377 | 0.2659 | 0.044 | 0.044 | 0.1502 | 0.044 | 0.044 | 0.044 | 0.1502 | 0.044 | 0.044 | 0.1502 | 0.1465 | 0.3788 | 0.6535 | 0.3818 | 0.4669 | 0.3746 | 0.2328 | 0.5205 | 0.6896 | 1.0245 | 0.8402 | 0.2292 | 0.5476 | 0.5544 | 0.5909 | 0.044 | 0.1502
Load_TR5_F1_2 | prosumer | 0.0452 | 0.0848 | 0.1679 | 0.031 | 0.2218 | 0.031 | 0.1212 | 0.046 | 0.0357 | 0.217 | 0.031 | 0.1466 | 0.1062 | 0.1118 | 0.1479 | 0.5411 | 0.1699 | 0.1814 | 1.1648 | 0.2362 | 0.5351 | 0.2229 | 0.1604 | 0.2492 | 0.4375 | 0.1437 | 0.8878 | 0.9841 | 1.7038 | 0.3512 | 0.1321 | 0.294 | 0.1454 | 0.1626 | 0.1363 | 0.031 | 0.031 | 0.2218 | 0.031 | 0.0611 | 0.1062 | 0.1862 | 0.5603 | 0.4993 | 1.6543 | 1.2479 | 1.3114 | 0.0528
Load_TR5_F1_20 | prosumer | 0.1452 | 0.041 | 0.2162 | 0.1175 | 0.1183 | 0.2154 | 0.041 | 0.041 | 0.2441 | 0.0896 | 0.1534 | 0.1803 | 0.041 | 0.041 | 0.1943 | 0.1393 | 0.1439 | 0.2589 | 0.1796 | 0.1773 | 0.3336 | 0.1356 | 0.3539 | 0.1939 | 0.3194 | 0.1988 | 0.1582 | 0.4797 | 0.5003 | 0.1306 | 0.041 | 0.1035 | 0.2407 | 0.0969 | 0.983 | 0.1113 | 0.3279 | 0.2025 | 0.041 | 0.0972 | 0.1393 | 0.1382 | 0.1955 | 0.1382 | 0.2575 | 0.0691 | 0.1173 | 0.1321
Load_TR5_F1_20_dup | customer | 0.6951 | 0.1181 | 0.1246 | 0.1379 | 0.1193 | 0.0959 | 0.1654 | 0.0918 | 0.1785 | 0.0786 | 0.055 | 0.1287 | 0.1654 | 0.1287 | 0.1654 | 0.055 | 0.2468 | 0.1654 | 0.1287 | 0.2283 | 0.573 | 0.3187 | 0.2964 | 0.1873 | 0.4188 | 0.1248 | 0.1007 | 0.4779 | 0.6697 | 0.4855 | 0.3675 | 0.2011 | 0.3861 | 0.2939 | 0.5352 | 0.5567 | 0.0747 | 0.3551 | 0.5732 | 0.6467 | 0.6594 | 0.6272 | 0.1382 | 0.1558 | 0.1973 | 0.1654 | 0.1287 | 0.0944
Load_TR5_F1_21 | prosumer | 0.1668 | 0.2896 | 0.1261 | 0.1748 | 0.2182 | 0.1555 | 0.0644 | 0.1797 | 0.1677 | 0.0996 | 0.2752 | 0.1395 | 0.1221 | 0.2527 | 0.053 | 0.2581 | 0.2032 | 0.053 | 0.3217 | 0.1516 | 0.4329 | 0.2624 | 0.7122 | 0.7566 | 1.1665 | 2.1045 | 0.6858 | 0.5745 | 0.3358 | 0.5615 | 0.2372 | 0.1677 | 0.3076 | 0.9522 | 0.359 | 0.4273 | 0.1622 | 0.1251 | 0.1663 | 0.053 | 0.3217 | 0.053 | 0.1635 | 0.3926 | 0.4829 | 0.6041 | 0.1657 | 0.1441
Load_TR5_F1_21_dup | customer | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.3006 | 0.2847 | 0.2087 | 0.205 | 0.2059 | 0.2879 | 0.3057 | 0.1324 | 0.1438 | 0.2555 | 0.4431 | 0.13 | 0.1743 | 0.3443 | 0.4953 | 0.5251 | 1.1424 | 0.5962 | 0.7185 | 0.5776 | 0.5331 | 1.8481 | 0.3585 | 0.3926 | 0.3864 | 0.339
Load_TR5_F1_22 | prosumer | 0.0961 | 0.1695 | 0.052 | 0.052 | 0.2135 | 0.052 | 0.052 | 0.1254 | 0.1401 | 0.052 | 0.052 | 0.1915 | 0.074 | 0.1475 | 0.1181 | 0.1034 | 0.1621 | 0.052 | 0.1621 | 1.4472 | 0.9506 | 0.2446 | 0.2053 | 0.3391 | 0.2655 | 0.3001 | 0.3408 | 0.3233 | 0.4203 | 0.2282 | 0.3681 | 0.1788 | 0.1289 | 0.1768 | 0.052 | 0.0555 | 0.3483 | 0.2021 | 0.291 | 0.4155 | 0.8597 | 0.7705 | 0.5189 | 0.5491 | 0.5861 | 0.5769 | 0.3658 | 0.052
Load_TR5_F1_22_dup | customer | 0.058 | 0.1267 | 0.0776 | 0.058 | 0.1463 | 0.058 | 0.058 | 0.1022 | 0.1022 | 0.0678 | 0.1365 | 0.058 | 0.1463 | 0.058 | 0.0654 | 1.0992 | 1.1933 | 0.2864 | 0.2032 | 0.2937 | 0.1718 | 0.2595 | 0.3398 | 0.1839 | 0.3416 | 0.2361 | 0.8835 | 0.058 | 0.1365 | 0.0678 | 0.058 | 1.6588 | 0.058 | 0.0874 | 0.1169 | 0.086 | 0.1463 | 0.2148 | 0.2628 | 0.288 | 0.5232 | 0.6548 | 0.473 | 0.2369 | 0.369 | 0.3137 | 0.2683 | 0.3559
Load_TR5_F1_23 | customer | 0.184 | 0.14 | 0.0615 | 0.2625 | 0.055 | 0.1252 | 0.1923 | 0.1317 | 0.055 | 0.2612 | 0.0628 | 0.1857 | 0.2668 | 0.3739 | 0.3134 | 0.218 | 1.6168 | 0.262 | 0.2278 | 0.2918 | 0.2696 | 0.4895 | 0.5717 | 0.8104 | 1.2746 | 0.4101 | 1.3911 | 0.0589 | 0.1334 | 0.4524 | 0.6053 | 0.5149 | 0.3906 | 0.3857 | 0.5421 | 0.1028 | 0.1837 | 0.2713 | 0.3303 | 0.7206 | 1.074 | 0.838 | 1.105 | 0.7647 | 0.9023 | 1.2318 | 0.9515 | 0.1032
Load_TR5_F1_23_dup | prosumer | 0.7328 | 0.055 | 0.055 | 0.2103 | 0.055 | 0.0762 | 0.1891 | 0.055 | 0.055 | 0.1891 | 0.0762 | 0.055 | 0.2103 | 0.055 | 0.1397 | 0.4894 | 0.0825 | 0.2103 | 0.055 | 0.1397 | 0.1293 | 0.3652 | 1.3166 | 0.1825 | 0.3603 | 0.2824 | 1.3561 | 0.2503 | 0.055 | 1.4082 | 0.4507 | 0.055 | 0.3924 | 0.5889 | 0.27 | 0.2222 | 1.6244 | 2.4061 | 0.8453 | 0.1117 | 0.1731 | 1.6949 | 3.506 | 2.3506 | 0.9372 | 0.6114 | 0.5798 | 0.5611
Load_TR5_F1_24 | prosumer | 0.1846 | 0.052 | 0.1382 | 0.0984 | 0.1117 | 0.125 | 0.052 | 0.1581 | 0.0785 | 0.052 | 0.1051 | 0.1316 | 0.0984 | 0.1382 | 0.0866 | 0.1948 | 0.763 | 0.1846 | 0.1172 | 0.3215 | 0.052 | 0.052 | 0.3039 | 0.052 | 0.1316 | 0.1051 | 0.1183 | 0.1183 | 0.0918 | 0.1448 | 0.052 | 0.2949 | 0.2154 | 1.5008 | 0.2367 | 0.3393 | 0.1532 | 0.0852 | 0.1515 | 0.052 | 0.178 | 0.0586 | 0.3263 | 0.3473 | 0.335 | 0.7911 | 0.052 | 0.1051
Load_TR5_F1_24_dup | customer | 0.052 | 0.0552 | 0.2612 | 0.052 | 0.1592 | 0.1734 | 0.094 | 0.1857 | 0.1307 | 0.052 | 0.0875 | 0.0746 | 0.052 | 0.2063 | 0.1101 | 0.2063 | 0.1101 | 1.0975 | 0.1882 | 0.0585 | 0.1643 | 0.0941 | 0.1101 | 0.158 | 0.1318 | 0.1004 | 0.2063 | 0.052 | 0.1916 | 0.1248 | 0.1804 | 0.379 | 1.3817 | 0.3342 | 0.5401 | 0.6942 | 0.4156 | 0.1031 | 0.379 | 0.2581 | 0.617 | 0.618 | 0.4313 | 1.3941 | 0.7858 | 1.0613 | 0.9628 | 0.052
Load_TR5_F1_25 | customer | 0.2277 | 0.1243 | 0.1656 | 0.2047 | 0.0927 | 0.1985 | 0.1444 | 0.1454 | 0.1152 | 0.047 | 0.2502 | 0.0927 | 0.0927 | 0.0836 | 0.047 | 0.2593 | 0.2592 | 0.9445 | 2.7829 | 2.7613 | 0.2763 | 0.11 | 0.135 | 0.2079 | 0.047 | 0.1596 | 0.1833 | 0.079 | 0.1124 | 0.2442 | 0.0836 | 1.0067 | 0.1857 | 0.2508 | 0.114 | 0.3375 | 0.0832 | 0.3343 | 0.5636 | 0.3652 | 0.5152 | 1.5357 | 0.3681 | 0.888 | 0.7643 | 0.7423 | 0.8905 | 0.5542
Load_TR5_F1_25_dup | customer | 0.2338 | 0.051 | 0.2942 | 0.051 | 0.1216 | 0.051 | 0.2668 | 0.0784 | 0.051 | 0.153 | 0.1216 | 0.051 | 0.1412 | 0.204 | 0.051 | 0.255 | 0.0902 | 0.098 | 0.2394 | 2.6012 | 1.3969 | 0.2445 | 0.9139 | 0.6013 | 0.0619 | 0.2237 | 0.051 | 0.1666 | 0.0966 | 0.2489 | 0.1522 | 0.18 | 0.2012 | 0.051 | 0.0981 | 0.2472 | 0.0745 | 0.098 | 0.0908 | 0.729 | 0.4399 | 2.4673 | 0.9931 | 0.8134 | 0.751 | 0.3876 | 0.5335 | 0.425
Load_TR5_F1_26 | customer | 0.1637 | 0.0781 | 0.1623 | 0.043 | 0.1974 | 0.043 | 0.043 | 0.043 | 0.0711 | 0.1694 | 0.043 | 0.1623 | 0.0781 | 0.043 | 0.1974 | 0.043 | 0.043 | 0.0781 | 0.1623 | 0.043 | 0.1974 | 0.043 | 0.1062 | 0.1343 | 0.0608 | 0.2026 | 0.1372 | 0.0458 | 0.1439 | 1.1537 | 0.99 | 0.7154 | 0.8472 | 0.1679 | 1.5339 | 0.227 | 0.0559 | 0.1062 | 0.1913 | 0.1283 | 0.2876 | 0.3685 | 0.1879 | 0.1632 | 0.3802 | 0.1527 | 0.1623 | 0.0781
Load_TR5_F1_26_dup | prosumer | 0.3889 | 0.036 | 0.0658 | 0.2803 | 0.036 | 0.251 | 0.0951 | 0.1451 | 0.1936 | 0.0433 | 0.2075 | 0.1385 | 0.1763 | 0.1404 | 0.1652 | 0.346 | 0.177 | 0.2036 | 0.0681 | 0.2729 | 0.0438 | 0.6498 | 0.5867 | 0.1841 | 0.1884 | 0.1853 | 0.036 | 0.4786 | 1.071 | 0.0416 | 0.1755 | 0.5927 | 0.4823 | 0.1572 | 0.4115 | 0.1955 | 0.4435 | 0.4027 | 0.9073 | 0.5598 | 0.4798 | 0.4657 | 0.6704 | 0.4797 | 0.7998 | 0.5376 | 0.3218 | 0.4944
Load_TR5_F1_27 | customer | 0.3355 | 0.03 | 0.2352 | 0.1303 | 0.03 | 0.2765 | 0.089 | 0.106 | 0.2594 | 0.03 | 0.2804 | 0.0851 | 0.1126 | 0.2529 | 0.1008 | 0.188 | 0.1244 | 0.18 | 0.2235 | 0.1676 | 0.2859 | 0.0554 | 0.4946 | 0.1009 | 1.28 | 0.6405 | 0.136 | 0.2261 | 0.3831 | 0.2857 | 0.1736 | 0.4428 | 0.0831 | 0.2742 | 0.233 | 0.1294 | 0.1589 | 0.2132 | 0.0373 | 0.0897 | 0.2302 | 0.478 | 0.3043 | 0.5559 | 0.5468 | 0.0811 | 0.2018 | 0.1126
Load_TR5_F1_27_dup | customer | 0.2333 | 0.039 | 0.039 | 0.2605 | 0.0481 | 0.1115 | 0.1598 | 0.1397 | 0.039 | 0.1643 | 0.1352 | 0.039 | 0.1815 | 0.118 | 0.0481 | 0.1242 | 0.1662 | 0.0979 | 0.2016 | 0.0843 | 0.2854 | 0.2661 | 0.1894 | 0.6597 | 1.181 | 0.1388 | 0.1607 | 0.0934 | 0.1679 | 0.1587 | 0.039 | 0.1433 | 0.1659 | 0.168 | 0.1903 | 0.2389 | 0.1311 | 0.039 | 0.1498 | 0.1498 | 0.0798 | 0.1815 | 0.0772 | 0.1524 | 0.4818 | 0.2669 | 0.3303 | 0.1669
Load_TR5_F1_28 | prosumer | 0.051 | 0.4264 | 0.402 | 0.347 | 0.051 | 0.1084 | 0.1514 | 0.0582 | 0.2016 | 0.051 | 0.051 | 0.1944 | 0.0653 | 0.051 | 0.1657 | 0.1298 | 0.0804 | 0.4554 | 1.2735 | 0.623 | 0.2781 | 0.1889 | 0.3027 | 0.1012 | 0.2227 | 0.3186 | 0.2013 | 0.5976 | 0.051 | 0.051 | 0.3491 | 0.051 | 0.8446 | 1.0398 | 0.4196 | 0.2601 | 0.051 | 0.051 | 0.1514 | 0.1084 | 0.051 | 0.2088 | 0.051 | 0.1801 | 0.0797 | 0.1299 | 0.1299 | 0.051
Load_TR5_F1_28_dup | prosumer | 0.0828 | 0.3005 | 0.1203 | 0.1861 | 0.2644 | 0.053 | 0.3975 | 0.053 | 0.2986 | 0.1519 | 0.1125 | 0.1736 | 0.2174 | 0.192 | 0.1618 | 0.285 | 1.0412 | 0.4504 | 0.3785 | 0.5039 | 1.8385 | 0.3031 | 0.5089 | 0.4949 | 0.187 | 0.3336 | 0.2526 | 0.6256 | 0.2402 | 0.2999 | 0.3324 | 0.368 | 0.2463 | 0.392 | 0.3135 | 1.2219 | 0.5563 | 0.431 | 0.7192 | 0.5783 | 0.8724 | 0.8356 | 2.3937 | 1.1209 | 0.7088 | 0.3251 | 0.6898 | 1.4503
Load_TR5_F1_29 | prosumer | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.0525 | 2.016 | 1.9701 | 0.8798 | 0.046 | 0.046 | 0.5628 | 0.1847 | 0.3667 | 0.2386 | 0.2599 | 0.2534 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.0732 | 0.6827 | 1.4867 | 1.7548 | 0.1454 | 0.2021 | 0.2986 | 0.3227 | 0.3572 | 0.2727 | 0.3063 | 0.3269 | 0.3309 | 0.2719
Load_TR5_F1_29_dup | prosumer | 0.1423 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.2771 | 0.9332 | 0.6475 | 1.6374 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.0546 | 0.049 | 0.049 | 0.3074 | 0.2842 | 1.5805 | 0.2101 | 1.2582 | 0.8357 | 0.719 | 1.6428 | 0.2927 | 0.0605 | 0.0682 | 0.1691 | 0.1932 | 0.169 | 0.282 | 0.2293 | 0.049 | 0.049 | 0.049 | 0.049
Load_TR5_F1_2_dup | customer | 0.24 | 0.1051 | 0.1162 | 0.2351 | 0.0806 | 0.2063 | 0.0925 | 0.1383 | 0.2137 | 0.1557 | 0.1575 | 0.2314 | 0.0675 | 0.4457 | 0.155 | 0.2006 | 0.1127 | 0.1274 | 0.2245 | 0.1663 | 0.2607 | 0.1475 | 0.2412 | 0.1713 | 0.1274 | 0.3109 | 0.1006 | 0.4876 | 0.2211 | 0.1995 | 0.1241 | 0.2642 | 0.1481 | 0.1764 | 0.1575 | 0.1503 | 0.2435 | 0.4251 | 0.2682 | 0.5424 | 0.7282 | 0.7043 | 1.4914 | 0.4221 | 0.6774 | 0.5308 | 0.0998 | 0.291
Load_TR5_F1_3 | prosumer | 0.6041 | 0.4777 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.0967 | 0.4063 | 0.1012 | 0.1653 | 0.2773 | 0.3935 | 0.1885 | 0.0639 | 0.0559 | 0.1099 | 0.1234 | 0.058 | 0.1665 | 0.0956 | 0.131 | 0.2195 | 0.266 | 0.4829 | 0.3242 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.1323 | 0.3962 | 0.5761 | 0.7449 | 1.0218
Load_TR5_F1_30 | prosumer | 0.1144 | 0.053 | 0.1553 | 0.1007 | 0.0735 | 0.1826 | 0.053 | 0.1826 | 0.0735 | 0.053 | 0.1962 | 0.0598 | 0.1417 | 0.1144 | 0.0541 | 0.3865 | 1.5645 | 1.6284 | 0.9545 | 0.486 | 0.9845 | 0.9277 | 0.3469 | 0.3184 | 1.5284 | 0.8684 | 0.9896 | 0.7306 | 0.1395 | 0.1395 | 0.2365 | 0.2998 | 0.4525 | 0.5663 | 1.9813 | 0.6236 | 0.2627 | 1.6272 | 0.4333 | 0.5375 | 0.479 | 0.6916 | 0.4893 | 0.5414 | 0.3509 | 0.6293 | 0.4389 | 0.053
Load_TR5_F1_30_dup | prosumer | 0.0845 | 0.1982 | 0.1287 | 0.0616 | 0.0712 | 0.1191 | 0.0808 | 1.1053 | 0.052 | 0.2763 | 0.0926 | 0.1461 | 0.2228 | 0.076 | 0.2929 | 0.0616 | 0.5678 | 0.2903 | 0.1734 | 0.1874 | 0.1911 | 0.1047 | 0.2111 | 0.1578 | 0.1928 | 0.4333 | 0.36 | 0.7057 | 0.7308 | 0.839 | 0.805 | 0.1496 | 0.1383 | 0.2306 | 0.2096 | 0.3717 | 0.0909 | 0.0634 | 0.3485 | 0.4179 | 0.2974 | 0.2682 | 0.052 | 0.3536 | 1.0553 | 0.6836 | 0.1738 | 0.2728
Load_TR5_F1_31 | customer | 0.2913 | 0.1639 | 0.1054 | 0.2354 | 0.0507 | 0.1556 | 0.1785 | 0.1634 | 0.0563 | 0.2131 | 0.1277 | 0.0786 | 0.2689 | 0.044 | 1.2127 | 0.192 | 0.118 | 0.3454 | 0.1165 | 0.128 | 0.4899 | 0.7212 | 0.1447 | 0.2028 | 0.044 | 0.118 | 0.118 | 0.4513 | 0.3702 | 0.1897 | 0.1221 | 0.2254 | 0.044 | 0.0775 | 0.1221 | 0.1314 | 0.6778 | 0.0526 | 0.3341 | 0.2589 | 0.5138 | 0.4047 | 0.4028 | 0.6705 | 0.044 | 0.044 | 0.1919 | 0.1556
Load_TR5_F1_31_dup | prosumer | 2.0271 | 1.2574 | 0.6104 | 0.06 | 0.13 | 0.06 | 0.13 | 0.06 | 0.06 | 0.13 | 0.06 | 0.095 | 0.095 | 0.0989 | 0.0911 | 0.06 | 0.095 | 0.095 | 0.1183 | 0.0717 | 0.0794 | 0.1105 | 0.0872 | 0.1028 | 0.06 | 0.06 | 0.13 | 0.06 | 0.06 | 0.06 | 0.2667 | 0.6446 | 2.0459 | 0.7705 | 0.0853 | 0.2753 | 0.4176 | 0.5043 | 1.3708 | 1.3785 | 1.6999 | 1.2519 | 1.1478 | 0.5731 | 0.9915 | 0.095 | 0.06 | 0.13
Load_TR5_F1_32 | customer | 0.048 | 0.0924 | 0.1304 | 0.048 | 0.1747 | 0.048 | 0.1367 | 0.086 | 0.1367 | 0.086 | 0.048 | 0.048 | 0.067 | 0.1557 | 0.9676 | 0.1747 | 0.048 | 0.2005 | 0.048 | 0.091 | 0.277 | 0.1557 | 0.048 | 0.1747 | 0.6058 | 0.2467 | 0.4461 | 0.233 | 0.5724 | 0.3604 | 0.048 | 0.1747 | 0.048 | 0.048 | 0.3037 | 0.2736 | 0.2772 | 0.1621 | 0.0607 | 0.1379 | 0.3199 | 0.3103 | 0.2277 | 0.3807 | 0.3754 | 0.4142 | 0.048 | 0.048
Load_TR5_F1_32_dup | prosumer | 0.3471 | 0.2733 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.2663 | 0.044 | 0.0931 | 0.3009 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.0615 | 0.2307 | 0.236 | 0.1818 | 0.4674 | 0.3596 | 0.3306 | 0.269 | 0.5863
Load_TR5_F1_33 | prosumer | 0.5102 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.0799 | 0.0643 | 0.056 | 0.056 | 0.056 | 0.0686 | 0.1312 | 0.123 | 0.056 | 0.1296 | 1.0819 | 0.0646 | 0.1655 | 0.0657 | 0.0621 | 0.076 | 0.056 | 0.056 | 0.2531 | 0.1122 | 0.2102 | 0.2995 | 0.0714 | 0.1981 | 0.2599 | 0.6699 | 0.9721 | 0.3589 | 0.4434 | 0.7124 | 0.4994 | 2.2346 | 0.5222 | 0.5257 | 0.4342 | 0.3977
Load_TR5_F1_33_dup | customer | 0.1601 | 0.051 | 0.051 | 0.1409 | 0.1024 | 0.0894 | 0.1531 | 0.1345 | 0.051 | 0.1024 | 0.1409 | 0.051 | 0.1088 | 0.1345 | 0.0574 | 0.1858 | 1.3861 | 1.1272 | 0.8272 | 0.1024 | 1.0378 | 0.4506 | 1.5144 | 1.3072 | 0.7698 | 0.2705 | 0.2362 | 0.1922 | 0.051 | 0.1152 | 0.128 | 0.051 | 0.3986 | 0.2209 | 0.173 | 1.2588 | 0.051 | 0.051 | 0.1601 | 0.0831 | 0.1216 | 0.1216 | 0.3255 | 0.3417 | 0.5548 | 0.6603 | 0.5308 | 0.4311
Load_TR5_F1_34 | prosumer | 0.1528 | 0.1901 | 0.051 | 0.2476 | 0.0954 | 0.051 | 0.2187 | 0.1242 | 0.051 | 0.0803 | 0.2361 | 0.0776 | 0.051 | 0.1169 | 0.1462 | 0.0656 | 0.4483 | 0.1131 | 0.1169 | 0.1462 | 0.1382 | 0.2048 | 0.1309 | 0.1535 | 0.9911 | 0.9146 | 1.534 | 0.4236 | 0.2702 | 0.2589 | 0.2234 | 0.1989 | 0.264 | 0.3709 | 0.1121 | 0.1828 | 0.1309 | 0.051 | 0.1242 | 0.2187 | 0.051 | 0.051 | 0.2536 | 0.2318 | 0.1417 | 0.264 | 0.9862 | 0.1744
Load_TR5_F1_34_dup | prosumer | 0.1304 | 0.096 | 0.1661 | 0.081 | 0.2015 | 0.1377 | 0.0887 | 0.2081 | 0.0848 | 0.1976 | 0.1185 | 0.108 | 0.0728 | 0.2425 | 0.089 | 0.054 | 0.1801 | 0.0914 | 0.3283 | 0.054 | 0.1195 | 0.198 | 0.1422 | 0.1826 | 0.2257 | 0.1119 | 0.2558 | 0.0617 | 0.2659 | 0.0656 | 0.0848 | 0.0925 | 0.2081 | 0.0771 | 0.1077 | 0.2288 | 0.1589 | 0.0627 | 0.2081 | 0.108 | 0.2025 | 0.1503 | 0.1198 | 0.3066 | 0.8204 | 0.6346 | 0.1797 | 0.1715
Load_TR5_F1_35 | prosumer | 0.5915 | 0.3745 | 0.4484 | 0.207 | 0.1702 | 0.0636 | 0.3541 | 0.2626 | 0.269 | 0.2289 | 0.2686 | 0.2648 | 0.2661 | 0.2529 | 0.3069 | 0.1288 | 0.718 | 0.9403 | 1.3476 | 0.5447 | 0.3232 | 0.6133 | 0.3959 | 0.4299 | 0.2492 | 0.2986 | 0.1577 | 0.2454 | 0.3635 | 0.0993 | 0.3713 | 0.2367 | 0.1791 | 0.2451 | 1.5217 | 1.2629 | 1.2367 | 0.3663 | 0.3687 | 0.4167 | 0.7188 | 0.4132 | 0.2566 | 0.2274 | 0.2091 | 0.2439 | 0.0727 | 0.4523
Load_TR5_F1_35_dup | prosumer | 0.051 | 0.183 | 0.051 | 0.051 | 0.117 | 0.117 | 0.075 | 0.159 | 0.051 | 0.051 | 0.183 | 0.051 | 0.075 | 0.2441 | 0.059 | 0.1706 | 0.3283 | 0.091 | 0.183 | 0.0782 | 0.205 | 0.097 | 0.105 | 0.129 | 0.7201 | 1.0765 | 1.7123 | 0.135 | 0.099 | 0.0898 | 0.211 | 1.0226 | 0.273 | 0.1647 | 0.375 | 0.1545 | 0.317 | 0.2055 | 0.2988 | 0.3377 | 0.4685 | 0.4584 | 0.3753 | 0.423 | 0.2075 | 0.147 | 0.087 | 0.051
Load_TR5_F1_36 | customer | 0.1989 | 0.1303 | 0.1044 | 0.2247 | 0.053 | 0.1733 | 0.1558 | 0.053 | 0.278 | 0.0731 | 0.2221 | 0.1298 | 0.103 | 0.053 | 0.1929 | 0.5735 | 0.6314 | 1.1819 | 1.1535 | 3.3692 | 0.1172 | 0.1412 | 0.1879 | 0.1348 | 0.1493 | 0.1298 | 0.103 | 0.2216 | 0.1075 | 0.1517 | 0.4183 | 0.0656 | 0.2332 | 1.1138 | 0.1927 | 0.053 | 0.2534 | 0.0757 | 0.2247 | 0.3849 | 0.5666 | 0.5426 | 0.4281 | 0.768 | 0.4039 | 0.4995 | 0.2156 | 0.1044
Load_TR5_F1_36_dup | customer | 0.1507 | 0.1704 | 0.172 | 0.1225 | 0.1622 | 0.2326 | 0.0806 | 0.3142 | 0.085 | 0.2787 | 0.1312 | 0.148 | 0.2618 | 0.055 | 0.1669 | 0.1679 | 0.2993 | 0.3775 | 0.3908 | 0.2893 | 0.413 | 0.2782 | 0.3258 | 0.2531 | 0.4924 | 0.9133 | 0.8595 | 0.5097 | 0.2288 | 0.1515 | 0.3362 | 0.102 | 1.2301 | 0.4141 | 0.6375 | 0.2257 | 0.4954 | 0.5625 | 0.7363 | 1.0162 | 0.9119 | 0.7043 | 0.6906 | 0.7608 | 1.018 | 0.5556 | 0.5392 | 0.3999
Load_TR5_F1_37 | customer | 0.1291 | 0.1276 | 0.1276 | 0.0998 | 0.2354 | 0.049 | 0.2506 | 0.0846 | 0.1524 | 0.1828 | 0.049 | 0.2468 | 0.0825 | 0.1552 | 0.4013 | 0.051 | 0.2423 | 0.4396 | 0.3202 | 0.208 | 0.3643 | 2.0818 | 3.0903 | 3.8191 | 0.2899 | 0.543 | 0.2207 | 0.4353 | 0.3969 | 0.4174 | 0.1905 | 0.5038 | 0.2894 | 0.5923 | 1.6549 | 2.9331 | 2.8048 | 0.5459 | 0.3604 | 0.5657 | 0.8815 | 0.3509 | 0.6689 | 0.7241 | 0.7315 | 1.1945 | 0.8301 | 0.8539
Load_TR5_F1_37_dup | prosumer | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.0532 | 0.0595 | 0.053 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.1353 | 0.2197 | 0.4123 | 1.1481 | 0.1499 | 0.3171 | 0.049 | 0.0751 | 0.1171 | 0.187 | 0.602 | 0.4376 | 0.5025 | 0.411 | 0.5308 | 0.4038 | 0.2963 | 0.049 | 0.049
Load_TR5_F1_38 | prosumer | 0.6841 | 0.042 | 0.1755 | 1.1465 | 0.0573 | 0.1945 | 0.042 | 0.2098 | 0.042 | 0.0878 | 0.164 | 0.042 | 0.1259 | 0.1259 | 0.042 | 0.1437 | 0.3136 | 1.5229 | 3.9419 | 1.8629 | 0.7235 | 1.7822 | 0.5827 | 1.2677 | 3.3366 | 3.3049 | 0.3946 | 0.1406 | 0.2754 | 0.4439 | 0.0947 | 0.4038 | 1.5654 | 0.6596 | 0.4342 | 1.4636 | 0.5049 | 0.897 | 1.5531 | 0.4858 | 0.626 | 0.6328 | 0.9222 | 0.8603 | 0.5259 | 0.7311 | 0.4982 | 0.1411
Load_TR5_F1_38_dup | prosumer | 0.1333 | 0.055 | 0.0724 | 0.1159 | 0.055 | 0.1333 | 0.055 | 0.055 | 0.1333 | 0.055 | 0.055 | 0.055 | 0.0942 | 0.1382 | 0.055 | 0.0855 | 0.1029 | 0.0724 | 0.1159 | 0.055 | 0.0637 | 0.1246 | 0.055 | 0.1203 | 0.0681 | 0.055 | 0.055 | 0.055 | 0.1333 | 0.0637 | 0.1246 | 0.0811 | 0.1072 | 0.055 | 0.055 | 0.055 | 0.055 | 0.059 | 0.2811 | 0.3592 | 0.2424 | 0.3613 | 0.306 | 0.4816 | 0.055 | 0.055 | 0.1333 | 0.055
Load_TR5_F1_39 | customer | 0.4504 | 0.8277 | 0.3266 | 0.1017 | 0.1755 | 0.2468 | 0.0832 | 0.1786 | 0.0907 | 0.3316 | 0.056 | 0.2912 | 0.1311 | 0.0701 | 0.5827 | 0.3275 | 0.2775 | 0.5213 | 0.3053 | 1.1494 | 0.379 | 0.1157 | 0.1965 | 0.2257 | 0.056 | 0.2569 | 0.1654 | 0.328 | 1.6611 | 0.1787 | 0.3045 | 0.2387 | 0.0607 | 0.2282 | 0.1976 | 0.1157 | 0.138 | 0.2843 | 0.056 | 0.2616 | 0.1607 | 0.056 | 0.303 | 0.056 | 0.2177 | 0.2046 | 0.056 | 0.15
Load_TR5_F1_39_dup | customer | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.152 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.0636 | 0.4703 | 0.7173 | 1.5514 | 1.1889 | 0.057 | 1.0733 | 1.423 | 0.057 | 0.066 | 0.057 | 0.5247 | 0.0698 | 0.1112 | 0.6944 | 0.4288 | 0.069 | 0.0708 | 0.063 | 0.0718 | 0.0896 | 0.1365 | 0.1814 | 0.2534 | 0.1172 | 0.2839 | 0.3384 | 0.057 | 0.057 | 0.057
Load_TR5_F1_3_dup | customer | 0.2002 | 0.144 | 0.058 | 0.058 | 0.1201 | 0.0819 | 0.058 | 0.144 | 0.058 | 0.058 | 0.058 | 0.058 | 0.144 | 0.058 | 0.1201 | 0.3609 | 0.1448 | 0.0913 | 0.1072 | 0.1058 | 0.058 | 0.058 | 0.144 | 0.058 | 0.0914 | 0.1106 | 0.058 | 0.058 | 0.144 | 0.058 | 0.0867 | 0.1153 | 0.0676 | 0.1344 | 0.0697 | 0.1174 | 0.0978 | 0.1176 | 1.5884 | 0.4717 | 0.3775 | 0.3866 | 0.4334 | 0.2613 | 0.101 | 0.058 | 0.058 | 0.0771
Load_TR5_F1_4 | customer | 0.052 | 0.1318 | 0.052 | 0.052 | 0.052 | 0.052 | 0.1185 | 0.0653 | 0.114 | 0.0697 | 0.052 | 0.052 | 0.1318 | 0.052 | 0.052 | 0.1318 | 0.052 | 0.1318 | 0.052 | 0.1318 | 0.052 | 0.0875 | 0.0963 | 0.052 | 0.052 | 0.1318 | 0.052 | 0.1318 | 0.052 | 0.1318 | 0.1059 | 0.2139 | 0.0963 | 0.0875 | 0.052 | 0.0919 | 0.0919 | 0.052 | 0.1318 | 0.052 | 0.052 | 0.052 | 0.0919 | 0.0919 | 0.0564 | 0.1273 | 0.052 | 0.1318
Load_TR5_F1_40 | prosumer | 0.2612 | 0.0887 | 0.0841 | 0.1025 | 0.0753 | 0.1997 | 0.1346 | 0.052 | 0.223 | 0.052 | 0.2046 | 0.1531 | 0.052 | 0.223 | 0.052 | 0.052 | 0.223 | 1.5374 | 1.0583 | 1.6796 | 0.4897 | 0.3853 | 0.2528 | 0.6096 | 1.6211 | 1.2582 | 1.1136 | 0.4685 | 0.3496 | 0.4558 | 0.2916 | 0.319 | 0.1175 | 0.0621 | 0.2183 | 0.9479 | 1.3586 | 0.6168 | 0.5448 | 0.4976 | 0.4117 | 0.5686 | 0.5498 | 0.6104 | 0.547 | 0.4828 | 0.052 | 0.2153
Load_TR5_F1_40_dup | prosumer | 0.1302 | 0.2348 | 0.1105 | 0.1502 | 0.0978 | 0.0782 | 0.2999 | 0.052 | 0.3 | 0.078 | 0.104 | 0.274 | 0.052 | 0.1827 | 0.1953 | 0.0585 | 0.3195 | 0.052 | 0.052 | 0.2606 | 0.1175 | 0.4408 | 0.2047 | 0.0643 | 0.2752 | 0.3046 | 0.2744 | 0.2063 | 0.3179 | 0.1763 | 0.2649 | 0.2088 | 0.0782 | 0.2346 | 0.1435 | 0.052 | 0.326 | 0.052 | 0.2505 | 0.2088 | 0.052 | 0.2999 | 0.0782 | 0.2082 | 0.1698 | 0.052 | 0.196 | 0.182
Load_TR5_F1_41 | customer | 0.1012 | 0.059 | 0.059 | 0.1749 | 0.059 | 0.1539 | 0.0801 | 0.059 | 0.1749 | 0.059 | 0.0643 | 0.1697 | 0.059 | 0.0801 | 0.1539 | 0.059 | 0.5437 | 0.6522 | 0.1577 | 0.059 | 0.1903 | 0.2404 | 0.0979 | 0.1644 | 0.059 | 0.0643 | 0.1697 | 0.059 | 0.1749 | 0.059 | 0.1328 | 0.1012 | 0.059 | 0.138 | 0.4502 | 1.8377 | 1.4449 | 0.401 | 0.1757 | 0.1588 | 0.3177 | 1.1583 | 0.359 | 0.1661 | 0.1275 | 0.1064 | 0.059 | 0.1012
Load_TR5_F1_41_dup | customer | 0.2435 | 0.1346 | 0.1854 | 0.13 | 0.1674 | 0.2277 | 0.0924 | 0.2231 | 0.1346 | 0.1228 | 0.1728 | 0.1246 | 0.0927 | 0.2178 | 0.1097 | 0.2207 | 0.1296 | 0.1076 | 0.1979 | 0.1296 | 0.2605 | 0.1047 | 0.1629 | 0.2024 | 0.055 | 0.055 | 0.168 | 0.1973 | 0.1002 | 0.1755 | 0.1746 | 0.1584 | 0.1604 | 0.1152 | 0.1401 | 0.2251 | 0.0756 | 0.3808 | 0.1895 | 0.3846 | 0.2207 | 0.06 | 0.2073 | 0.1529 | 0.1445 | 0.2207 | 0.055 | 0.0927
Load_TR5_F1_42 | prosumer | 0.1215 | 0.3431 | 0.049 | 0.0856 | 0.2766 | 0.049 | 0.2372 | 0.1249 | 0.0937 | 0.0775 | 0.1441 | 0.218 | 0.049 | 0.2177 | 0.2403 | 0.2604 | 0.4375 | 0.2915 | 0.2322 | 0.2064 | 0.5212 | 0.4022 | 0.5971 | 0.5654 | 0.556 | 0.3323 | 0.0734 | 0.2166 | 0.2162 | 0.2894 | 0.2895 | 1.0522 | 0.183 | 0.5128 | 0.2384 | 0.2484 | 0.3668 | 0.2496 | 0.4172 | 0.3824 | 0.4541 | 0.5373 | 0.5812 | 0.8393 | 0.4813 | 0.3707 | 0.4313 | 0.1098
Load_TR5_F1_42_dup | customer | 0.3401 | 0.048 | 0.3417 | 0.1155 | 0.1304 | 0.3268 | 0.048 | 0.2293 | 0.1593 | 0.2299 | 0.2849 | 0.1229 | 0.2893 | 0.1679 | 0.0892 | 0.2931 | 0.048 | 0.2689 | 0.1495 | 0.3059 | 0.3016 | 0.2922 | 0.1395 | 0.2577 | 0.1354 | 0.2534 | 0.6062 | 1.8694 | 2.97 | 2.5697 | 0.098 | 0.6365 | 1.781 | 0.641 | 0.4051 | 0.0577 | 0.4119 | 0.1304 | 0.0893 | 0.4529 | 0.4841 | 0.6337 | 0.4791 | 0.5695 | 0.815 | 0.2994 | 0.3223 | 0.1984
Load_TR5_F1_43 | customer | 0.2407 | 0.0515 | 0.1553 | 0.032 | 0.045 | 0.1618 | 0.032 | 0.032 | 0.1099 | 0.0969 | 0.032 | 0.1748 | 0.032 | 0.045 | 0.1902 | 0.1326 | 0.3237 | 0.1177 | 0.3585 | 0.3317 | 0.108 | 0.052 | 0.1748 | 0.032 | 0.1099 | 0.0969 | 0.0645 | 0.1424 | 0.032 | 0.1683 | 0.0385 | 0.0446 | 0.6723 | 0.2481 | 0.5358 | 0.075 | 0.0877 | 0.1731 | 0.1575 | 1.761 | 1.303 | 0.7325 | 0.0969 | 0.1099 | 0.032 | 0.1748 | 0.032 | 0.0774
Load_TR5_F1_43_dup | customer | 0.1457 | 0.1652 | 0.091 | 0.2199 | 0.05 | 0.1745 | 0.1364 | 0.05 | 0.261 | 0.05 | 0.2278 | 0.0831 | 0.05 | 0.261 | 0.05 | 0.1634 | 0.4102 | 0.8739 | 0.2294 | 0.1184 | 0.1652 | 0.1457 | 0.05 | 0.2541 | 0.0568 | 0.0637 | 0.2473 | 0.05 | 0.1457 | 0.1307 | 0.1393 | 0.091 | 0.3849 | 1.7713 | 0.1876 | 0.1128 | 0.5027 | 1.2823 | 1.566 | 0.2458 | 0.1652 | 0.0637 | 0.1321 | 0.05 | 0.0846 | 0.2264 | 0.0615 | 0.2494
Load_TR5_F1_44 | customer | 0.2633 | 0.1011 | 0.1969 | 0.1674 | 0.046 | 0.1341 | 0.1786 | 0.0976 | 0.1544 | 0.21 | 0.046 | 0.1562 | 0.164 | 0.1233 | 0.1231 | 0.2248 | 0.068 | 0.171 | 0.3985 | 0.1011 | 0.2801 | 0.3212 | 0.1343 | 0.061 | 1.1349 | 1.4962 | 0.4798 | 0.4055 | 0.2054 | 0.2747 | 0.3837 | 0.1872 | 0.3199 | 0.2888 | 0.5064 | 0.2186 | 0.1472 | 0.2281 | 0.2867 | 0.1635 | 0.105 | 0.1492 | 0.1176 | 0.0846 | 0.2082 | 0.1817 | 0.2341 | 0.4464
Load_TR5_F1_44_dup | customer | 0.2615 | 0.1453 | 0.1845 | 0.2355 | 0.203 | 0.171 | 0.2916 | 0.053 | 0.2013 | 0.2786 | 0.053 | 0.2998 | 0.1181 | 0.1128 | 0.3671 | 0.0928 | 0.146 | 0.391 | 0.3426 | 0.0739 | 0.3881 | 1.9036 | 0.9134 | 0.648 | 0.1426 | 0.0943 | 0.3524 | 0.0862 | 0.2013 | 0.2786 | 0.0702 | 0.2443 | 0.1055 | 0.3174 | 0.1426 | 0.2525 | 0.2274 | 0.1669 | 0.313 | 0.053 | 0.2478 | 0.053 | 0.3118 | 0.1061 | 0.1913 | 0.6354 | 0.5581 | 0.3928
Load_TR5_F1_45 | customer | 0.1567 | 0.1153 | 0.085 | 0.1864 | 0.1153 | 0.1276 | 0.2082 | 0.051 | 0.051 | 0.8154 | 0.182 | 0.051 | 0.2082 | 0.051 | 0.2419 | 0.0939 | 0.0581 | 0.2649 | 0.3714 | 0.4128 | 0.2885 | 0.4313 | 1.2908 | 1.4749 | 0.5477 | 0.2046 | 1.7778 | 1.2717 | 0.344 | 0.2016 | 0.1591 | 0.051 | 0.3552 | 0.4088 | 0.1555 | 0.0777 | 0.2438 | 0.0866 | 0.5036 | 0.5111 | 0.3863 | 1.0942 | 0.853 | 0.6364 | 0.8508 | 0.3273 | 1.5761 | 0.624
Load_TR5_F1_45_dup | customer | 0.029 | 0.0874 | 0.0407 | 0.0485 | 0.0796 | 0.029 | 0.029 | 0.0757 | 0.0523 | 0.029 | 0.099 | 0.029 | 0.099 | 0.029 | 0.0881 | 0.0619 | 0.0651 | 0.1104 | 1.3678 | 0.2823 | 1.4858 | 0.3209 | 0.029 | 0.7676 | 0.6405 | 0.8802 | 1.1558 | 1.1272 | 0.9902 | 0.099 | 0.252 | 0.1342 | 0.029 | 0.2458 | 0.3066 | 0.808 | 0.6179 | 1.7028 | 0.1977 | 0.23 | 0.3198 | 0.2501 | 0.2333 | 0.4451 | 0.2102 | 0.0562 | 0.0718 | 0.0757
Load_TR5_F1_46 | prosumer | 0.0828 | 0.2447 | 0.198 | 0.2374 | 0.2351 | 0.1423 | 0.2385 | 0.1446 | 0.2019 | 0.2706 | 0.053 | 0.2306 | 0.1134 | 0.2533 | 0.2192 | 0.053 | 0.2953 | 1.466 | 0.6042 | 0.4713 | 0.1383 | 0.1272 | 0.2228 | 2.1385 | 1.3627 | 0.5646 | 0.4529 | 0.3873 | 1.4349 | 0.5601 | 0.4666 | 0.3839 | 0.4178 | 0.644 | 0.9666 | 0.2606 | 0.2238 | 0.2889 | 0.1738 | 0.2893 | 0.4693 | 0.3239 | 0.2333 | 0.1814 | 0.1149 | 0.2868 | 0.053 | 0.053
Load_TR5_F1_46_dup | prosumer | 0.1391 | 0.0698 | 0.055 | 0.1292 | 0.0797 | 0.1243 | 0.0847 | 0.0748 | 0.1342 | 0.055 | 0.055 | 0.055 | 0.055 | 0.154 | 0.055 | 0.154 | 0.055 | 0.0698 | 0.1549 | 0.0809 | 0.1506 | 0.3023 | 0.1334 | 0.0995 | 0.055 | 0.149 | 0.0599 | 0.0748 | 0.1342 | 0.055 | 0.154 | 0.055 | 0.1328 | 0.0797 | 0.055 | 0.055 | 0.1843 | 0.3363 | 0.7531 | 0.5459 | 0.4085 | 0.5276 | 0.6763 | 0.8884 | 1.4786 | 0.9512 | 0.2299 | 0.0698
Load_TR5_F1_47 | prosumer | 0.1906 | 0.1569 | 0.041 | 0.2571 | 0.041 | 0.041 | 0.2571 | 0.041 | 0.0837 | 0.1643 | 0.091 | 0.1691 | 0.1289 | 0.041 | 0.1855 | 0.1125 | 0.417 | 0.4713 | 0.317 | 0.7688 | 0.5579 | 0.1128 | 0.2025 | 0.147 | 0.269 | 0.3098 | 0.0624 | 0.5622 | 0.2379 | 0.3072 | 0.1749 | 0.2212 | 0.3976 | 0.2677 | 1.54 | 0.8935 | 0.3006 | 0.2074 | 0.2812 | 0.7091 | 0.6645 | 0.5613 | 0.502 | 0.3732 | 0.5405 | 0.6082 | 2.0001 | 0.849
Load_TR5_F1_47_dup | prosumer | 0.059 | 0.059 | 0.2356 | 0.059 | 0.1955 | 0.0991 | 0.1312 | 0.1634 | 0.059 | 0.1473 | 0.1473 | 0.059 | 0.2356 | 0.059 | 0.2035 | 0.0911 | 0.2527 | 0.3011 | 0.3088 | 0.0991 | 0.1393 | 0.1553 | 0.059 | 0.1232 | 0.1714 | 0.059 | 0.3034 | 0.2797 | 0.2644 | 0.2441 | 0.1245 | 0.1293 | 0.1874 | 0.059 | 0.0751 | 0.2196 | 0.059 | 0.059 | 0.0792 | 0.5997 | 0.4783 | 0.5831 | 0.7136 | 0.4828 | 0.6819 | 0.7289 | 0.2031 | 0.067
Load_TR5_F1_48 | prosumer | 0.3966 | 0.048 | 0.2254 | 0.048 | 0.177 | 0.0964 | 0.048 | 0.048 | 0.2012 | 0.0722 | 0.0722 | 0.2012 | 0.048 | 0.2381 | 0.0561 | 1.1458 | 0.173 | 0.0831 | 1.5637 | 1.092 | 0.8784 | 0.1642 | 0.0577 | 0.2699 | 1.4787 | 1.3972 | 0.5871 | 0.1129 | 0.2628 | 0.0818 | 0.3137 | 0.1177 | 0.1212 | 0.3283 | 0.1177 | 0.2373 | 0.4648 | 0.2968 | 0.49 | 0.4245 | 0.1448 | 0.3338 | 0.4466 | 0.844 | 0.5972 | 0.5222 | 0.7211 | 1.2859
Load_TR5_F1_48_dup | customer | 0.2116 | 0.1155 | 0.052 | 0.198 | 0.1292 | 0.1621 | 0.1651 | 0.0906 | 0.2275 | 0.0611 | 0.2003 | 0.1269 | 0.052 | 0.1337 | 0.1133 | 0.2183 | 0.1061 | 0.2086 | 0.1414 | 0.2603 | 0.5509 | 0.6033 | 1.7647 | 0.2211 | 1.3299 | 0.3311 | 0.1714 | 0.3125 | 0.218 | 0.1337 | 0.1356 | 0.1099 | 0.1549 | 0.1723 | 0.0974 | 0.2298 | 0.2053 | 0.2068 | 0.2664 | 0.4388 | 0.5269 | 0.3782 | 0.3096 | 0.2578 | 0.4539 | 0.342 | 0.3836 | 0.0649
Load_TR5_F1_49 | customer | 0.5271 | 0.3924 | 0.052 | 0.1241 | 0.052 | 0.1241 | 0.052 | 0.052 | 0.1241 | 0.052 | 0.088 | 0.088 | 0.1001 | 0.076 | 0.1179 | 0.06 | 0.052 | 0.1443 | 0.072 | 0.2195 | 0.9678 | 0.2438 | 1.2209 | 0.052 | 0.052 | 0.0794 | 0.1152 | 0.1042 | 0.2232 | 0.2285 | 0.2163 | 0.1881 | 0.2584 | 0.1605 | 1.0138 | 0.2468 | 0.1744 | 0.1033 | 0.4723 | 0.134 | 0.052 | 0.052 | 0.1081 | 0.068 | 0.281 | 0.3245 | 0.3463 | 0.2095
Load_TR5_F1_49_dup | prosumer | 0.0654 | 0.0916 | 0.2736 | 0.045 | 0.2848 | 0.0804 | 0.1234 | 0.0786 | 0.2139 | 0.1513 | 0.0747 | 0.1786 | 0.1066 | 0.2216 | 0.0821 | 0.2163 | 0.1489 | 0.1899 | 0.2042 | 0.1995 | 0.045 | 0.045 | 0.2208 | 0.1178 | 0.2029 | 0.1606 | 0.1463 | 0.2698 | 0.0553 | 0.3671 | 0.4948 | 0.1885 | 0.0506 | 0.2533 | 0.1119 | 0.0842 | 0.2662 | 0.0598 | 0.1833 | 0.2635 | 0.3514 | 0.4239 | 0.4415 | 0.4478 | 0.2084 | 0.112 | 0.179 | 0.1863
Load_TR5_F1_4_dup | prosumer | 0.049 | 0.1236 | 0.0904 | 0.049 | 0.1651 | 0.049 | 0.0656 | 0.1485 | 0.049 | 0.1153 | 0.0987 | 0.049 | 0.1933 | 0.0904 | 0.049 | 0.1651 | 0.049 | 0.049 | 0.1651 | 0.049 | 0.0904 | 0.1236 | 0.049 | 0.0822 | 0.168 | 0.1807 | 1.9156 | 4.0634 | 3.9635 | 1.215 | 0.1324 | 0.0886 | 0.1699 | 0.0886 | 0.2117 | 0.083 | 0.1242 | 0.0685 | 0.0878 | 0.3478 | 0.5764 | 0.4253 | 0.4389 | 0.287 | 0.049 | 0.049 | 0.049 | 0.1568
Load_TR5_F1_5 | prosumer | 0.7991 | 0.3182 | 0.2632 | 0.201 | 0.0892 | 0.2655 | 0.1595 | 0.1936 | 0.05 | 0.3032 | 0.1609 | 0.1131 | 0.3511 | 0.05 | 0.3877 | 0.173 | 0.1802 | 0.4399 | 0.4383 | 0.3602 | 3.3494 | 3.5355 | 0.9457 | 0.2805 | 0.3966 | 0.3196 | 0.134 | 0.2858 | 0.1783 | 0.109 | 0.2763 | 0.3002 | 0.2233 | 0.196 | 0.9557 | 1.874 | 0.4749 | 1.2022 | 0.2256 | 0.3007 | 0.2734 | 0.2615 | 0.5913 | 0.1326 | 0.1493 | 0.2928 | 0.0996 | 0.1936
Load_TR5_F1_5_dup | prosumer | 0.048 | 0.0977 | 0.135 | 0.0604 | 0.1723 | 0.048 | 0.1536 | 0.0791 | 0.1164 | 0.1164 | 0.048 | 0.048 | 0.1785 | 1.1422 | 0.9261 | 1.7886 | 0.9431 | 0.172 | 0.211 | 0.4106 | 0.048 | 0.048 | 0.0977 | 0.135 | 0.048 | 0.1847 | 0.048 | 0.1164 | 0.1164 | 0.048 | 0.0853 | 0.4263 | 0.0673 | 0.2575 | 0.1948 | 0.3023 | 0.3193 | 0.2013 | 0.2121 | 0.4092 | 0.3351 | 0.4645 | 0.6314 | 0.3764 | 0.3423 | 0.27 | 0.2639 | 0.3699
Load_TR5_F1_6 | prosumer | 0.258 | 0.0583 | 0.2362 | 0.0801 | 0.0762 | 0.2401 | 0.044 | 0.1978 | 0.1185 | 0.1531 | 0.1632 | 0.044 | 0.2723 | 0.044 | 0.2469 | 0.0693 | 0.044 | 0.1853 | 0.149 | 0.0793 | 0.4058 | 0.0996 | 0.1462 | 0.1557 | 0.9155 | 0.1147 | 0.486 | 0.0887 | 0.1456 | 0.1706 | 0.044 | 0.2508 | 0.0655 | 0.1769 | 0.1394 | 0.3897 | 0.2232 | 0.0926 | 0.2816 | 0.2115 | 0.0977 | 0.1963 | 0.1307 | 0.044 | 0.2633 | 0.044 | 0.044 | 0.2723
Load_TR5_F1_6_dup | customer | 0.1728 | 0.1251 | 0.055 | 0.2036 | 0.1204 | 0.055 | 0.199 | 0.055 | 0.199 | 0.1251 | 0.1335 | 0.1827 | 0.0628 | 0.199 | 0.0589 | 0.1433 | 1.02 | 0.2928 | 0.2601 | 0.0772 | 0.205 | 0.0565 | 0.1933 | 0.1409 | 0.1499 | 0.338 | 0.1067 | 0.3042 | 0.3662 | 0.364 | 0.2023 | 0.384 | 0.3808 | 0.3776 | 0.2259 | 1.3143 | 0.3038 | 0.1262 | 0.5049 | 0.5403 | 0.6729 | 0.6086 | 0.5623 | 0.4768 | 0.6972 | 0.4268 | 0.0877 | 0.3795
Load_TR5_F1_7 | prosumer | 0.051 | 0.1074 | 0.0972 | 0.0766 | 0.128 | 0.051 | 0.051 | 0.051 | 0.4186 | 0.4288 | 0.3839 | 0.2471 | 0.0972 | 0.1074 | 0.092 | 0.2637 | 2.6756 | 0.3543 | 0.9258 | 2.55 | 2.6526 | 0.1343 | 0.051 | 0.2043 | 0.2002 | 0.8036 | 1.6783 | 0.9432 | 0.813 | 0.2173 | 0.2744 | 0.0612 | 0.1539 | 0.4633 | 1.4048 | 2.7428 | 2.4486 | 0.2002 | 0.3458 | 0.3635 | 0.5881 | 0.8014 | 0.556 | 0.5941 | 0.4396 | 0.5006 | 0.8619 | 0.9223
Load_TR5_F1_7_dup | customer | 0.2337 | 0.1909 | 0.1489 | 0.0991 | 0.1155 | 0.1976 | 0.2568 | 0.05 | 0.05 | 0.2455 | 0.2089 | 0.05 | 0.2568 | 0.1305 | 0.2316 | 0.11 | 0.3528 | 0.1687 | 0.2328 | 0.1847 | 0.0869 | 0.1708 | 0.1326 | 0.164 | 0.1073 | 0.3001 | 0.097 | 0.1422 | 0.1236 | 0.1278 | 0.343 | 0.1645 | 0.1007 | 0.3772 | 0.2448 | 0.3433 | 0.3241 | 0.3341 | 0.4225 | 0.3039 | 0.5482 | 0.6948 | 0.5142 | 0.4091 | 0.2508 | 0.4073 | 0.1802 | 0.14
Load_TR5_F1_8 | prosumer | 0.1021 | 0.0765 | 0.051 | 0.051 | 0.051 | 0.1191 | 0.0595 | 0.051 | 0.1276 | 0.051 | 0.0851 | 0.0936 | 0.051 | 0.051 | 0.1063 | 0.9506 | 3.7008 | 2.1565 | 0.1336 | 0.8791 | 0.1704 | 0.3164 | 0.4135 | 0.2164 | 0.148 | 0.1665 | 0.221 | 0.3259 | 0.6539 | 1.3671 | 0.183 | 0.1235 | 0.1376 | 0.3636 | 0.2477 | 1.6964 | 1.9953 | 0.4034 | 0.1688 | 0.4239 | 0.3667 | 0.5587 | 0.7773 | 0.5141 | 0.7033 | 0.8149 | 0.6299 | 0.3412
Load_TR5_F1_8_dup | customer | 0.048 | 0.195 | 0.048 | 0.048 | 0.175 | 0.068 | 0.1349 | 0.1081 | 0.048 | 0.175 | 0.068 | 0.1282 | 0.1148 | 0.048 | 0.2365 | 0.0591 | 0.9735 | 0.7847 | 0.4849 | 0.9601 | 0.2027 | 0.2099 | 0.0547 | 0.1883 | 0.048 | 0.048 | 0.195 | 0.048 | 0.1081 | 0.1349 | 0.048 | 0.195 | 0.048 | 0.1616 | 0.14 | 0.0881 | 0.1549 | 0.048 | 0.048 | 0.0747 | 0.1683 | 0.048 | 0.195 | 0.048 | 0.048 | 0.195 | 0.048 | 0.048
Load_TR5_F1_9 | prosumer | 0.1478 | 0.1019 | 0.2355 | 0.0953 | 0.2088 | 0.1706 | 0.048 | 0.0642 | 0.3152 | 0.048 | 0.2579 | 0.1215 | 0.048 | 0.153 | 0.2264 | 0.1425 | 0.1882 | 0.1807 | 0.142 | 0.2269 | 0.1659 | 0.3339 | 0.1215 | 0.1615 | 0.1129 | 0.1774 | 0.202 | 0.048 | 0.1858 | 0.1936 | 0.048 | 0.1649 | 0.2145 | 0.048 | 0.3314 | 0.052 | 1.554 | 0.9349 | 0.308 | 0.3652 | 0.6464 | 0.2952 | 0.4262 | 0.6245 | 0.5171 | 0.7581 | 0.3536 | 0.2079
Load_TR5_F1_9_dup | customer | 0.2041 | 0.0516 | 0.044 | 0.2117 | 0.044 | 0.1584 | 0.0974 | 0.044 | 0.0974 | 0.1636 | 0.044 | 0.2117 | 0.044 | 0.0669 | 0.1889 | 0.044 | 0.1507 | 0.105 | 0.0453 | 0.1126 | 0.1431 | 0.044 | 0.2117 | 0.044 | 0.1889 | 0.0669 | 0.044 | 0.2041 | 0.078 | 0.1584 | 0.0974 | 0.044 | 0.1202 | 0.1555 | 0.0502 | 0.2881 | 0.1162 | 0.2566 | 0.1627 | 0.3488 | 0.3327 | 0.3155 | 0.3923 | 0.3337 | 0.5652 | 0.5351 | 0.508 | 0.4985
Load_TR5_F4_1 | customer | 0.054 | 0.1363 | 0.054 | 0.054 | 0.054 | 0.1134 | 0.0769 | 0.054 | 0.1363 | 0.054 | 0.1363 | 0.054 | 0.1363 | 0.054 | 0.0586 | 0.1317 | 0.054 | 0.142 | 0.054 | 0.1363 | 0.054 | 0.1089 | 0.2131 | 0.6667 | 0.6497 | 0.6032 | 0.3758 | 1.0353 | 0.3792 | 0.3198 | 0.2253 | 0.2515 | 0.1872 | 0.0769 | 0.1134 | 0.054 | 0.054 | 0.0964 | 0.1836 | 0.2242 | 0.7454 | 1.4284 | 1.57 | 0.1541 | 0.054 | 0.054 | 0.0814 | 0.1089
Load_TR5_F4_10 | customer | 0.0669 | 0.0988 | 0.047 | 0.047 | 0.047 | 0.1028 | 0.0629 | 0.0828 | 0.0828 | 0.047 | 0.1187 | 0.047 | 0.1187 | 0.047 | 0.0828 | 0.0828 | 0.047 | 0.3877 | 0.4484 | 0.4059 | 0.1032 | 0.9693 | 0.1147 | 0.047 | 0.047 | 0.047 | 0.1187 | 0.047 | 0.0924 | 0.0904 | 0.2487 | 0.1139 | 0.1226 | 0.8594 | 0.6317 | 0.2995 | 0.3067 | 0.2301 | 0.0799 | 0.6736 | 1.9048 | 0.6113 | 0.2666 | 0.4106 | 0.3129 | 0.1607 | 0.1187 | 0.047
Load_TR5_F4_100 | prosumer | 0.055 | 0.1705 | 0.089 | 0.1297 | 0.1297 | 0.055 | 0.1161 | 0.1433 | 0.055 | 0.2044 | 0.055 | 0.055 | 0.1908 | 0.0686 | 0.3947 | 0.1941 | 0.089 | 0.1705 | 0.0611 | 0.5856 | 0.1365 | 0.0686 | 0.1908 | 0.055 | 0.055 | 0.055 | 0.2044 | 0.055 | 0.055 | 0.2044 | 0.055 | 0.055 | 0.1161 | 0.5131 | 0.9945 | 0.6442 | 0.5896 | 0.352 | 0.4263 | 0.8857 | 1.3344 | 1.611 | 0.4013 | 0.5798 | 0.3508 | 0.7732 | 0.4494 | 0.2853
Load_TR5_F4_11 | customer | 0.7858 | 0.5869 | 0.054 | 0.0873 | 0.204 | 0.054 | 0.2373 | 0.054 | 0.079 | 0.2123 | 0.054 | 0.2373 | 0.054 | 0.054 | 0.601 | 0.2231 | 0.4158 | 0.508 | 0.1052 | 0.054 | 0.179 | 0.1123 | 0.054 | 0.2373 | 0.054 | 0.0957 | 0.2533 | 0.2369 | 0.154 | 0.2493 | 1.1139 | 0.6231 | 0.3419 | 0.3698 | 0.1767 | 0.162 | 0.3254 | 0.2003 | 0.1605 | 0.5599 | 0.464 | 0.4968 | 0.699 | 0.646 | 0.7486 | 0.8089 | 0.3026 | 0.228
Load_TR5_F4_12 | prosumer | 0.939 | 0.8032 | 0.7648 | 0.768 | 0.2341 | 0.054 | 0.0622 | 0.2259 | 0.054 | 0.2259 | 0.0622 | 0.1031 | 0.185 | 0.054 | 0.2341 | 0.054 | 0.2238 | 0.1113 | 0.054 | 0.2341 | 0.054 | 0.2014 | 0.0867 | 0.1277 | 0.1604 | 0.186 | 0.652 | 2.257 | 0.4371 | 0.4202 | 0.5784 | 0.3529 | 0.2959 | 0.3025 | 0.174 | 0.217 | 0.3918 | 0.1927 | 0.2401 | 0.5368 | 0.8139 | 0.6806 | 0.6944 | 0.6325 | 0.58 | 0.5673 | 0.4065 | 0.185
Load_TR5_F4_13 | customer | 0.1368 | 0.197 | 0.1315 | 0.1253 | 0.214 | 0.1005 | 0.3244 | 0.1095 | 0.2114 | 0.0934 | 0.2388 | 0.0614 | 0.3999 | 0.055 | 0.2855 | 0.1757 | 0.2352 | 0.1035 | 0.1776 | 0.2133 | 0.106 | 0.2544 | 0.4778 | 0.3487 | 1.2603 | 0.2916 | 0.1506 | 0.1385 | 0.2346 | 0.0978 | 0.8029 | 0.2136 | 0.3379 | 0.2686 | 0.535 | 0.4214 | 0.5376 | 0.759 | 1.3593 | 1.6134 | 0.2847 | 0.6262 | 0.5446 | 0.5743 | 0.2411 | 0.0937 | 0.2643 | 0.055
Load_TR5_F4_14 | prosumer | 0.5326 | 0.4626 | 0.0933 | 0.2348 | 0.048 | 0.1199 | 0.2082 | 0.048 | 0.2382 | 0.206 | 0.118 | 0.1024 | 0.1557 | 0.048 | 0.2183 | 0.1097 | 0.0584 | 0.2892 | 0.0891 | 0.1652 | 0.1629 | 0.1221 | 0.1557 | 0.0983 | 0.0933 | 0.0768 | 0.1598 | 0.1682 | 0.0695 | 0.2379 | 0.0806 | 0.5004 | 0.1322 | 0.048 | 0.1508 | 0.1773 | 0.1221 | 0.206 | 0.1221 | 0.1557 | 0.0983 | 0.0645 | 0.2492 | 0.3124 | 0.5749 | 0.2328 | 0.048 | 0.2266
Load_TR5_F4_15 | prosumer | 0.059 | 0.1145 | 0.2695 | 0.0745 | 0.059 | 0.059 | 0.2906 | 0.1089 | 0.1034 | 0.1256 | 0.059 | 0.059 | 0.3328 | 0.0668 | 0.201 | 0.2486 | 0.2089 | 0.5018 | 0.3218 | 0.318 | 0.9994 | 0.1515 | 0.2949 | 0.1598 | 0.1089 | 0.1433 | 0.2063 | 0.1644 | 0.0645 | 0.1732 | 0.2264 | 0.059 | 0.2296 | 0.1699 | 0.0823 | 2.1504 | 1.7166 | 1.0376 | 0.5035 | 0.4854 | 0.5082 | 0.4437 | 0.4704 | 0.6192 | 0.6116 | 0.7538 | 0.7302 | 0.14
Load_TR5_F4_16 | prosumer | 0.7939 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.109 | 1.7501 | 0.555 | 0.1984 | 0.2096 | 0.2131 | 0.2018 | 0.4004 | 0.1991 | 1.3974 | 1.101 | 0.7099 | 0.1262 | 0.1026 | 0.2956 | 0.1644 | 0.084 | 0.0583 | 0.078 | 0.2233 | 0.1999 | 0.2088 | 0.4803 | 0.3475 | 0.4249 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
Load_TR5_F4_17 | prosumer | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.152 | 0.2685 | 0.073 | 0.1127 | 0.166 | 0.3207 | 1.2309 | 0.4035 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.2725 | 0.048 | 0.048 | 0.1496 | 0.1438 | 0.1018 | 0.3566 | 0.4857 | 0.2268 | 0.3622 | 0.3157 | 0.4097 | 0.407 | 0.566 | 0.5608 | 0.5317 | 0.7213 | 0.5175 | 0.4638 | 0.6262 | 0.6296 | 0.601
Load_TR5_F4_18 | prosumer | 0.2334 | 0.3141 | 0.06 | 0.2559 | 0.143 | 0.1746 | 0.2947 | 0.0977 | 0.2311 | 0.2759 | 0.1681 | 0.2332 | 0.2737 | 0.1781 | 0.201 | 1.424 | 0.2497 | 0.167 | 0.3906 | 0.627 | 1.0312 | 1.2344 | 0.5372 | 0.1996 | 0.2066 | 0.3159 | 0.2835 | 0.4451 | 0.4459 | 0.4082 | 0.3773 | 0.5148 | 0.6512 | 1.5358 | 0.2754 | 0.5667 | 1.0938 | 1.3624 | 0.3572 | 0.4671 | 1.4783 | 0.3912 | 0.572 | 0.7005 | 0.3235 | 0.5222 | 0.3006 | 0.2288
Load_TR5_F4_19 | customer | 0.053 | 0.053 | 0.1233 | 0.0909 | 0.0909 | 0.1233 | 0.0855 | 0.1287 | 0.0638 | 0.1504 | 0.1974 | 0.3666 | 0.053 | 0.053 | 0.0928 | 0.1652 | 0.1686 | 0.053 | 0.1017 | 0.1125 | 0.0801 | 0.1837 | 0.0682 | 0.1612 | 0.053 | 0.1612 | 0.053 | 0.1504 | 0.0638 | 0.1504 | 0.0638 | 0.1092 | 0.2453 | 0.1231 | 0.0588 | 0.053 | 0.1612 | 0.1797 | 1.6573 | 0.6479 | 0.5389 | 0.4696 | 0.5206 | 0.3291 | 0.2217 | 0.1017 | 0.1017 | 0.1125
Load_TR5_F4_2 | prosumer | 2.9335 | 1.6401 | 0.141 | 0.049 | 0.2078 | 0.1143 | 0.0773 | 0.1764 | 0.7969 | 0.6295 | 0.245 | 0.049 | 0.2048 | 0.049 | 0.1269 | 0.3123 | 0.0604 | 0.2048 | 0.1173 | 0.1127 | 0.141 | 0.1173 | 0.049 | 0.1173 | 0.2878 | 0.3387 | 0.399 | 0.4045 | 0.2847 | 0.2496 | 0.2945 | 0.089 | 0.2375 | 0.3103 | 0.2041 | 0.6377 | 0.3278 | 0.3567 | 0.3819 | 0.4658 | 0.5042 | 0.5401 | 1.128 | 0.6397 | 0.5606 | 0.7066 | 0.4859 | 0.2165
Load_TR5_F4_20 | prosumer | 0.249 | 0.0761 | 0.2142 | 0.1167 | 0.196 | 0.1238 | 0.0724 | 0.0977 | 0.2295 | 0.0614 | 0.0909 | 0.2364 | 0.076 | 0.1056 | 0.2142 | 0.054 | 0.1019 | 0.3227 | 0.2204 | 0.2334 | 0.1891 | 0.372 | 0.2426 | 0.2875 | 0.3566 | 0.4615 | 0.0852 | 0.1203 | 0.5008 | 0.2385 | 0.1426 | 0.3734 | 0.2803 | 0.3049 | 0.2326 | 0.0641 | 0.1713 | 0.1717 | 0.1231 | 0.5982 | 0.5191 | 0.5977 | 0.5743 | 0.51 | 0.5327 | 0.6257 | 1.4823 | 0.3129
Load_TR5_F4_21 | prosumer | 0.4621 | 0.5326 | 0.216 | 0.1757 | 0.1185 | 0.0957 | 0.1772 | 0.1025 | 0.1144 | 0.206 | 0.055 | 0.156 | 0.0728 | 0.2009 | 0.1195 | 0.1466 | 0.1738 | 0.1466 | 0.06 | 0.2603 | 0.0601 | 0.0703 | 0.1313 | 0.156 | 0.0728 | 0.7281 | 0.9978 | 0.4152 | 0.1531 | 0.1151 | 0.261 | 0.1426 | 0.0927 | 1.1943 | 1.2834 | 2.8018 | 2.4707 | 0.2535 | 0.0669 | 0.1466 | 0.055 | 0.212 | 0.1085 | 0.1466 | 0.1738 | 0.055 | 0.2179 | 0.1025
Load_TR5_F4_22 | customer | 0.4092 | 0.4689 | 0.2745 | 0.0825 | 0.056 | 0.056 | 0.056 | 0.056 | 0.1621 | 0.056 | 0.056 | 0.056 | 0.0931 | 0.1249 | 1.1265 | 0.2981 | 0.3939 | 0.2389 | 0.3099 | 0.2129 | 0.2857 | 0.4314 | 0.1946 | 1.1244 | 0.2046 | 0.1699 | 0.0669 | 0.4543 | 0.2532 | 0.4601 | 0.5225 | 0.1864 | 0.2249 | 0.3084 | 0.3099 | 0.5262 | 0.4812 | 0.4458 | 0.3986 | 0.5641 | 0.9553 | 0.8125 | 0.5739 | 0.388 | 0.056 | 0.1621 | 0.056 | 0.1621
Load_TR5_F4_23 | customer | 0.7049 | 0.9701 | 1.0225 | 0.3353 | 0.1325 | 0.0845 | 0.2461 | 0.0882 | 0.0736 | 0.2169 | 0.1137 | 0.071 | 0.1939 | 0.048 | 0.2169 | 0.1137 | 0.1785 | 0.1521 | 0.0557 | 0.2092 | 0.048 | 0.2596 | 0.071 | 0.1401 | 0.429 | 0.263 | 0.385 | 0.2886 | 0.2152 | 2.2526 | 0.6063 | 0.1602 | 0.4749 | 0.5446 | 0.2724 | 0.3464 | 0.3643 | 0.4836 | 0.3406 | 0.6645 | 0.7353 | 1.3967 | 0.8031 | 1.1132 | 0.5928 | 0.7787 | 0.6981 | 0.7621
Load_TR5_F4_24 | prosumer | 0.3001 | 0.052 | 0.052 | 0.1919 | 0.1602 | 0.1087 | 0.0946 | 0.1399 | 0.1129 | 0.0794 | 0.2727 | 0.052 | 0.1513 | 0.1467 | 0.1061 | 0.1638 | 0.2204 | 0.5232 | 0.9055 | 0.2152 | 0.1403 | 0.1599 | 0.2575 | 0.9897 | 0.5953 | 0.1639 | 0.2976 | 0.25 | 0.9784 | 0.2008 | 0.2069 | 0.1425 | 0.2857 | 0.1312 | 0.2322 | 0.4236 | 0.237 | 0.2421 | 0.2125 | 0.4928 | 0.3938 | 0.5219 | 0.4457 | 2.0184 | 0.1513 | 0.1467 | 0.1061 | 0.6616
Load_TR5_F4_25 | customer | 0.047 | 0.0715 | 0.2021 | 0.047 | 0.1695 | 0.1042 | 0.0797 | 0.194 | 0.047 | 0.096 | 0.1776 | 0.047 | 0.2185 | 0.0552 | 0.047 | 0.194 | 0.0797 | 0.047 | 0.1695 | 0.1042 | 1.1978 | 0.1295 | 0.2215 | 0.047 | 0.047 | 0.0552 | 0.2185 | 0.047 | 0.2266 | 0.047 | 0.1368 | 0.1368 | 0.047 | 0.1776 | 0.096 | 0.047 | 0.096 | 0.1813 | 0.2961 | 0.3475 | 0.2992 | 0.3623 | 0.4825 | 0.4101 | 0.2706 | 0.6937 | 0.4656 | 0.3333
Load_TR5_F4_26 | prosumer | 0.246 | 0.1434 | 0.056 | 0.3713 | 0.0938 | 0.2014 | 0.2637 | 0.056 | 0.2268 | 0.2214 | 0.0728 | 0.1771 | 0.2502 | 0.1631 | 0.1079 | 0.305 | 0.1561 | 0.1935 | 0.7992 | 1.0302 | 1.2653 | 0.5029 | 0.507 | 0.4493 | 0.5137 | 1.2999 | 2.7737 | 2.4234 | 0.2332 | 0.4668 | 0.4469 | 0.6927 | 0.5666 | 0.4984 | 0.208 | 0.1598 | 0.7965 | 1.6024 | 0.498 | 0.4926 | 0.7155 | 0.6602 | 0.4386 | 0.8984 | 0.4452 | 0.5236 | 0.1199 | 0.1484
Load_TR5_F4_27 | prosumer | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.281 | 0.7151 | 0.2405 | 0.2721 | 0.5582 | 0.7718 | 1.9762 | 3.1351 | 1.5547 | 0.1672 | 0.0856 | 0.057 | 1.46 | 1.8352 | 0.0795 | 0.08 | 0.057 | 0.057 | 0.057 | 0.1952 | 0.2707 | 0.3561 | 0.0998 | 0.082 | 0.0708 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
Load_TR5_F4_28 | prosumer | 0.1506 | 0.2362 | 0.0688 | 0.1671 | 0.2366 | 0.052 | 0.2342 | 0.1694 | 0.0931 | 0.126 | 0.1694 | 0.1191 | 0.1671 | 0.2198 | 0.0688 | 0.1839 | 0.2198 | 0.0931 | 0.3105 | 0.052 | 0.3806 | 0.052 | 0.3907 | 0.0602 | 0.065 | 0.3569 | 0.292 | 0.1778 | 1.4041 | 0.3689 | 0.183 | 0.2975 | 0.1628 | 0.428 | 0.1013 | 0.2789 | 0.1589 | 0.2355 | 0.2923 | 0.4746 | 0.593 | 0.4111 | 0.0602 | 0.2366 | 0.1671 | 0.052 | 0.1671 | 0.052
Load_TR5_F4_29 | prosumer | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.1007 | 0.0942 | 0.1464 | 0.4828 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.227 | 0.4069 | 0.1121 | 0.159 | 0.9771 | 0.1451 | 0.1188 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
Load_TR5_F4_3 | customer | 0.1341 | 0.213 | 0.0872 | 0.047 | 0.2237 | 0.0985 | 0.0617 | 0.1675 | 0.1437 | 0.0728 | 0.2237 | 0.047 | 0.1996 | 0.0711 | 0.2731 | 0.3418 | 0.211 | 1.2291 | 0.1032 | 0.047 | 1.7792 | 0.0948 | 1.0298 | 0.2442 | 0.0663 | 0.3358 | 0.0988 | 0.6997 | 0.1018 | 1.1374 | 0.2911 | 0.1577 | 0.0617 | 0.2752 | 0.047 | 0.047 | 0.2076 | 0.1256 | 0.0507 | 0.2899 | 0.047 | 0.0872 | 0.1835 | 0.1133 | 0.2156 | 0.0624 | 0.1862 | 0.1507
Load_TR5_F4_30 | customer | 0.0874 | 0.194 | 0.043 | 0.2295 | 0.0519 | 0.043 | 0.0963 | 0.1851 | 0.043 | 0.2384 | 0.043 | 0.1318 | 0.1496 | 0.043 | 0.1313 | 0.043 | 0.043 | 0.3475 | 0.2765 | 0.1737 | 0.3478 | 0.1229 | 0.0763 | 0.2786 | 0.083 | 0.2428 | 1.1604 | 0.7085 | 2.3414 | 0.2063 | 0.0554 | 0.9001 | 0.8564 | 2.0212 | 0.8081 | 0.3079 | 0.2778 | 0.2556 | 1.483 | 0.6676 | 0.7069 | 0.8558 | 1.2159 | 0.7832 | 0.984 | 0.71 | 0.5429 | 0.2384
Load_TR5_F4_31 | customer | 0.3136 | 0.051 | 0.051 | 0.1408 | 0.2238 | 0.1408 | 0.051 | 0.3136 | 0.051 | 0.051 | 0.2238 | 0.056 | 0.3008 | 0.0589 | 0.1453 | 0.2193 | 0.051 | 0.2238 | 0.0759 | 0.1865 | 0.1531 | 0.1109 | 0.1909 | 0.2036 | 0.106 | 0.1688 | 0.051 | 0.2081 | 0.1565 | 0.051 | 0.3026 | 0.0808 | 0.2036 | 0.161 | 0.056 | 0.1672 | 0.1924 | 0.1408 | 0.2238 | 0.0909 | 0.203 | 0.1217 | 0.0909 | 0.1009 | 0.0981 | 0.2066 | 0.1109 | 0.2238
Load_TR5_F4_32 | prosumer | 0.1551 | 0.055 | 0.055 | 0.1551 | 0.055 | 0.1551 | 0.055 | 0.065 | 0.1451 | 0.055 | 0.1551 | 0.055 | 0.1451 | 0.065 | 0.1367 | 0.851 | 0.7112 | 2.303 | 0.3828 | 0.1964 | 0.1765 | 0.055 | 0.135 | 0.075 | 0.2953 | 0.9941 | 0.6782 | 1.1517 | 0.3573 | 0.2001 | 0.2612 | 0.2636 | 0.3156 | 0.4421 | 0.3217 | 0.3138 | 0.1616 | 0.3836 | 0.5758 | 0.5081 | 0.6567 | 0.4941 | 0.5726 | 2.8637 | 0.45 | 0.6458 | 0.1884 | 0.7147
Load_TR5_F4_33 | customer | 0.192 | 0.0862 | 0.056 | 0.056 | 0.056 | 0.056 | 0.2155 | 0.1996 | 0.0787 | 0.056 | 0.2223 | 0.056 | 0.1542 | 0.124 | 0.0922 | 0.2505 | 0.1372 | 1.179 | 0.2526 | 1.1199 | 0.2467 | 1.0049 | 0.1405 | 0.2994 | 0.056 | 0.2071 | 0.0838 | 0.0678 | 0.423 | 0.0771 | 0.3182 | 0.317 | 0.3865 | 1.137 | 0.2283 | 0.3675 | 0.3163 | 0.1286 | 0.2701 | 1.6466 | 1.7999 | 2.2906 | 2.0485 | 1.0965 | 0.9267 | 0.9875 | 1.1188 | 0.7316
Load_TR5_F4_34 | prosumer | 0.1047 | 0.1047 | 0.044 | 0.1378 | 0.0716 | 0.044 | 0.1268 | 0.0826 | 0.044 | 0.044 | 0.044 | 0.1598 | 0.0495 | 0.6503 | 0.9008 | 0.0881 | 0.044 | 0.9498 | 0.6503 | 0.1516 | 1.4207 | 1.0478 | 0.9159 | 0.044 | 0.044 | 0.4538 | 0.4583 | 2.7192 | 1.3738 | 0.6099 | 0.2043 | 0.044 | 0.044 | 0.1654 | 0.044 | 0.044 | 1.0771 | 0.2194 | 0.3348 | 0.3417 | 0.5597 | 0.3118 | 0.3995 | 0.5233 | 0.4384 | 0.2062 | 0.0771 | 0.1323
Load_TR5_F4_35 | prosumer | 0.05 | 0.1319 | 0.0705 | 0.05 | 0.05 | 0.1523 | 0.05 | 0.1319 | 0.0705 | 0.1063 | 0.096 | 0.05 | 0.1319 | 0.0705 | 0.05 | 0.139 | 1.5035 | 0.3587 | 0.0957 | 0.1841 | 0.146 | 0.05 | 0.209 | 0.1019 | 0.1472 | 0.1893 | 0.3844 | 0.0756 | 0.05 | 0.1011 | 0.1521 | 0.05 | 0.1523 | 0.2208 | 0.3385 | 0.3104 | 0.3991 | 0.3007 | 0.3743 | 0.6636 | 1.0465 | 1.315 | 0.493 | 0.4434 | 0.6178 | 0.6807 | 0.3404 | 0.4472
Load_TR5_F4_36 | prosumer | 0.05 | 0.1328 | 0.0921 | 0.1001 | 0.1467 | 0.05 | 0.0914 | 0.1052 | 0.05 | 0.1467 | 0.05 | 0.0707 | 0.1259 | 0.05 | 0.05 | 0.1328 | 0.0921 | 0.1454 | 0.2538 | 0.1556 | 0.1828 | 0.1202 | 0.0655 | 0.1483 | 0.112 | 1.2612 | 0.5659 | 0.2471 | 0.5128 | 0.3285 | 0.5208 | 2.499 | 0.8067 | 0.2649 | 0.6206 | 0.2903 | 0.2317 | 0.1465 | 1.4728 | 0.5586 | 0.2492 | 0.4321 | 0.5427 | 0.3807 | 0.7621 | 0.4165 | 0.562 | 0.1467
Load_TR5_F4_37 | customer | 0.1628 | 0.1912 | 0.0916 | 0.1865 | 0.1237 | 0.2303 | 0.052 | 0.294 | 0.0599 | 0.1068 | 0.0968 | 0.2782 | 0.052 | 0.302 | 0.0879 | 0.341 | 0.2129 | 0.3778 | 0.2519 | 0.6205 | 0.1232 | 0.0649 | 0.3045 | 0.1004 | 0.5421 | 0.313 | 0.2221 | 0.1976 | 0.3349 | 0.322 | 0.2901 | 0.3763 | 0.2338 | 0.675 | 0.8375 | 0.2647 | 0.3415 | 0.2426 | 0.1603 | 0.4432 | 0.445 | 0.5055 | 0.5189 | 0.3522 | 0.1628 | 0.1912 | 0.052 | 0.139
Load_TR5_F4_38 | prosumer | 0.05 | 0.2216 | 0.1718 | 0.05 | 0.2138 | 0.143 | 0.0943 | 0.2138 | 0.1535 | 0.2086 | 0.1116 | 0.1491 | 0.2138 | 0.1718 | 0.05 | 0.05 | 0.5838 | 0.0734 | 0.1413 | 0.3087 | 0.3113 | 0.3728 | 0.3436 | 0.1049 | 1.291 | 0.3525 | 0.2337 | 0.302 | 0.1253 | 0.2398 | 0.1535 | 0.05 | 0.05 | 0.1718 | 1.418 | 0.4689 | 0.4449 | 0.3547 | 0.61 | 0.5986 | 0.483 | 0.6328 | 0.578 | 0.7096 | 0.7654 | 0.2706 | 0.6686 | 0.3174
Load_TR5_F4_39 | prosumer | 0.05 | 0.1414 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1414 | 0.05 | 0.05 | 0.05 | 0.1312 | 0.0602 | 0.1261 | 0.0652 | 0.1363 | 0.0551 | 0.1058 | 0.0855 | 0.0805 | 0.1759 | 0.2357 | 0.0855 | 0.05 | 0.2925 | 0.1261 | 0.2499 | 0.1363 | 0.05 | 0.1414 | 0.05 | 0.05 | 0.1414 | 0.05 | 0.1414 | 0.05 | 0.3561 | 0.213 | 0.1154 | 0.2692 | 0.3338 | 0.5455 | 0.4882 | 0.3716 | 0.6086 | 0.6778 | 0.246 | 0.05
Load_TR5_F4_4 | customer | 0.045 | 0.2125 | 0.0737 | 0.045 | 0.1187 | 0.1674 | 0.0818 | 0.1737 | 0.0756 | 0.2327 | 0.1083 | 0.1023 | 0.2874 | 0.1111 | 0.1359 | 0.1504 | 0.1862 | 0.1268 | 1.0609 | 0.2868 | 1.0327 | 0.1396 | 0.1285 | 0.0505 | 0.1006 | 0.1318 | 0.1187 | 0.045 | 0.2411 | 0.045 | 0.0941 | 0.0696 | 0.0573 | 0.1921 | 0.1145 | 0.1227 | 0.1716 | 0.274 | 0.5327 | 0.4979 | 2.4926 | 2.9234 | 1.7905 | 0.4894 | 0.6216 | 0.4697 | 0.0572 | 0.2289
Load_TR5_F4_40 | customer | 0.0775 | 0.1612 | 0.1411 | 0.054 | 0.054 | 0.2013 | 0.1244 | 0.1679 | 0.1579 | 0.1277 | 0.4962 | 0.054 | 0.1344 | 0.1601 | 0.0853 | 0.2483 | 0.1815 | 0.3166 | 1.0666 | 1.1524 | 1.7757 | 0.4892 | 0.4267 | 0.2844 | 0.196 | 0.2274 | 0.175 | 0.258 | 0.1635 | 0.1713 | 0.054 | 0.2013 | 0.2797 | 0.1119 | 0.2083 | 0.1314 | 0.1351 | 0.2619 | 0.6065 | 0.4631 | 0.5144 | 0.4882 | 0.4165 | 0.6303 | 0.532 | 0.5817 | 0.4917 | 0.1512
Load_TR5_F4_41 | customer | 0.2152 | 0.054 | 0.2005 | 0.0687 | 0.1492 | 0.1199 | 0.098 | 0.1712 | 0.054 | 0.2005 | 0.0687 | 0.054 | 0.2152 | 0.054 | 0.2796 | 0.1053 | 0.054 | 0.2152 | 0.2001 | 0.224 | 0.3661 | 0.2761 | 0.311 | 0.3327 | 0.2591 | 0.0711 | 0.2928 | 0.1116 | 0.1472 | 0.4351 | 0.3864 | 0.1846 | 0.1199 | 0.054 | 0.098 | 0.1712 | 0.054 | 0.2152 | 0.054 | 0.1932 | 0.076 | 0.2878 | 0.6727 | 0.4242 | 0.7049 | 0.13 | 0.054 | 0.2152
Load_TR5_F4_42 | customer | 0.1915 | 0.052 | 0.1317 | 0.1184 | 0.0852 | 0.165 | 0.052 | 0.052 | 0.1716 | 0.0786 | 0.0919 | 0.1583 | 0.052 | 0.1982 | 0.052 | 0.0985 | 0.1517 | 0.052 | 0.1982 | 0.052 | 0.1269 | 0.2414 | 0.1052 | 2.6881 | 3.0594 | 0.9474 | 0.0918 | 0.1224 | 0.1517 | 0.052 | 0.2017 | 0.052 | 0.165 | 0.0852 | 0.118 | 0.5186 | 0.8933 | 0.1742 | 0.3685 | 0.2497 | 0.5331 | 0.6675 | 0.3525 | 0.5543 | 0.4957 | 0.3725 | 0.1583 | 0.052
Load_TR5_F4_43 | customer | 0.1587 | 0.058 | 0.2057 | 0.058 | 0.1453 | 0.1184 | 0.058 | 0.2057 | 0.058 | 0.1788 | 0.0848 | 0.058 | 0.2057 | 0.058 | 0.0848 | 0.1788 | 0.058 | 0.058 | 0.2057 | 0.058 | 0.0636 | 0.4267 | 0.1494 | 0.0814 | 0.1892 | 0.262 | 0.105 | 0.2454 | 0.191 | 0.2057 | 0.058 | 0.1654 | 0.0983 | 0.1117 | 0.202 | 0.0833 | 0.1398 | 0.2574 | 0.4234 | 0.4254 | 0.4231 | 0.522 | 0.4849 | 0.4589 | 0.567 | 0.4406 | 0.7226 | 0.058
Load_TR5_F4_44 | customer | 0.0843 | 0.0843 | 0.047 | 0.1216 | 0.047 | 0.0636 | 0.1051 | 0.047 | 0.1216 | 0.047 | 0.0802 | 0.0885 | 0.047 | 0.047 | 0.047 | 0.1216 | 0.047 | 0.0496 | 0.2313 | 0.1236 | 0.1051 | 0.047 | 0.1216 | 0.0553 | 0.1133 | 0.047 | 0.0796 | 0.1354 | 0.2264 | 0.1266 | 0.047 | 0.1216 | 0.047 | 0.1216 | 0.047 | 0.047 | 0.7151 | 1.3085 | 0.0595 | 0.2949 | 0.1798 | 0.3553 | 0.2687 | 0.2144 | 0.0968 | 0.0719 | 0.047 | 0.047
Load_TR5_F4_45 | prosumer | 0.1096 | 0.1894 | 0.055 | 0.1688 | 0.2021 | 0.0931 | 0.2779 | 0.055 | 0.2571 | 0.1138 | 0.1983 | 0.1727 | 0.0804 | 0.1057 | 0.2398 | 0.055 | 0.2316 | 0.1393 | 0.055 | 0.3159 | 0.055 | 0.2067 | 0.1642 | 0.1311 | 0.1558 | 0.4695 | 0.1185 | 0.0631 | 0.177 | 0.1939 | 0.1057 | 0.2652 | 0.2572 | 0.4232 | 0.7511 | 0.4148 | 0.4997 | 0.3768 | 1.6193 | 0.3896 | 0.5428 | 0.8284 | 2.537 | 0.7227 | 0.1563 | 0.3943 | 0.6894 | 0.2876
Load_TR5_F4_46 | prosumer | 1.0587 | 0.8183 | 0.054 | 0.0689 | 0.1283 | 0.054 | 0.1432 | 0.054 | 0.054 | 0.054 | 0.0936 | 0.1036 | 0.1234 | 0.0738 | 0.0936 | 0.1036 | 0.054 | 0.054 | 0.1432 | 0.054 | 0.054 | 0.1432 | 0.054 | 0.1432 | 0.054 | 0.054 | 0.1432 | 0.054 | 0.1283 | 0.0689 | 0.054 | 0.054 | 0.1432 | 0.054 | 0.054 | 0.054 | 0.1432 | 0.1126 | 0.2243 | 0.4758 | 0.468 | 0.683 | 0.7948 | 0.562 | 0.054 | 0.054 | 0.054 | 0.059
Load_TR5_F4_47 | prosumer | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.1337 | 0.2621 | 0.2509 | 0.2509 | 0.1609 | 0.0638 | 0.2678 | 0.0737 | 0.3428 | 0.1143 | 0.2615 | 0.054 | 0.052 | 0.0644 | 0.3203 | 0.1457 | 0.2667 | 0.3607 | 0.3902 | 0.342 | 0.1632 | 0.052 | 0.052
Load_TR5_F4_48 | customer | 0.1292 | 0.1656 | 0.1701 | 0.0824 | 0.1589 | 0.1924 | 0.046 | 0.2373 | 0.114 | 0.1166 | 0.1307 | 0.15 | 0.2012 | 0.1694 | 0.5333 | 0.2927 | 0.1864 | 0.2741 | 0.1956 | 0.1571 | 0.2584 | 0.046 | 0.1842 | 0.17 | 0.0742 | 0.277 | 0.046 | 0.3966 | 0.1114 | 0.046 | 0.1344 | 0.225 | 0.0562 | 0.2146 | 0.1366 | 0.1075 | 1.1214 | 0.716 | 0.5446 | 0.5283 | 2.148 | 0.7579 | 0.4785 | 0.71 | 0.7612 | 0.7373 | 0.8152 | 0.6386
Load_TR5_F4_49 | prosumer | 0.2314 | 0.05 | 0.05 | 0.2314 | 0.05 | 0.083 | 0.1985 | 0.05 | 0.2314 | 0.05 | 0.05 | 0.1985 | 0.083 | 0.1325 | 0.149 | 0.05 | 0.2749 | 0.151 | 1.3022 | 0.0665 | 0.05 | 0.05 | 0.05 | 0.2349 | 0.0914 | 0.1744 | 0.2067 | 0.05 | 0.0747 | 0.2067 | 0.05 | 0.3507 | 0.2304 | 0.1373 | 0.4906 | 0.0641 | 0.2528 | 0.294 | 0.2263 | 0.5023 | 0.5621 | 1.4561 | 0.3774 | 0.5289 | 0.4062 | 0.5193 | 0.416 | 0.4258
Load_TR5_F4_5 | prosumer | 0.1448 | 0.046 | 0.046 | 0.046 | 0.1182 | 0.046 | 0.046 | 0.1182 | 0.046 | 0.0942 | 0.0701 | 0.058 | 0.1062 | 0.1103 | 0.233 | 0.2388 | 0.2333 | 0.2099 | 0.2496 | 0.2703 | 0.4573 | 0.358 | 0.046 | 0.1182 | 0.046 | 0.1182 | 0.046 | 0.1625 | 0.2845 | 0.221 | 0.1467 | 0.0982 | 0.0661 | 0.0901 | 0.0741 | 0.046 | 0.1182 | 0.046 | 0.1182 | 0.046 | 0.046 | 0.0982 | 0.0661 | 0.046 | 0.1365 | 0.3367 | 0.448 | 0.5261
Load_TR5_F4_50 | customer | 0.2317 | 0.05 | 0.1491 | 0.1326 | 0.05 | 0.05 | 0.2317 | 0.05 | 0.1739 | 0.1078 | 0.1161 | 0.1952 | 0.1 | 0.1506 | 0.1326 | 0.05 | 0.083 | 0.1986 | 0.9399 | 0.1656 | 0.2032 | 0.0852 | 0.4559 | 0.05 | 0.0913 | 0.1904 | 0.05 | 0.2069 | 1.2381 | 0.2942 | 0.271 | 0.2388 | 0.0667 | 0.1396 | 0.2441 | 0.1598 | 1.1115 | 1.0271 | 1.7857 | 0.7888 | 0.614 | 0.8793 | 0.7816 | 0.7571 | 0.862 | 0.4073 | 0.2317 | 0.05
Load_TR5_F4_51 | customer | 0.1724 | 0.052 | 0.052 | 0.1603 | 0.064 | 0.052 | 0.1062 | 0.1182 | 0.052 | 0.052 | 0.052 | 0.1182 | 0.1062 | 0.052 | 0.1724 | 0.052 | 0.052 | 0.0701 | 0.1543 | 0.052 | 0.1724 | 0.052 | 0.1122 | 0.1122 | 0.064 | 0.1716 | 0.3244 | 0.3322 | 0.3384 | 0.1732 | 0.2354 | 0.5092 | 0.3405 | 0.2106 | 0.1488 | 0.4184 | 0.1759 | 0.2282 | 0.2875 | 0.4697 | 0.3508 | 0.3541 | 0.7338 | 0.5716 | 0.49 | 0.3307 | 0.052 | 0.052
Load_TR5_F4_52 | customer | 0.044 | 0.1195 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.1296 | 0.0507 | 0.044 | 0.0782 | 0.3909 | 0.3556 | 0.3176 | 0.2964 | 0.3118 | 0.2079 | 0.1944 | 0.1949 | 0.4397 | 0.4044 | 0.0509 | 0.49 | 0.2273 | 0.2375 | 0.2187 | 0.5082 | 0.6658 | 0.59 | 0.505 | 0.2639 | 0.1905 | 0.0538 | 0.0711 | 0.1484 | 0.3616 | 0.466 | 0.6069 | 0.7207 | 0.746 | 0.6935 | 0.6626 | 0.2442 | 0.3622
Load_TR5_F4_53 | customer | 0.1196 | 0.0902 | 0.024 | 0.1858 | 0.024 | 0.149 | 0.0608 | 0.024 | 0.024 | 0.024 | 0.0608 | 0.149 | 0.024 | 0.1563 | 0.2827 | 0.1973 | 0.3006 | 0.3177 | 0.2639 | 0.0608 | 0.024 | 0.1858 | 0.024 | 0.1416 | 0.0681 | 0.024 | 0.024 | 0.1269 | 0.1977 | 0.1613 | 0.1538 | 0.2645 | 0.1332 | 0.2108 | 0.151 | 2.0849 | 0.9228 | 1.6825 | 0.0975 | 0.1508 | 0.4277 | 0.142 | 0.2265 | 0.4905 | 0.3381 | 0.2445 | 0.3032 | 0.024
Load_TR5_F4_54 | customer | 0.13 | 0.1182 | 0.1991 | 0.0661 | 0.1726 | 0.1744 | 0.051 | 0.1991 | 0.163 | 0.051 | 0.2028 | 0.1593 | 0.1245 | 0.2332 | 0.107 | 0.0635 | 0.0854 | 0.2465 | 0.0811 | 0.1765 | 0.0736 | 0.1364 | 0.1579 | 0.1188 | 0.1923 | 0.1698 | 0.0698 | 0.2227 | 0.1447 | 0.1426 | 0.6175 | 0.4993 | 0.2852 | 0.1458 | 0.2383 | 0.1238 | 0.1647 | 0.0854 | 0.2367 | 0.1313 | 0.3201 | 0.4132 | 0.4843 | 0.372 | 0.3296 | 0.7609 | 0.6238 | 0.4331
Load_TR5_F4_55 | prosumer | 0.051 | 0.1264 | 0.2189 | 0.051 | 0.0761 | 0.1163 | 0.2039 | 0.1414 | 0.1413 | 0.1135 | 0.051 | 0.3013 | 1.2585 | 0.176 | 0.1253 | 2.2153 | 0.5016 | 2.0074 | 0.0718 | 0.051 | 0.2943 | 0.051 | 0.1066 | 0.1583 | 0.1314 | 0.0579 | 0.1969 | 0.051 | 0.2368 | 1.5149 | 1.4184 | 0.6507 | 0.1228 | 0.1167 | 0.1597 | 0.138 | 0.7057 | 0.9844 | 0.2452 | 1.6374 | 1.1847 | 1.0935 | 0.2025 | 0.2021 | 0.1205 | 0.0912 | 0.2472 | 0.0646
Load_TR5_F4_56 | customer | 0.1348 | 0.15 | 0.059 | 0.1955 | 0.0893 | 0.059 | 0.1348 | 0.15 | 0.059 | 0.2258 | 0.059 | 0.1955 | 0.1827 | 0.134 | 0.918 | 0.8815 | 0.8815 | 0.2505 | 0.059 | 0.1955 | 0.1035 | 0.1273 | 0.1576 | 0.059 | 0.0969 | 0.1879 | 0.059 | 0.1348 | 0.2026 | 0.1123 | 0.1351 | 0.363 | 0.3193 | 1.6016 | 2.7804 | 1.2233 | 0.2613 | 0.2755 | 0.299 | 0.5571 | 0.4384 | 0.4632 | 0.5529 | 0.2041 | 0.2258 | 0.059 | 0.0818 | 0.7632
Load_TR5_F4_57 | prosumer | 0.8637 | 0.1029 | 0.1773 | 0.057 | 0.0911 | 0.1509 | 0.1293 | 0.1203 | 0.057 | 0.0765 | 0.1808 | 0.0799 | 0.1495 | 0.1307 | 0.1446 | 0.0667 | 0.057 | 0.1648 | 0.1231 | 0.1182 | 0.1495 | 0.1615 | 1.2584 | 0.5228 | 0.3132 | 0.7412 | 1.7858 | 1.7133 | 0.7954 | 1.2842 | 0.4234 | 0.1877 | 1.7472 | 0.1928 | 0.3058 | 0.1216 | 0.1544 | 0.2597 | 0.26 | 0.4129 | 0.4068 | 0.4694 | 0.5083 | 0.3559 | 1.0889 | 0.709 | 0.7756 | 0.4747
Load_TR5_F4_58 | prosumer | 0.333 | 0.1097 | 0.13 | 0.2078 | 0.0939 | 0.2492 | 0.3933 | 0.3405 | 0.3482 | 0.1866 | 0.171 | 0.137 | 0.2547 | 0.0887 | 0.2369 | 0.1009 | 0.1569 | 0.3196 | 0.1033 | 0.5267 | 1.245 | 0.1789 | 0.3844 | 0.2203 | 0.089 | 0.325 | 0.988 | 0.4287 | 0.749 | 0.2481 | 2.3863 | 2.2271 | 0.052 | 1.4753 | 1.0835 | 1.2448 | 0.2941 | 0.1202 | 0.1853 | 1.8189 | 0.5887 | 0.3311 | 0.6811 | 0.2477 | 0.559 | 0.4459 | 0.4519 | 0.6233
Load_TR5_F4_59 | prosumer | 0.041 | 0.2133 | 0.1746 | 0.1115 | 0.1428 | 0.1479 | 0.2401 | 0.041 | 0.3402 | 0.0477 | 0.1536 | 0.2343 | 0.1078 | 0.2901 | 0.041 | 0.2686 | 0.1193 | 0.1746 | 0.0723 | 0.182 | 0.0744 | 0.3135 | 0.041 | 0.1345 | 0.2534 | 0.1011 | 0.3961 | 0.0802 | 0.041 | 0.2133 | 0.0677 | 0.1479 | 1.9435 | 2.2345 | 1.3594 | 0.5364 | 0.3331 | 0.1531 | 0.2604 | 0.3161 | 0.2804 | 0.392 | 0.663 | 1.6105 | 0.5087 | 0.5108 | 0.041 | 0.1746
Load_TR5_F4_6 | customer | 0.095 | 0.1737 | 0.0621 | 0.0727 | 0.2121 | 0.046 | 0.3739 | 0.046 | 0.1217 | 0.0826 | 0.1264 | 0.0549 | 0.1575 | 0.1362 | 0.1084 | 0.3075 | 1.1083 | 0.1109 | 0.1586 | 0.1262 | 0.1425 | 0.148 | 0.088 | 1.433 | 0.6571 | 0.2053 | 0.2251 | 0.1224 | 0.1885 | 0.2665 | 0.3602 | 0.2817 | 0.2266 | 0.1672 | 0.3076 | 0.379 | 0.251 | 0.1448 | 0.193 | 0.5151 | 0.584 | 0.7448 | 0.3152 | 0.1262 | 0.1586 | 0.1262 | 0.0988 | 0.2182
Load_TR5_F4_60 | customer | 0.04 | 0.0461 | 0.1195 | 0.04 | 0.1072 | 0.0583 | 0.04 | 0.1195 | 0.0461 | 0.04 | 0.1256 | 0.04 | 0.04 | 0.1256 | 0.0842 | 0.1727 | 0.3822 | 0.2856 | 0.9181 | 0.2675 | 0.2384 | 0.1256 | 0.04 | 0.04 | 0.1256 | 0.04 | 0.04 | 0.0706 | 0.1914 | 0.1624 | 0.2601 | 0.1256 | 0.1499 | 0.0823 | 0.123 | 0.04 | 0.0767 | 0.1372 | 0.3035 | 0.7185 | 0.6839 | 0.7205 | 0.8795 | 0.987 | 0.6354 | 0.9947 | 0.5583 | 0.5734
Load_TR5_F4_61 | customer | 0.6339 | 0.6964 | 0.1321 | 0.0724 | 0.1958 | 0.1231 | 0.051 | 0.2083 | 0.051 | 0.051 | 0.051 | 0.2642 | 0.0762 | 0.051 | 0.0653 | 0.198 | 0.1321 | 0.4171 | 0.1321 | 0.3885 | 0.2884 | 0.0796 | 1.8893 | 2.384 | 0.5967 | 0.1582 | 0.1321 | 0.2083 | 0.0555 | 0.1296 | 0.3282 | 0.142 | 0.0724 | 0.408 | 0.2791 | 0.2349 | 0.2191 | 0.4302 | 0.3105 | 0.051 | 0.2894 | 0.051 | 0.1082 | 0.2322 | 0.051 | 0.2679 | 0.0724 | 0.6229
Load_TR5_F4_62 | prosumer | 0.048 | 0.1268 | 0.1268 | 0.0552 | 0.1985 | 0.048 | 0.1913 | 0.0623 | 0.1053 | 0.1483 | 0.048 | 0.2056 | 0.048 | 0.048 | 0.3368 | 0.2116 | 0.2895 | 2.4062 | 1.4482 | 0.05 | 0.2056 | 0.048 | 0.048 | 0.0784 | 0.2003 | 0.9269 | 0.2163 | 0.4795 | 1.1743 | 0.509 | 0.3107 | 0.2259 | 0.048 | 0.1913 | 0.0623 | 0.0703 | 0.0785 | 0.2925 | 0.3955 | 0.3432 | 0.4712 | 0.3574 | 0.3945 | 0.653 | 0.3656 | 0.376 | 0.5437 | 0.1565
Load_TR5_F4_63 | prosumer | 0.5885 | 0.5791 | 0.7509 | 0.6754 | 0.5453 | 0.1059 | 0.1891 | 0.056 | 0.1225 | 0.1724 | 0.056 | 0.0643 | 0.4871 | 0.3224 | 0.214 | 0.0809 | 0.1641 | 0.1308 | 0.0976 | 0.1974 | 0.056 | 0.1142 | 0.1807 | 0.056 | 0.1891 | 0.1059 | 0.2835 | 0.1807 | 0.1502 | 0.3406 | 0.2658 | 0.863 | 0.2167 | 1.4063 | 1.0041 | 1.0812 | 0.1097 | 0.4736 | 0.4209 | 0.4908 | 0.8513 | 2.2454 | 0.7545 | 0.6512 | 0.5914 | 0.6059 | 0.6685 | 0.1857
Load_TR5_F4_64 | prosumer | 0.054 | 0.054 | 0.0604 | 0.1753 | 0.054 | 0.1817 | 0.054 | 0.0795 | 0.1562 | 0.054 | 0.137 | 0.0987 | 0.054 | 0.1817 | 0.054 | 0.1753 | 0.0604 | 0.054 | 0.1817 | 0.054 | 0.054 | 0.054 | 0.1817 | 0.054 | 0.1753 | 0.0604 | 0.1434 | 0.0923 | 0.1575 | 0.168 | 0.1591 | 0.4725 | 2.6402 | 0.3953 | 0.6177 | 0.4088 | 0.7757 | 0.2566 | 0.3824 | 0.9033 | 0.6088 | 0.2266 | 0.3203 | 0.8766 | 0.5862 | 0.75 | 0.5295 | 0.3707
Load_TR5_F4_65 | customer | 0.042 | 0.1043 | 0.1168 | 0.042 | 0.042 | 0.1791 | 0.042 | 0.1479 | 0.0732 | 0.042 | 0.0482 | 0.1729 | 0.042 | 0.1666 | 0.0545 | 0.042 | 0.1654 | 0.1928 | 0.9245 | 0.1338 | 0.2477 | 0.0821 | 0.1083 | 0.1693 | 0.042 | 0.0981 | 0.123 | 0.0482 | 0.1729 | 0.042 | 0.1106 | 0.1106 | 0.0607 | 0.1604 | 0.042 | 0.0744 | 0.0734 | 0.0856 | 0.1782 | 1.1115 | 0.4385 | 0.1779 | 0.5282 | 0.5562 | 0.042 | 0.0545 | 0.1666 | 0.042
Load_TR5_F4_66 | customer | 0.0583 | 0.1996 | 0.1272 | 0.0696 | 0.1452 | 0.4545 | 0.1168 | 0.0959 | 0.0738 | 0.2831 | 0.047 | 0.2234 | 0.047 | 0.1548 | 0.1833 | 0.1147 | 0.2352 | 0.938 | 0.1805 | 0.3166 | 0.0772 | 0.0696 | 0.0871 | 0.251 | 0.1999 | 0.1628 | 0.1753 | 0.126 | 0.2261 | 0.1387 | 0.047 | 0.1753 | 0.1628 | 0.206 | 1.8584 | 1.6722 | 0.3755 | 0.336 | 1.1846 | 0.5901 | 0.6213 | 1.806 | 0.4357 | 0.6185 | 0.5931 | 0.3749 | 0.8884 | 0.3232
Load_TR5_F4_67 | customer | 0.202 | 0.0941 | 0.233 | 0.1207 | 0.048 | 0.2112 | 0.1425 | 0.048 | 0.0969 | 0.0969 | 0.2007 | 0.153 | 0.048 | 0.048 | 0.3057 | 0.048 | 0.1023 | 0.0915 | 0.2731 | 0.0806 | 0.2156 | 0.2152 | 0.852 | 0.3701 | 0.3394 | 0.3124 | 0.6268 | 0.4228 | 0.5915 | 0.1607 | 0.2443 | 0.2725 | 0.2054 | 0.6678 | 0.1679 | 0.4191 | 1.6601 | 1.4665 | 1.8601 | 1.2398 | 0.6132 | 0.6025 | 0.843 | 0.8558 | 0.565 | 0.5317 | 0.273 | 0.511
Load_TR5_F4_68 | customer | 0.0968 | 0.1445 | 0.1445 | 0.057 | 0.0729 | 0.216 | 0.057 | 0.232 | 0.057 | 0.0809 | 0.2081 | 0.057 | 0.2096 | 0.0809 | 0.1246 | 0.364 | 0.4456 | 0.2019 | 0.6558 | 0.2321 | 0.5173 | 0.3291 | 0.7225 | 0.9856 | 0.2963 | 0.185 | 0.0994 | 0.0997 | 0.2522 | 1.4628 | 0.3185 | 1.2477 | 0.7794 | 1.9419 | 0.232 | 0.122 | 0.2459 | 0.3588 | 0.1219 | 0.4426 | 0.3061 | 0.3804 | 0.1524 | 0.1365 | 0.0729 | 0.216 | 0.057 | 0.232
Load_TR5_F4_69 | prosumer | 0.1547 | 0.1578 | 0.1601 | 0.096 | 0.1296 | 0.2323 | 0.052 | 0.2588 | 0.1031 | 0.1296 | 0.1296 | 0.1547 | 0.1437 | 0.1155 | 0.1897 | 0.2835 | 0.0601 | 0.9033 | 2.4538 | 1.7618 | 0.1437 | 0.7608 | 1.9779 | 0.5447 | 0.6928 | 0.3797 | 0.3338 | 0.5683 | 0.3971 | 0.052 | 0.3099 | 0.052 | 0.0952 | 0.2667 | 0.052 | 0.1547 | 0.052 | 0.2072 | 0.1547 | 0.052 | 0.2072 | 0.1547 | 0.1296 | 0.1663 | 0.118 | 0.1437 | 0.2182 | 0.052
Load_TR5_F4_7 | customer | 0.136 | 0.1209 | 0.1209 | 0.046 | 0.2722 | 0.046 | 0.1745 | 0.1437 | 0.0596 | 0.1822 | 0.046 | 0.2722 | 0.046 | 0.0757 | 0.2425 | 0.0715 | 0.3588 | 0.933 | 0.714 | 0.2434 | 0.2231 | 0.1775 | 1.9894 | 2.549 | 1.9466 | 0.1298 | 0.0996 | 0.2186 | 0.046 | 0.2178 | 0.1005 | 0.063 | 0.1054 | 0.1737 | 0.2032 | 0.3901 | 0.9162 | 0.853 | 1.7691 | 0.3755 | 0.5304 | 0.3004 | 0.8065 | 0.4171 | 0.6165 | 0.361 | 0.4816 | 0.1635
Load_TR5_F4_70 | customer | 0.05 | 0.05 | 0.1493 | 0.1172 | 0.077 | 0.1895 | 0.05 | 0.1268 | 0.1397 | 0.1129 | 0.1046 | 0.0989 | 0.05 | 0.797 | 0.6887 | 0.2205 | 1.1601 | 0.5106 | 0.2225 | 0.2671 | 0.2287 | 0.3314 | 0.2489 | 0.1355 | 0.1244 | 0.1424 | 0.3048 | 0.4503 | 0.2004 | 0.5588 | 0.2949 | 0.2788 | 0.1145 | 0.1309 | 0.2275 | 0.1309 | 1.2677 | 0.2358 | 0.099 | 0.2787 | 0.3824 | 0.2451 | 0.3327 | 0.2994 | 0.2606 | 0.3874 | 0.134 | 0.1615
Load_TR5_F4_71 | customer | 0.2002 | 0.044 | 0.0724 | 0.1718 | 0.044 | 0.044 | 0.1079 | 0.1363 | 0.044 | 0.1718 | 0.0724 | 0.044 | 0.2082 | 0.1518 | 0.0511 | 0.2203 | 0.0766 | 0.2748 | 0.2583 | 0.1934 | 0.1628 | 0.1877 | 0.0598 | 0.2405 | 0.3706 | 0.1137 | 0.9997 | 0.2401 | 0.1977 | 0.2804 | 0.1647 | 0.05 | 0.044 | 0.1935 | 0.0944 | 0.1662 | 0.1976 | 0.1649 | 0.4148 | 0.1667 | 0.3347 | 0.2351 | 0.2823 | 0.392 | 0.2383 | 0.2444 | 0.1782 | 0.0724
Load_TR5_F4_72 | prosumer | 1.3405 | 1.1761 | 0.7166 | 0.2204 | 0.052 | 0.052 | 0.1575 | 0.052 | 0.052 | 0.1123 | 0.0972 | 0.052 | 0.1047 | 0.1047 | 0.2765 | 0.2685 | 0.1651 | 1.1689 | 1.6927 | 0.87 | 0.2333 | 0.2163 | 0.1222 | 1.1117 | 0.2406 | 0.2523 | 0.1245 | 0.3395 | 0.2227 | 0.1612 | 0.2216 | 0.2236 | 0.3841 | 0.4724 | 1.1489 | 0.2717 | 0.1649 | 0.2439 | 2.005 | 0.6656 | 0.7687 | 0.6086 | 0.7297 | 0.6059 | 0.9153 | 0.4973 | 0.1575 | 0.052
Load_TR5_F4_73 | prosumer | 0.1663 | 0.1505 | 0.0638 | 0.1032 | 0.1603 | 0.1722 | 0.1072 | 0.048 | 0.3867 | 0.2429 | 0.2659 | 0.2014 | 0.048 | 0.134 | 0.1828 | 0.119 | 0.1641 | 2.2787 | 0.048 | 1.0755 | 0.1648 | 0.0771 | 0.6387 | 1.2281 | 0.9713 | 0.3102 | 0.1118 | 0.2083 | 0.3044 | 0.2688 | 0.0555 | 0.2412 | 0.0756 | 0.1828 | 0.1221 | 0.0598 | 0.2353 | 0.3853 | 0.3204 | 0.5445 | 0.3761 | 0.5718 | 0.5129 | 0.6295 | 0.6291 | 0.2334 | 0.1978 | 0.119
Load_TR5_F4_74 | customer | 0.2442 | 0.1447 | 0.1256 | 0.1927 | 0.1531 | 0.2976 | 0.0628 | 0.1393 | 0.1117 | 0.3059 | 0.1449 | 0.151 | 0.2958 | 0.0529 | 0.3312 | 0.049 | 0.2318 | 0.276 | 0.8216 | 3.5879 | 1.7002 | 0.3055 | 0.3409 | 0.0639 | 0.2606 | 0.1819 | 0.4295 | 0.4314 | 0.5067 | 0.4203 | 1.4424 | 0.3758 | 0.3081 | 0.537 | 0.3559 | 1.5179 | 0.1119 | 0.1778 | 0.4472 | 0.3055 | 0.5424 | 0.334 | 1.0495 | 0.9741 | 0.7053 | 0.4441 | 0.4781 | 0.6523
Load_TR5_F4_75 | customer | 0.1214 | 0.1214 | 0.0547 | 0.1881 | 0.048 | 0.1147 | 0.128 | 0.048 | 0.048 | 0.1947 | 0.048 | 0.1747 | 0.068 | 0.048 | 0.1947 | 0.3551 | 0.1414 | 0.1014 | 0.1014 | 0.1414 | 0.0709 | 0.394 | 0.195 | 0.088 | 0.1547 | 0.048 | 0.128 | 0.1147 | 0.088 | 0.1547 | 0.048 | 0.1947 | 0.048 | 0.048 | 0.048 | 0.1747 | 0.068 | 0.108 | 0.1347 | 0.048 | 0.4156 | 0.7895 | 0.5445 | 0.6456 | 0.168 | 0.048 | 0.1947 | 0.048
Load_TR5_F4_76 | customer | 0.0683 | 0.1023 | 1.222 | 0.1228 | 0.0741 | 0.1433 | 0.047 | 0.0768 | 0.2626 | 0.0555 | 0.1611 | 0.1697 | 0.1236 | 0.0555 | 0.2685 | 0.0623 | 0.0895 | 0.2268 | 0.2324 | 1.2485 | 0.1621 | 0.4317 | 0.4068 | 0.1938 | 0.2534 | 0.6064 | 0.2762 | 0.262 | 0.254 | 0.1347 | 0.2047 | 0.1193 | 0.1927 | 0.1466 | 0.047 | 0.1236 | 0.047 | 0.1466 | 0.1927 | 0.1236 | 0.1237 | 0.139 | 0.1236 | 0.047 | 0.2923 | 0.047 | 0.047 | 0.2004
Load_TR5_F4_77 | prosumer | 0.3765 | 0.9101 | 2.6996 | 2.552 | 0.053 | 0.2153 | 0.053 | 0.0825 | 0.1858 | 0.053 | 0.1563 | 0.112 | 0.053 | 0.1415 | 0.1268 | 0.053 | 0.2153 | 0.0557 | 0.2338 | 0.307 | 0.127 | 0.2153 | 0.053 | 0.1563 | 0.112 | 0.112 | 0.1563 | 0.053 | 0.2153 | 0.053 | 0.2488 | 0.3665 | 0.1895 | 0.2484 | 0.3012 | 0.16 | 0.2588 | 0.3615 | 0.3567 | 0.37 | 0.3897 | 0.6623 | 0.5976 | 0.6651 | 0.7529 | 0.5718 | 0.9651 | 0.4724
Load_TR5_F4_78 | customer | 0.1884 | 0.049 | 0.1024 | 0.2299 | 0.049 | 0.049 | 0.2833 | 0.049 | 0.1481 | 0.1189 | 0.1225 | 0.1564 | 0.1676 | 0.1647 | 0.049 | 0.049 | 0.2833 | 0.049 | 0.1564 | 0.1759 | 0.049 | 0.1647 | 0.1676 | 0.1151 | 0.3693 | 0.6983 | 0.2581 | 0.318 | 0.2737 | 0.2185 | 0.1962 | 0.049 | 0.1316 | 0.171 | 0.0787 | 0.2299 | 0.1024 | 0.1068 | 0.2655 | 0.4184 | 0.4894 | 0.5142 | 0.6144 | 0.7707 | 0.2511 | 0.4369 | 0.2491 | 0.1765
Load_TR5_F4_79 | customer | 0.1181 | 0.0693 | 0.2156 | 0.053 | 0.1181 | 0.1668 | 0.053 | 0.0855 | 0.1994 | 0.053 | 0.2319 | 0.053 | 0.1425 | 0.1425 | 0.119 | 0.2319 | 0.1492 | 0.1738 | 0.403 | 0.053 | 0.1425 | 0.3568 | 1.3679 | 0.7109 | 0.173 | 0.3832 | 0.2319 | 0.053 | 0.1994 | 0.0899 | 1.0914 | 0.6433 | 0.5068 | 0.5322 | 0.1286 | 1.2908 | 0.1965 | 0.508 | 0.053 | 0.2319 | 0.053 | 0.1668 | 0.1181 | 0.053 | 0.2319 | 0.2142 | 0.2675 | 0.3032
Load_TR5_F4_8 | customer | 0.1743 | 0.0768 | 0.049 | 0.0908 | 0.1604 | 0.049 | 0.2021 | 0.049 | 0.0838 | 0.1673 | 0.049 | 0.2021 | 0.2364 | 0.1673 | 0.1292 | 0.2364 | 0.7858 | 0.1812 | 0.9941 | 0.054 | 0.205 | 0.0627 | 0.6707 | 0.4439 | 1.6145 | 0.071 | 0.2103 | 0.3042 | 0.0905 | 0.2278 | 0.049 | 0.049 | 0.0786 | 0.202 | 1.5383 | 0.1029 | 0.2461 | 0.2184 | 0.0674 | 0.2147 | 0.049 | 0.049 | 0.049 | 0.2021 | 0.049 | 0.0908 | 0.1604 | 0.049
Load_TR5_F4_80 | customer | 0.1376 | 0.1288 | 0.3217 | 0.0934 | 0.198 | 0.2083 | 0.1226 | 0.328 | 0.1155 | 0.1179 | 0.2077 | 0.1873 | 0.1774 | 0.2732 | 0.049 | 0.1463 | 0.1606 | 0.1499 | 0.384 | 0.4024 | 0.049 | 0.2978 | 0.1528 | 0.1287 | 0.3218 | 0.049 | 0.3217 | 0.1288 | 0.0785 | 1.1039 | 0.53 | 0.2375 | 0.147 | 0.2592 | 0.2157 | 0.1514 | 0.3692 | 0.4014 | 0.3686 | 0.3927 | 0.4473 | 0.5524 | 0.287 | 0.2244 | 0.1463 | 0.1775 | 0.2592 | 0.1187
Load_TR5_F4_81 | customer | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.06 | 0.0899 | 0.163 | 0.0591 | 0.2877 | 0.0905 | 0.6387 | 0.6794 | 0.9458 | 0.1676 | 0.2268 | 2.8895 | 2.4637 | 0.204 | 0.0889 | 0.095 | 0.2208 | 0.419 | 0.1311 | 0.1461 | 0.2022 | 0.1516 | 0.1879 | 0.0522 | 0.1281 | 0.2001 | 0.1955 | 0.1417 | 0.5705 | 0.4933 | 0.1941 | 0.045 | 0.0666 | 0.064 | 0.2125 | 0.3375 | 0.412
Load_TR5_F4_82 | prosumer | 0.2091 | 0.052 | 0.052 | 0.1448 | 0.1163 | 0.0806 | 0.1805 | 0.052 | 0.052 | 0.2091 | 0.052 | 0.052 | 0.2896 | 0.2305 | 0.052 | 0.1305 | 0.4018 | 1.4706 | 1.0982 | 0.2691 | 0.328 | 0.3136 | 0.1617 | 0.3498 | 0.0855 | 0.1838 | 0.2156 | 0.1096 | 0.256 | 0.0965 | 0.3434 | 0.3906 | 0.3079 | 0.4272 | 0.4269 | 0.3901 | 0.2666 | 0.4757 | 0.3066 | 0.4837 | 0.3702 | 0.4149 | 0.6143 | 0.4379 | 0.8896 | 0.5909 | 0.5924 | 0.1377
Load_TR5_F4_83 | prosumer | 0.2502 | 0.0812 | 0.057 | 0.3804 | 0.057 | 0.1814 | 0.2415 | 0.1248 | 0.3676 | 0.0715 | 0.1886 | 0.2488 | 0.0688 | 0.2663 | 1.6146 | 0.3621 | 1.6108 | 1.6425 | 0.8514 | 0.295 | 0.2546 | 1.2896 | 1.5985 | 0.7078 | 0.8469 | 1.6905 | 0.6134 | 0.4 | 0.146 | 0.524 | 0.2709 | 0.3697 | 0.2371 | 0.2151 | 0.2351 | 0.1862 | 1.7444 | 0.2355 | 0.1991 | 0.5013 | 0.5376 | 0.6308 | 0.3167 | 0.4452 | 0.4891 | 0.4082 | 0.633 | 0.5903
Load_TR5_F4_84 | prosumer | 0.048 | 0.048 | 0.199 | 0.0552 | 0.1919 | 0.2737 | 0.2215 | 0.048 | 0.1775 | 0.0768 | 0.1127 | 0.1415 | 0.048 | 0.1271 | 0.1271 | 0.0725 | 0.2088 | 0.0578 | 0.1415 | 0.1915 | 0.048 | 0.2062 | 0.048 | 0.0579 | 0.0745 | 0.2083 | 0.1446 | 0.1062 | 0.3185 | 0.1636 | 0.1532 | 0.1622 | 0.0784 | 0.1648 | 0.2754 | 0.4645 | 0.2361 | 0.5174 | 0.6009 | 0.1893 | 0.2141 | 0.2507 | 0.2183 | 0.2388 | 0.5387 | 0.3243 | 0.3726 | 0.048
Load_TR5_F4_85 | prosumer | 0.1736 | 0.079 | 0.0723 | 0.1803 | 0.052 | 0.1803 | 0.0723 | 0.079 | 0.1736 | 0.052 | 0.2006 | 0.052 | 1.1586 | 0.2515 | 0.0723 | 0.052 | 0.052 | 0.2006 | 0.052 | 0.1331 | 0.1195 | 0.0723 | 0.1803 | 0.052 | 0.2006 | 0.052 | 0.052 | 0.2006 | 0.052 | 0.1803 | 0.0723 | 0.0588 | 0.1938 | 0.052 | 0.1263 | 0.1263 | 0.052 | 0.2006 | 0.052 | 0.052 | 0.052 | 0.2006 | 0.052 | 0.1263 | 0.1263 | 0.052 | 0.052 | 0.2006
Load_TR5_F4_86 | customer | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.043 | 0.2503 | 0.0563 | 0.043 | 0.043 | 0.1514 | 0.8412 | 0.7811 | 0.0445 | 0.043 | 0.1031 | 0.0617 | 0.2839 | 0.8533 | 1.9292 | 0.2448 | 1.0383 | 0.7692 | 0.2979 | 0.0756 | 0.1516 | 0.3966 | 0.3258 | 0.1625 | 0.2583 | 0.3125 | 0.3268 | 0.4805 | 0.3311 | 0.3028 | 0.4056 | 0.3163 | 0.043
Load_TR5_F4_87 | customer | 0.2793 | 0.051 | 0.2135 | 0.1245 | 0.0654 | 0.1952 | 0.1283 | 0.2097 | 0.051 | 0.1197 | 0.2183 | 0.0725 | 0.1068 | 0.1493 | 0.1746 | 0.0684 | 0.1543 | 0.5492 | 1.6685 | 0.2918 | 0.4273 | 0.2542 | 0.2678 | 1.7167 | 1.218 | 0.9745 | 0.4179 | 0.1747 | 0.3841 | 0.2167 | 0.9833 | 0.4371 | 0.5058 | 0.4131 | 0.0632 | 0.1398 | 0.2161 | 0.0853 | 0.2397 | 0.1712 | 0.5876 | 0.2832 | 0.6451 | 0.3554 | 0.6087 | 0.3433 | 0.2765 | 0.5299
Load_TR5_F4_88 | prosumer | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.5192 | 1.5153 | 1.3561 | 0.1802 | 0.2232 | 0.4003 | 0.5148 | 1.2055 | 1.5289 | 0.3707 | 0.211 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.2142 | 0.2646 | 0.4164 | 0.5209 | 0.3373 | 0.4941 | 0.5537 | 0.8093 | 0.6119 | 1.0903 | 0.9392 | 0.4533
Load_TR5_F4_89 | prosumer | 0.044 | 0.044 | 0.044 | 0.1701 | 0.1784 | 0.077 | 0.2716 | 0.044 | 0.0825 | 0.2661 | 0.044 | 0.1564 | 0.1922 | 0.044 | 0.1056 | 0.133 | 0.1374 | 0.411 | 0.1372 | 0.1427 | 0.143 | 0.2358 | 0.0989 | 0.1876 | 0.3897 | 0.2667 | 0.3322 | 0.1264 | 0.0715 | 0.2661 | 0.0825 | 0.0989 | 0.2222 | 0.0714 | 0.044 | 0.1577 | 0.2297 | 0.1539 | 0.2638 | 0.3589 | 0.5777 | 0.4148 | 0.6542 | 0.7443 | 0.629 | 0.7133 | 0.7156 | 0.6493
Load_TR5_F4_9 | prosumer | 0.238 | 0.1647 | 0.1331 | 0.1597 | 0.0821 | 0.1163 | 0.16 | 0.1285 | 0.2081 | 0.1647 | 0.049 | 0.238 | 0.049 | 1.0872 | 0.4641 | 0.2784 | 0.2592 | 0.2686 | 0.1875 | 0.3369 | 0.2336 | 0.3029 | 0.2202 | 0.1107 | 0.1777 | 0.2065 | 0.3692 | 0.25 | 0.4071 | 0.295 | 0.1814 | 0.2536 | 0.1953 | 0.3237 | 0.2545 | 0.049 | 0.2533 | 0.0818 | 0.0962 | 0.6424 | 0.5716 | 0.5645 | 0.7884 | 0.8184 | 0.4111 | 0.0546 | 0.247 | 0.1501
Load_TR5_F4_90 | customer | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.0791 | 1.9011 | 0.2937 | 0.3105 | 0.2505 | 0.2475 | 0.2517 | 0.2367 | 1.2697 | 0.1178 | 0.1469 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.1755 | 1.7667 | 0.6794 | 0.1568 | 0.1159 | 0.1366 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052
Load_TR5_F4_91 | prosumer | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.083 | 0.1384 | 0.1369 | 0.1853 | 0.1261 | 0.056 | 1.394 | 0.1815 | 0.1285 | 0.1354 | 0.1991 | 0.54 | 0.8736 | 0.1662 | 0.0846 | 0.056 | 0.1941 | 0.3287 | 0.204 | 0.1648 | 0.3601 | 0.2678 | 0.5601 | 0.465 | 0.301 | 0.056 | 0.056 | 0.056 | 0.056 | 0.3047 | 0.4429
Load_TR5_F4_92 | customer | 0.326 | 0.3392 | 0.1538 | 0.3174 | 0.051 | 0.0681 | 0.2619 | 0.2036 | 0.1538 | 0.2354 | 0.1216 | 0.0902 | 0.381 | 0.051 | 0.1258 | 0.1808 | 0.2681 | 0.248 | 0.2039 | 0.1281 | 0.2569 | 0.1686 | 0.106 | 0.3653 | 0.051 | 0.3558 | 0.3405 | 0.5106 | 0.6078 | 0.3887 | 0.8306 | 0.555 | 0.4688 | 0.3721 | 0.0763 | 0.3404 | 0.1309 | 0.051 | 0.2172 | 0.254 | 0.051 | 0.1947 | 0.2608 | 0.0667 | 0.2804 | 0.1908 | 0.1256 | 0.3456
Load_TR5_F4_93 | prosumer | 0.1458 | 0.1396 | 0.1458 | 0.1252 | 0.1006 | 0.1126 | 0.053 | 0.1602 | 0.1252 | 0.0729 | 0.1981 | 0.0674 | 0.2324 | 0.053 | 0.1193 | 0.168 | 0.0555 | 0.1484 | 0.2378 | 0.3124 | 1.6102 | 1.1177 | 1.2406 | 0.1746 | 0.1107 | 0.0729 | 0.2263 | 0.2805 | 0.0626 | 0.1396 | 0.1458 | 0.1396 | 0.053 | 0.1458 | 0.053 | 0.2565 | 0.4337 | 0.4947 | 0.384 | 0.4052 | 0.4053 | 0.4537 | 0.5216 | 0.6453 | 0.9386 | 1.0846 | 0.6146 | 0.5508
Load_TR5_F4_94 | prosumer | 0.1344 | 0.1941 | 0.0787 | 0.1918 | 0.1654 | 0.0699 | 0.1653 | 0.172 | 0.05 | 0.2211 | 0.1362 | 0.0996 | 0.0996 | 0.05 | 0.1416 | 0.482 | 0.1921 | 0.3207 | 0.2014 | 0.2337 | 0.2423 | 0.0786 | 0.0553 | 0.2265 | 0.282 | 0.405 | 2.7645 | 2.2962 | 0.172 | 0.0859 | 0.05 | 0.4333 | 0.131 | 0.2812 | 0.5795 | 0.4778 | 1.8261 | 0.8334 | 1.4204 | 1.6361 | 0.4765 | 0.7509 | 0.6254 | 0.5312 | 0.5274 | 1.0229 | 0.05 | 0.0715
Load_TR5_F4_95 | prosumer | 0.051 | 0.0996 | 0.1552 | 0.051 | 0.2038 | 0.051 | 0.1691 | 0.0857 | 0.0857 | 0.1691 | 0.051 | 0.2038 | 0.051 | 0.15 | 0.1341 | 0.0706 | 0.4214 | 0.4061 | 0.6091 | 1.7343 | 1.4378 | 1.3511 | 0.2924 | 0.2688 | 0.2807 | 0.2291 | 0.4585 | 0.5051 | 1.6417 | 0.7489 | 0.2606 | 0.2171 | 2.4586 | 1.568 | 0.2604 | 0.0526 | 0.1983 | 0.3563 | 0.1005 | 0.3787 | 1.3591 | 1.2323 | 1.6769 | 0.4526 | 0.6832 | 0.4417 | 0.4545 | 0.1969
Load_TR5_F4_96 | prosumer | 0.049 | 0.049 | 0.1253 | 0.049 | 0.049 | 0.049 | 0.0956 | 0.0787 | 0.049 | 0.1253 | 0.049 | 0.049 | 0.049 | 0.049 | 0.1535 | 0.049 | 0.1253 | 0.049 | 0.0829 | 0.0914 | 0.049 | 0.049 | 0.049 | 0.1253 | 0.3776 | 0.3721 | 0.1472 | 0.0531 | 0.0805 | 0.0956 | 0.16 | 0.1796 | 0.1691 | 0.0871 | 0.0871 | 0.1083 | 0.0659 | 0.049 | 0.1083 | 0.0659 | 0.0829 | 0.0914 | 0.0659 | 0.1083 | 0.0829 | 0.1439 | 0.2947 | 0.1253
Load_TR5_F4_97 | customer | 0.0805 | 0.1166 | 0.058 | 0.058 | 0.058 | 0.1391 | 0.058 | 0.094 | 0.1031 | 0.058 | 0.058 | 0.058 | 0.058 | 0.085 | 0.1121 | 0.058 | 0.1391 | 0.058 | 0.1391 | 0.4029 | 0.88 | 1.3771 | 2.6699 | 1.4184 | 0.4593 | 0.1604 | 0.1501 | 0.0923 | 0.158 | 0.1069 | 0.1303 | 0.1529 | 0.2872 | 1.2107 | 0.1698 | 0.3561 | 0.2597 | 0.5491 | 0.4235 | 0.5749 | 0.5082 | 0.467 | 0.5229 | 0.8017 | 0.703 | 0.4433 | 0.2821 | 0.0625
Load_TR5_F4_98 | customer | 0.045 | 0.045 | 0.045 | 0.045 | 0.1544 | 0.1577 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.049 | 0.2292 | 0.1017 | 0.0734 | 0.057 | 0.1996 | 0.1666 | 0.2274 | 0.2567 | 0.1686 | 0.0695 | 0.134 | 1.0829 | 0.1163 | 0.1215 | 1.1184 | 0.8544 | 1.7868 | 0.3957 | 0.527 | 0.6848 | 0.5763 | 0.7255 | 0.6205 | 0.4336 | 0.045 | 0.045
Load_TR5_F4_99 | prosumer | 0.2444 | 0.3396 | 0.3352 | 0.2106 | 0.7025 | 0.0958 | 0.2017 | 0.1949 | 0.0866 | 0.164 | 0.1458 | 0.2315 | 0.0664 | 0.2984 | 0.133 | 0.2246 | 0.3021 | 0.1346 | 0.1039 | 0.2973 | 0.1341 | 0.2046 | 0.1684 | 0.3081 | 0.5225 | 0.313 | 1.2997 | 0.3944 | 0.2393 | 0.2201 | 0.2113 | 0.133 | 0.1581 | 0.2249 | 0.0954 | 0.1448 | 0.2866 | 0.047 | 0.2685 | 0.1628 | 0.1391 | 0.1406 | 0.0712 | 0.2567 | 0.1746 | 0.047 | 0.2973 | 0.047
Load_TR5_F5_1 | customer | 0.1103 | 0.06 | 0.267 | 0.0993 | 0.1543 | 0.2119 | 0.06 | 0.184 | 0.1822 | 0.0909 | 0.0987 | 0.2714 | 0.0948 | 0.0761 | 0.2283 | 0.1219 | 0.2045 | 0.1153 | 0.1064 | 0.2045 | 0.1617 | 0.06 | 0.1001 | 0.2351 | 0.1381 | 0.3484 | 2.3407 | 2.7231 | 3.1865 | 2.3878 | 0.4536 | 0.2229 | 0.06 | 0.25 | 0.1162 | 0.1778 | 0.1885 | 0.06 | 0.2366 | 0.1296 | 0.2281 | 0.5775 | 0.253 | 0.3114 | 0.7919 | 0.8517 | 0.4993 | 0.2806
Load_TR5_F5_10 | customer | 0.0812 | 0.1491 | 0.1499 | 0.137 | 0.0996 | 0.1749 | 0.0625 | 0.1549 | 0.1816 | 0.05 | 0.1491 | 0.1749 | 0.0625 | 0.1741 | 0.1624 | 0.1066 | 0.2298 | 0.05 | 0.1245 | 0.2363 | 0.077 | 0.4858 | 0.0579 | 0.1733 | 0.1632 | 0.05 | 0.2553 | 0.0812 | 0.0867 | 0.3413 | 0.1818 | 0.3064 | 0.1434 | 0.2714 | 1.4301 | 1.0857 | 3.225 | 2.8286 | 0.1505 | 0.8978 | 0.1928 | 0.05 | 0.0937 | 0.2428 | 0.05 | 0.135 | 1.0138 | 0.1114
Load_TR5_F5_10_dup | prosumer | 0.202 | 0.0639 | 0.1886 | 0.05 | 0.1609 | 0.0916 | 0.05 | 0.2025 | 0.05 | 0.147 | 0.1088 | 0.05 | 0.2025 | 0.05 | 0.05 | 0.1817 | 0.0708 | 0.05 | 0.2025 | 0.05 | 0.05 | 0.0585 | 0.4455 | 0.0508 | 0.1813 | 0.1195 | 0.2511 | 0.3142 | 1.5485 | 1.3025 | 0.7467 | 0.1898 | 0.3805 | 0.3283 | 0.2674 | 0.2337 | 0.3076 | 0.2627 | 0.5499 | 0.3237 | 0.4525 | 0.2798 | 0.1054 | 0.147 | 0.05 | 0.147 | 0.1054 | 0.05
Load_TR5_F5_11 | prosumer | 0.2752 | 0.058 | 0.3241 | 0.1353 | 0.1254 | 0.223 | 0.0913 | 0.3682 | 0.058 | 0.1764 | 0.2106 | 0.1306 | 0.1815 | 0.2313 | 0.1192 | 0.2313 | 0.3653 | 0.5515 | 1.3496 | 2.7223 | 2.7548 | 0.0819 | 1.1714 | 3.0089 | 0.281 | 0.491 | 0.3385 | 0.4117 | 0.3394 | 1.4451 | 0.4354 | 0.4909 | 0.3841 | 0.4009 | 0.6214 | 1.8131 | 0.4253 | 0.453 | 1.1866 | 0.373 | 0.5056 | 2.0979 | 1.3054 | 0.6352 | 0.225 | 0.2951 | 0.1368 | 0.1422
Load_TR5_F5_11_dup | prosumer | 0.4409 | 0.6433 | 0.6647 | 0.6793 | 0.3591 | 0.137 | 0.0896 | 0.296 | 0.137 | 0.2389 | 0.1682 | 0.1464 | 0.2399 | 0.1148 | 0.2452 | 0.051 | 0.222 | 0.0981 | 0.7339 | 0.9776 | 0.4562 | 0.3242 | 0.2388 | 1.0933 | 0.3 | 0.3514 | 0.1092 | 2.0739 | 0.3011 | 0.3951 | 0.13 | 0.1865 | 0.3781 | 0.5165 | 2.8077 | 2.5779 | 0.4291 | 0.7047 | 0.3088 | 0.4463 | 0.6032 | 0.5105 | 0.5632 | 0.3603 | 0.2301 | 0.3614 | 0.2504 | 0.1592
Load_TR5_F5_12 | prosumer | 0.2011 | 0.2092 | 0.05 | 0.2514 | 0.2946 | 0.066 | 0.341 | 0.189 | 0.3161 | 0.2299 | 0.0739 | 0.3489 | 0.209 | 0.2066 | 0.3433 | 0.0819 | 0.2255 | 0.1852 | 0.1853 | 0.2773 | 0.1588 | 0.2157 | 0.2334 | 0.0849 | 0.2928 | 0.1095 | 0.2735 | 0.5556 | 0.2036 | 0.38 | 0.2095 | 0.0761 | 0.2226 | 0.238 | 0.6768 | 1.3549 | 0.5686 | 0.4247 | 0.3512 | 0.6894 | 0.6696 | 0.9699 | 0.6543 | 0.7848 | 0.7403 | 0.6661 | 0.2413 | 0.0979
Load_TR5_F5_12_dup | prosumer | 0.049 | 0.1301 | 0.049 | 0.049 | 0.1301 | 0.049 | 0.049 | 0.049 | 0.049 | 0.1301 | 0.049 | 0.049 | 0.049 | 0.049 | 0.076 | 0.1031 | 0.049 | 0.0545 | 0.2581 | 0.213 | 0.1005 | 0.2811 | 0.2425 | 0.1894 | 0.1076 | 0.8626 | 0.804 | 1.7196 | 0.049 | 0.0535 | 0.2531 | 0.2672 | 0.2663 | 0.2146 | 0.1997 | 0.1386 | 0.0624 | 0.1661 | 0.1518 | 0.4245 | 1.631 | 1.5912 | 0.6136 | 0.479 | 0.3261 | 0.2234 | 0.2582 | 0.1723
Load_TR5_F5_13 | prosumer | 0.0831 | 0.076 | 0.0902 | 0.0846 | 0.2044 | 0.076 | 0.076 | 0.191 | 0.098 | 0.0831 | 0.2309 | 0.051 | 0.1652 | 0.1488 | 0.0712 | 0.1786 | 0.051 | 0.2159 | 0.3273 | 0.2034 | 0.1324 | 0.1009 | 0.213 | 0.051 | 0.1152 | 0.0913 | 0.2226 | 0.1303 | 0.1946 | 0.1528 | 0.051 | 0.1585 | 0.0913 | 0.1047 | 0.2092 | 0.0546 | 0.1922 | 0.2076 | 0.3956 | 0.6597 | 0.6714 | 0.394 | 0.631 | 0.4464 | 0.6568 | 0.5912 | 0.549 | 0.2313
Load_TR5_F5_13_dup | customer | 0.1248 | 0.1192 | 0.138 | 0.0581 | 0.13 | 0.1728 | 0.1161 | 0.1784 | 0.1161 | 0.054 | 0.2405 | 0.054 | 0.2239 | 0.0706 | 0.0932 | 0.2013 | 0.082 | 0.138 | 0.054 | 0.2123 | 0.4092 | 1.6801 | 0.2962 | 1.8505 | 0.5686 | 0.2632 | 0.0932 | 0.3894 | 0.0616 | 0.201 | 0.3359 | 0.2268 | 0.6528 | 3.255 | 3.8487 | 0.6859 | 0.3256 | 0.3864 | 0.6253 | 0.3839 | 2.2046 | 0.6525 | 0.6079 | 0.6051 | 0.4286 | 0.2112 | 0.0693 | 0.4614
Load_TR5_F5_14 | prosumer | 0.2572 | 0.1338 | 0.2275 | 0.2325 | 0.2198 | 0.0667 | 0.158 | 0.1335 | 0.2882 | 0.1718 | 0.1203 | 0.2992 | 0.1741 | 0.2452 | 0.1444 | 0.137 | 0.4853 | 0.1339 | 0.1883 | 2.4019 | 0.1991 | 0.4037 | 0.4172 | 0.4209 | 1.604 | 0.3209 | 0.4287 | 0.4453 | 0.0727 | 0.3567 | 0.2279 | 0.3004 | 2.2215 | 2.994 | 1.2104 | 0.3258 | 0.2056 | 0.2051 | 1.3044 | 0.535 | 0.7111 | 0.7845 | 0.7002 | 0.9448 | 0.7264 | 0.8549 | 0.1971 | 0.1126
Load_TR5_F5_14_dup | customer | 0.5554 | 0.3003 | 0.3098 | 0.4541 | 0.1821 | 0.0996 | 0.1585 | 0.1453 | 0.2101 | 0.1383 | 0.1434 | 0.1217 | 0.1453 | 0.2101 | 0.2786 | 0.1632 | 0.2279 | 0.0748 | 0.1895 | 0.1659 | 0.1453 | 0.048 | 0.1175 | 0.0758 | 0.2101 | 0.1453 | 0.048 | 0.0897 | 0.2657 | 0.048 | 0.3682 | 0.2611 | 0.2668 | 0.405 | 0.4344 | 0.3511 | 0.4187 | 0.4263 | 0.4758 | 0.7672 | 0.3863 | 0.5228 | 0.5176 | 0.7765 | 0.584 | 0.4003 | 0.2101 | 0.048
Load_TR5_F5_15 | prosumer | 0.1117 | 0.1945 | 0.059 | 0.0894 | 0.2424 | 0.0726 | 0.12 | 0.1515 | 0.1329 | 0.2081 | 0.1112 | 0.1935 | 0.1779 | 0.059 | 0.1373 | 0.3771 | 0.3184 | 0.1689 | 0.1911 | 0.1068 | 0.2405 | 0.1049 | 0.0894 | 0.2559 | 0.1229 | 0.4044 | 0.104 | 0.1112 | 0.119 | 0.1742 | 0.1373 | 0.2013 | 0.1491 | 0.2562 | 0.4602 | 2.5038 | 2.2337 | 1.7839 | 0.059 | 0.1607 | 0.1064 | 0.1373 | 0.2454 | 0.5737 | 1.0248 | 0.813 | 0.1373 | 0.2081
Load_TR5_F5_15_dup | customer | 2.01 | 1.5163 | 1.1188 | 0.3927 | 0.046 | 0.1757 | 0.0947 | 0.2238 | 0.1433 | 0.113 | 0.2542 | 0.046 | 0.1337 | 0.2334 | 0.046 | 0.261 | 0.3931 | 0.0905 | 0.2806 | 0.046 | 0.046 | 0.351 | 0.0594 | 0.0998 | 0.2352 | 0.4418 | 0.2325 | 0.1687 | 0.3426 | 0.5823 | 0.2114 | 0.2075 | 0.1888 | 0.308 | 0.3459 | 0.3722 | 0.0901 | 1.3821 | 0.6847 | 0.3782 | 0.4273 | 0.4013 | 0.3664 | 0.4493 | 0.2935 | 0.3343 | 0.2244 | 0.1427
Load_TR5_F5_16 | customer | 0.106 | 0.0928 | 0.1042 | 0.2225 | 0.0928 | 0.0818 | 0.2001 | 0.048 | 0.2419 | 0.1071 | 0.048 | 0.3011 | 0.048 | 0.1409 | 1.0852 | 0.6497 | 1.0244 | 0.35 | 0.048 | 0.1663 | 0.1156 | 1.0717 | 1.6559 | 2.3769 | 1.5037 | 0.1435 | 1.3555 | 0.124 | 0.2176 | 0.0555 | 0.1494 | 0.1437 | 0.1804 | 0.6536 | 0.4899 | 0.3867 | 0.069 | 0.3273 | 0.1265 | 0.3029 | 0.3283 | 0.405 | 0.9019 | 0.5911 | 1.054 | 0.6666 | 0.3452 | 0.9233
Load_TR5_F5_16_dup | customer | 0.1669 | 0.1813 | 0.1905 | 0.1027 | 0.2489 | 0.0522 | 0.1724 | 0.1995 | 0.032 | 0.1499 | 0.222 | 0.032 | 0.2534 | 0.1185 | 0.1596 | 0.3558 | 0.1244 | 0.0767 | 0.3309 | 0.9259 | 1.1574 | 3.3492 | 1.8591 | 0.0951 | 0.3241 | 0.0469 | 1.9778 | 0.5243 | 0.1613 | 0.2703 | 0.2832 | 0.2975 | 0.2202 | 0.0775 | 0.5564 | 0.1525 | 0.2291 | 0.1861 | 0.2396 | 0.4036 | 0.3704 | 0.7146 | 0.431 | 0.5869 | 0.5673 | 0.4435 | 0.4233 | 0.6206
Load_TR5_F5_17 | prosumer | 0.178 | 0.2006 | 0.0906 | 0.3618 | 0.1673 | 0.051 | 0.2943 | 0.1175 | 0.137 | 0.2748 | 0.051 | 0.0827 | 0.3124 | 0.1154 | 0.4071 | 0.2494 | 0.2094 | 0.111 | 0.1796 | 0.2693 | 0.3674 | 0.1873 | 0.4985 | 0.3272 | 0.466 | 0.2204 | 0.4638 | 0.2092 | 0.3781 | 0.4645 | 0.6152 | 0.7481 | 0.3937 | 0.302 | 0.7622 | 0.264 | 0.3752 | 0.3969 | 0.2851 | 0.2172 | 0.1946 | 0.1341 | 0.2523 | 0.0764 | 0.1258 | 0.2669 | 0.07 | 0.07
Load_TR5_F5_17_dup | prosumer | 0.0595 | 0.04 | 0.04 | 0.04 | 0.1506 | 0.0725 | 0.079 | 0.1441 | 0.04 | 0.1441 | 0.079 | 0.092 | 0.1311 | 0.04 | 0.301 | 0.4034 | 1.339 | 0.2214 | 0.1171 | 0.2581 | 1.7691 | 0.2637 | 0.0587 | 0.2018 | 0.0453 | 0.0787 | 0.1896 | 0.1443 | 0.3199 | 0.1208 | 0.0777 | 0.2435 | 1.1143 | 0.2523 | 3.3554 | 0.1098 | 0.2583 | 0.2273 | 1.4793 | 0.4631 | 0.1116 | 0.0969 | 0.2879 | 0.2323 | 0.2075 | 0.2063 | 0.04 | 0.1766
Load_TR5_F5_18 | customer | 0.3124 | 0.055 | 0.055 | 0.1899 | 0.085 | 0.1449 | 0.1299 | 0.055 | 0.2198 | 0.055 | 0.1524 | 0.1224 | 0.055 | 0.1899 | 0.1147 | 0.2492 | 0.2922 | 0.1399 | 0.2886 | 0.1585 | 0.293 | 0.1001 | 0.1954 | 0.9332 | 0.1475 | 0.1551 | 0.1749 | 0.0891 | 0.3149 | 0.1648 | 0.2227 | 0.1028 | 0.3522 | 0.4296 | 0.3384 | 0.2777 | 0.2856 | 0.3361 | 0.3128 | 0.4098 | 0.7265 | 0.3832 | 0.764 | 0.4222 | 0.5177 | 0.7216 | 0.5671 | 0.2274
Load_TR5_F5_18_dup | customer | 0.3258 | 0.1212 | 0.044 | 0.3211 | 0.044 | 0.1803 | 0.1119 | 0.1169 | 0.1985 | 0.1323 | 0.0783 | 0.1217 | 0.2434 | 0.0803 | 0.2363 | 0.1473 | 0.1825 | 0.1987 | 1.5251 | 0.2416 | 0.4094 | 0.4413 | 1.465 | 1.2962 | 0.7445 | 0.2439 | 0.044 | 0.0483 | 0.3168 | 0.044 | 0.2939 | 0.0713 | 0.203 | 0.2293 | 0.2409 | 0.143 | 0.5131 | 0.2023 | 0.2626 | 0.2061 | 0.3588 | 1.465 | 1.2156 | 0.5374 | 0.3748 | 0.712 | 0.5504 | 0.6041
Load_TR5_F5_19 | prosumer | 0.098 | 0.043 | 0.2922 | 0.0605 | 0.1045 | 0.214 | 0.2001 | 0.0498 | 0.2479 | 0.1765 | 0.2308 | 0.0498 | 0.1454 | 0.2072 | 0.1318 | 0.3448 | 0.3906 | 1.086 | 0.8529 | 1.2131 | 0.2706 | 0.5437 | 0.7316 | 0.4045 | 0.4192 | 1.4224 | 0.3748 | 0.5304 | 0.7186 | 0.4938 | 0.1432 | 0.5112 | 1.0251 | 1.3989 | 0.2113 | 0.0617 | 0.3244 | 0.3908 | 0.1623 | 0.3295 | 0.7291 | 0.6129 | 0.6007 | 0.5413 | 0.3499 | 0.5346 | 0.322 | 0.5838
Load_TR5_F5_19_dup | prosumer | 0.0592 | 0.1239 | 0.05 | 0.05 | 0.1728 | 0.1786 | 0.05 | 0.1332 | 0.05 | 0.1332 | 0.05 | 0.1147 | 0.0685 | 0.1101 | 0.0731 | 0.1332 | 0.05 | 0.0916 | 0.0916 | 0.3608 | 0.1861 | 0.1992 | 0.1637 | 0.0614 | 0.1487 | 0.2893 | 0.9825 | 0.1975 | 0.05 | 0.1332 | 0.05 | 0.05 | 0.1147 | 0.0685 | 0.1101 | 0.0731 | 0.0535 | 0.1494 | 0.1071 | 0.2184 | 0.087 | 0.05 | 0.1101 | 0.0731 | 0.1332 | 0.0736 | 0.2851 | 0.5839
Load_TR5_F5_1_dup | prosumer | 0.1979 | 0.2297 | 0.2523 | 0.2416 | 0.2829 | 0.1785 | 0.1712 | 0.1818 | 0.2825 | 0.0727 | 0.3199 | 0.2223 | 0.0637 | 0.3333 | 0.3621 | 0.3734 | 0.4717 | 1.7831 | 1.6713 | 1.074 | 1.9122 | 0.4463 | 0.6025 | 1.117 | 1.4914 | 2.6817 | 2.3395 | 0.5998 | 0.1894 | 0.5916 | 0.5341 | 0.8431 | 0.5277 | 0.6127 | 1.0442 | 1.319 | 2.0217 | 0.6095 | 0.3241 | 0.889 | 0.4616 | 0.6149 | 0.5445 | 2.7644 | 0.7887 | 0.4648 | 0.6738 | 0.1435
Load_TR5_F5_2 | customer | 0.1943 | 0.1692 | 0.06 | 0.1765 | 0.1037 | 0.1037 | 0.1765 | 0.06 | 0.2202 | 0.06 | 0.185 | 0.1238 | 0.1388 | 0.1542 | 0.2157 | 1.6762 | 0.3265 | 0.0849 | 0.1756 | 0.1142 | 0.1037 | 0.1765 | 0.06 | 0.2202 | 0.06 | 0.111 | 0.1692 | 0.06 | 0.2202 | 0.06 | 0.06 | 0.1182 | 0.1619 | 0.0746 | 0.2056 | 0.06 | 0.1692 | 0.1417 | 0.3783 | 0.2921 | 0.2134 | 0.6788 | 0.4592 | 2.0389 | 0.06 | 0.1547 | 0.1255 | 0.1037
Load_TR5_F5_20 | customer | 0.2492 | 0.4231 | 0.4704 | 0.297 | 0.4041 | 0.1941 | 0.2553 | 0.1589 | 0.1696 | 0.2027 | 0.0854 | 0.0974 | 0.1944 | 0.1185 | 0.2585 | 0.057 | 0.0664 | 0.3435 | 0.2147 | 0.3782 | 0.4266 | 1.0683 | 0.5219 | 0.3389 | 0.5009 | 0.2584 | 0.1691 | 0.2634 | 0.057 | 0.6442 | 0.3201 | 0.2253 | 0.1357 | 0.3794 | 0.2371 | 0.1502 | 0.1783 | 0.1215 | 0.109 | 0.2437 | 0.0813 | 0.0732 | 0.3039 | 0.057 | 0.1378 | 0.154 | 0.057 | 0.32
Load_TR5_F5_20_dup | prosumer | 0.0549 | 0.1151 | 0.1959 | 0.0753 | 0.1168 | 0.1501 | 0.1194 | 0.2249 | 0.1151 | 0.0463 | 0.1168 | 0.2274 | 0.042 | 1.0285 | 0.042 | 0.1423 | 0.2019 | 0.0463 | 0.2979 | 0.042 | 0.8804 | 0.0798 | 0.2145 | 0.1168 | 1.6646 | 1.1757 | 3.2997 | 2.541 | 1.2438 | 1.5634 | 0.1749 | 0.6995 | 0.9257 | 0.3406 | 0.36 | 0.2959 | 0.1229 | 0.2238 | 0.3934 | 0.673 | 0.5013 | 0.4607 | 0.5408 | 0.7808 | 0.9093 | 0.642 | 0.7049 | 0.3885
Load_TR5_F5_21 | customer | 0.2261 | 0.1183 | 0.2179 | 0.206 | 0.2014 | 0.1549 | 0.1579 | 0.2681 | 0.1372 | 0.1713 | 0.2893 | 0.2171 | 0.1549 | 0.5861 | 0.2669 | 0.3167 | 0.5327 | 0.1036 | 0.2623 | 0.1685 | 0.1875 | 0.2331 | 0.828 | 0.6723 | 0.3521 | 0.056 | 0.3769 | 0.1295 | 0.1459 | 0.1684 | 0.1318 | 0.3498 | 0.1565 | 0.1903 | 0.2535 | 0.1185 | 0.1158 | 0.3281 | 0.1185 | 0.2573 | 0.249 | 0.056 | 0.2581 | 0.1437 | 0.1606 | 0.065 | 0.3744 | 0.1229
Load_TR5_F5_21_dup | prosumer | 0.1502 | 0.1766 | 0.2127 | 0.1841 | 0.1451 | 0.1301 | 0.1766 | 0.2202 | 0.1412 | 0.1766 | 0.055 | 0.2327 | 0.1641 | 0.1226 | 0.1526 | 0.134 | 0.2402 | 0.2741 | 0.2325 | 0.1121 | 0.1828 | 0.2883 | 1.9101 | 0.4073 | 0.2228 | 0.5207 | 1.5341 | 0.4343 | 0.5523 | 0.199 | 0.1097 | 0.1219 | 0.1902 | 0.085 | 0.1916 | 0.2052 | 0.055 | 0.1766 | 0.2202 | 0.055 | 0.1734 | 0.2234 | 0.0976 | 0.1641 | 0.1902 | 0.1766 | 0.2202 | 0.055
Load_TR5_F5_22 | customer | 0.1423 | 0.2444 | 0.049 | 0.2696 | 0.0581 | 0.1221 | 0.2696 | 0.0947 | 0.0855 | 0.049 | 0.3518 | 0.049 | 0.1122 | 0.2065 | 0.1312 | 0.1448 | 0.4506 | 0.2928 | 0.328 | 0.3248 | 0.2101 | 0.5292 | 0.7204 | 0.96 | 0.3537 | 0.1476 | 0.2294 | 0.1714 | 0.1312 | 0.2362 | 0.1646 | 0.1472 | 0.0627 | 0.1315 | 0.5279 | 0.1581 | 0.2658 | 0.2185 | 0.8513 | 1.7079 | 0.4079 | 0.5628 | 0.8177 | 0.5989 | 1.0574 | 1.0192 | 0.447 | 0.2042
Load_TR5_F5_22_dup | prosumer | 0.1928 | 0.05 | 0.05 | 0.05 | 0.1019 | 0.1408 | 0.0565 | 0.1863 | 0.05 | 0.1928 | 0.05 | 0.1084 | 0.1344 | 0.063 | 0.1798 | 0.05 | 0.05 | 0.1928 | 0.252 | 0.05 | 0.4208 | 0.1934 | 0.4248 | 0.3224 | 0.102 | 0.1344 | 0.1084 | 0.05 | 0.1473 | 0.0954 | 0.0954 | 0.1473 | 0.05 | 0.1928 | 0.2173 | 0.2218 | 0.0824 | 0.05 | 0.063 | 0.1798 | 0.05 | 0.1863 | 0.0565 | 0.05 | 0.1473 | 0.0954 | 0.05 | 0.1928
Load_TR5_F5_23 | prosumer | 0.1062 | 0.1692 | 0.1342 | 0.051 | 0.1342 | 0.1377 | 0.2209 | 0.051 | 0.1298 | 0.2288 | 0.0766 | 0.2219 | 0.0601 | 0.2478 | 0.1247 | 0.1157 | 0.051 | 0.2244 | 0.051 | 0.2008 | 0.0746 | 0.1456 | 0.1298 | 0.0741 | 0.2451 | 0.0904 | 0.051 | 0.157 | 0.2016 | 0.0741 | 0.2732 | 0.2891 | 0.2191 | 0.5266 | 0.4128 | 0.481 | 0.2423 | 0.2171 | 0.2016 | 0.4007 | 0.4172 | 0.4559 | 0.3497 | 0.341 | 0.1298 | 0.1342 | 0.2244 | 0.051
Load_TR5_F5_23_dup | prosumer | 0.168 | 0.1534 | 0.258 | 0.048 | 0.2884 | 0.048 | 0.048 | 0.1163 | 0.1466 | 0.1299 | 0.5308 | 0.048 | 0.1215 | 0.219 | 0.1174 | 0.2149 | 0.2319 | 1.0138 | 0.4374 | 0.1705 | 0.2761 | 0.0807 | 0.2119 | 0.3278 | 0.274 | 1.066 | 1.7481 | 0.2599 | 0.1231 | 0.2149 | 0.1215 | 0.1466 | 0.1448 | 0.0929 | 0.048 | 0.2884 | 0.215 | 0.3018 | 0.4263 | 0.5276 | 0.6883 | 0.585 | 0.713 | 0.5029 | 0.5897 | 0.1969 | 0.1215 | 0.2149
Load_TR5_F5_24 | prosumer | 0.2002 | 0.051 | 0.1053 | 0.146 | 0.051 | 0.2002 | 0.051 | 0.1799 | 0.0713 | 0.0646 | 0.1867 | 0.051 | 0.1527 | 0.0985 | 0.051 | 0.2104 | 0.2529 | 0.1342 | 0.9534 | 2.7604 | 2.643 | 1.6825 | 1.4342 | 0.9421 | 1.2602 | 0.5304 | 0.2712 | 1.1947 | 0.5483 | 0.1663 | 0.051 | 0.1053 | 0.146 | 0.051 | 0.2002 | 0.051 | 0.1731 | 0.0781 | 0.0849 | 0.1663 | 0.051 | 0.112 | 0.1392 | 0.051 | 0.2002 | 0.051 | 0.1934 | 0.0578
Load_TR5_F5_24_dup | customer | 0.1812 | 0.094 | 0.053 | 0.053 | 0.1457 | 0.1784 | 0.0872 | 0.2368 | 0.3685 | 0.2149 | 0.2485 | 0.0943 | 0.134 | 0.1835 | 0.0977 | 0.2372 | 0.0868 | 0.068 | 0.1056 | 0.1761 | 0.3557 | 0.8156 | 0.7791 | 1.3357 | 0.3817 | 0.0824 | 0.053 | 0.1077 | 0.1788 | 0.0906 | 0.0735 | 0.1829 | 0.053 | 0.053 | 0.2635 | 0.0605 | 0.1477 | 0.1764 | 0.0804 | 0.2437 | 0.053 | 0.1206 | 0.1282 | 0.2433 | 0.0667 | 0.1898 | 0.1206 | 0.053
Load_TR5_F5_25 | customer | 0.125 | 0.3219 | 0.0532 | 0.1607 | 0.258 | 0.3189 | 0.1606 | 0.198 | 0.1327 | 0.0654 | 0.1538 | 0.349 | 0.1897 | 0.1443 | 0.1699 | 0.2118 | 0.1184 | 1.2139 | 0.089 | 0.3817 | 0.5662 | 1.755 | 0.3934 | 0.0457 | 0.1184 | 0.1607 | 1.8294 | 0.5928 | 0.0629 | 0.2673 | 0.1971 | 0.0798 | 0.2158 | 0.1702 | 0.3615 | 0.064 | 0.3306 | 0.5215 | 0.1184 | 1.0967 | 0.1143 | 0.117 | 0.2224 | 0.061 | 0.223 | 0.216 | 0.085 | 0.1892
Load_TR5_F5_25_dup | customer | 0.3155 | 0.2856 | 0.1826 | 0.051 | 0.1563 | 0.0773 | 0.051 | 0.176 | 0.0576 | 0.051 | 0.051 | 0.051 | 0.1299 | 0.1036 | 0.051 | 0.0775 | 0.1497 | 0.0839 | 0.1168 | 0.1778 | 0.2013 | 0.2233 | 0.2797 | 0.6797 | 1.1326 | 0.2343 | 0.2488 | 0.4601 | 1.1447 | 0.4182 | 0.2809 | 0.252 | 0.1972 | 0.0813 | 0.2645 | 0.0912 | 0.1227 | 0.4487 | 0.0829 | 1.3236 | 0.2743 | 0.316 | 0.5092 | 0.3299 | 1.8238 | 0.4567 | 0.4997 | 0.2536
Load_TR5_F5_26 | prosumer | 0.1153 | 0.4443 | 0.3577 | 0.0866 | 0.2102 | 0.1092 | 0.0839 | 0.1677 | 0.1167 | 0.2026 | 0.049 | 0.1446 | 0.1747 | 0.049 | 1.3867 | 0.1607 | 0.0979 | 0.2214 | 0.049 | 0.049 | 0.1611 | 0.282 | 0.4126 | 0.3187 | 2.3402 | 0.4133 | 0.2512 | 0.3364 | 0.2504 | 0.2386 | 0.1913 | 0.049 | 0.2026 | 0.1167 | 0.1887 | 1.7584 | 0.2468 | 0.1917 | 0.0999 | 1.4742 | 0.6111 | 0.2943 | 0.6868 | 0.5842 | 0.2964 | 0.3815 | 0.0866 | 0.2188
Load_TR5_F5_26_dup | customer | 0.3282 | 0.1475 | 0.1648 | 0.1441 | 0.3179 | 0.1578 | 0.2155 | 0.2602 | 0.1294 | 0.2107 | 0.1 | 0.2944 | 0.1711 | 0.046 | 0.1711 | 0.2865 | 0.3504 | 0.3966 | 0.2315 | 0.1523 | 0.1673 | 0.5371 | 0.0557 | 0.2027 | 0.5699 | 0.046 | 0.2628 | 0.2003 | 0.1422 | 0.3246 | 1.4739 | 1.274 | 0.9143 | 0.1446 | 0.2882 | 0.1972 | 0.269 | 0.2675 | 0.16 | 0.5056 | 0.3156 | 0.6068 | 0.394 | 0.3317 | 0.531 | 0.6483 | 0.2378 | 0.046
Load_TR5_F5_27 | prosumer | 0.041 | 0.1923 | 0.041 | 0.096 | 0.1373 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.1442 | 0.0891 | 0.041 | 0.1648 | 0.0821 | 0.0867 | 0.1808 | 0.2437 | 0.151 | 0.0823 | 0.0754 | 0.1579 | 0.041 | 0.1923 | 0.041 | 0.1717 | 0.0616 | 0.041 | 0.1923 | 0.041 | 0.0479 | 0.2028 | 0.2437 | 0.1334 | 0.1029 | 0.0548 | 2.0851 | 0.1773 | 0.7481 | 0.9131 | 0.4279 | 0.041 | 0.1923 | 0.041 | 0.1373 | 0.096 | 0.0616 | 0.1717
Load_TR5_F5_27_dup | customer | 0.05 | 0.0949 | 0.0949 | 0.05 | 0.1399 | 0.05 | 0.05 | 0.1399 | 0.05 | 0.06 | 0.1299 | 0.075 | 0.1149 | 0.05 | 0.1049 | 0.085 | 0.05 | 0.1399 | 0.05 | 0.07 | 0.1199 | 0.06 | 0.1299 | 0.08 | 0.1099 | 0.05 | 0.065 | 0.1249 | 0.05 | 0.1399 | 0.2075 | 0.3556 | 0.276 | 0.276 | 0.2049 | 1.6234 | 0.1197 | 0.1247 | 0.1334 | 0.3855 | 0.5627 | 0.4774 | 0.5542 | 0.6603 | 1.4868 | 0.07 | 0.1199 | 0.05
Load_TR5_F5_28 | prosumer | 0.4104 | 0.1769 | 0.0887 | 0.052 | 0.1769 | 0.0887 | 0.052 | 0.1622 | 0.1034 | 0.1181 | 0.1475 | 0.052 | 0.1769 | 0.0887 | 0.0616 | 0.0608 | 0.2962 | 0.1482 | 0.2616 | 0.7737 | 0.5057 | 0.4126 | 1.2857 | 0.4703 | 0.4581 | 0.1014 | 0.2729 | 0.429 | 0.199 | 0.052 | 0.2063 | 0.8133 | 1.645 | 0.2485 | 0.1782 | 0.149 | 0.077 | 0.2066 | 0.052 | 0.1769 | 0.0887 | 0.1255 | 0.1402 | 0.052 | 0.2136 | 0.052 | 0.4307 | 0.7567
Load_TR5_F5_28_dup | customer | 0.1225 | 0.1732 | 0.055 | 0.055 | 0.2407 | 0.055 | 0.0803 | 0.2154 | 0.055 | 0.055 | 0.2407 | 0.4263 | 0.2686 | 0.5726 | 0.4316 | 0.193 | 0.4769 | 0.1944 | 1.7142 | 0.363 | 0.255 | 0.5193 | 0.055 | 0.2407 | 0.055 | 0.1141 | 0.1816 | 0.055 | 0.2323 | 0.0634 | 0.0888 | 0.207 | 0.055 | 0.1394 | 0.1563 | 0.055 | 0.4476 | 0.1862 | 0.4807 | 0.4502 | 0.7055 | 0.8659 | 0.5759 | 0.5396 | 0.4763 | 0.5901 | 0.2859 | 0.1816
Load_TR5_F5_29 | prosumer | 0.2125 | 0.1055 | 0.3444 | 0.1609 | 0.2503 | 0.2057 | 0.1398 | 0.2717 | 0.2293 | 0.1611 | 0.3648 | 0.1348 | 0.2838 | 0.2371 | 0.4502 | 0.482 | 1.286 | 1.4774 | 0.4378 | 0.5316 | 1.1585 | 2.1421 | 1.3411 | 0.2584 | 1.3827 | 0.9833 | 1.4385 | 0.2273 | 0.1606 | 0.2777 | 1.0687 | 0.8232 | 0.2041 | 0.601 | 1.2829 | 1.783 | 0.596 | 0.3468 | 0.4104 | 0.6003 | 0.504 | 0.7192 | 0.8887 | 0.9528 | 0.9129 | 0.7395 | 0.5646 | 1.4496
Load_TR5_F5_29_dup | customer | 0.1658 | 0.2227 | 0.2087 | 0.1433 | 0.272 | 0.1658 | 0.2133 | 0.053 | 0.3466 | 0.382 | 0.1013 | 0.2839 | 0.2109 | 0.1497 | 0.3056 | 0.1904 | 0.2757 | 0.1332 | 0.1332 | 0.1768 | 0.3029 | 0.053 | 0.2222 | 0.2575 | 0.053 | 0.3608 | 0.1189 | 0.3187 | 0.3211 | 0.3237 | 0.2051 | 0.5032 | 0.5714 | 0.5626 | 0.1416 | 0.1123 | 0.3352 | 0.1514 | 0.3577 | 0.2053 | 0.5961 | 0.8847 | 0.7098 | 0.7661 | 2.2163 | 0.1259 | 0.3377 | 0.0691
Load_TR5_F5_2_dup | customer | 0.0524 | 0.2692 | 0.038 | 0.038 | 0.1969 | 0.1247 | 0.038 | 0.1247 | 0.1598 | 0.0752 | 0.038 | 0.1969 | 0.1185 | 0.2031 | 0.038 | 0.1753 | 0.1464 | 0.0442 | 0.1185 | 1.5196 | 0.038 | 0.1536 | 0.168 | 0.038 | 0.2837 | 0.038 | 0.0741 | 0.2476 | 0.038 | 0.103 | 0.4488 | 0.094 | 0.2305 | 0.2069 | 0.1928 | 0.1974 | 0.0996 | 0.1862 | 0.3958 | 0.217 | 0.237 | 0.2019 | 0.2116 | 0.3227 | 1.2214 | 0.3042 | 0.2707 | 0.1394
Load_TR5_F5_3 | customer | 0.054 | 0.2058 | 0.0612 | 0.1552 | 0.1118 | 0.0612 | 0.2058 | 0.054 | 0.2131 | 0.054 | 0.1408 | 0.1263 | 0.054 | 0.2449 | 0.0665 | 0.082 | 0.0558 | 0.2839 | 2.0941 | 0.0558 | 0.054 | 0.2211 | 0.067 | 0.1841 | 0.1266 | 0.0636 | 0.4962 | 0.2485 | 0.2289 | 0.2945 | 0.3296 | 0.2158 | 0.3585 | 0.22 | 0.2208 | 0.301 | 0.1408 | 0.054 | 0.494 | 0.393 | 0.359 | 0.4989 | 0.6185 | 0.49 | 0.6019 | 0.6115 | 0.7867 | 0.5229
Load_TR5_F5_30 | prosumer | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.4909 | 1.8134 | 0.7095 | 1.6692 | 0.1028 | 0.1182 | 1.4115 | 0.8384 | 0.7254 | 1.533 | 0.3607 | 0.8891 | 0.1045 | 0.3978 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.1601 | 0.5728 | 0.1869 | 0.046 | 0.046 | 0.046 | 0.046
Load_TR5_F5_30_dup | customer | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.0843 | 1.2632 | 0.3997 | 0.2224 | 0.0956 | 0.0593 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.0593 | 0.2144 | 1.41 | 0.4488 | 0.323 | 0.3741 | 0.2791 | 0.045 | 0.045 | 0.045 | 0.045
Load_TR5_F5_31 | prosumer | 0.0745 | 0.2671 | 0.0599 | 0.0524 | 0.3042 | 0.045 | 0.045 | 0.3115 | 0.045 | 0.267 | 0.0896 | 0.045 | 0.3115 | 0.045 | 0.1419 | 0.1262 | 0.1435 | 0.2387 | 0.3724 | 0.9866 | 0.6914 | 0.2187 | 0.1129 | 0.4818 | 0.2668 | 0.2184 | 0.2699 | 0.1786 | 0.1928 | 0.4334 | 0.4508 | 0.323 | 0.3917 | 0.6009 | 0.2799 | 0.045 | 0.3855 | 0.1392 | 0.1099 | 0.9199 | 0.6521 | 0.5774 | 0.9918 | 0.5748 | 0.5652 | 0.4367 | 0.9677 | 0.8614
Load_TR5_F5_31_dup | prosumer | 0.101 | 0.1558 | 0.053 | 0.053 | 0.053 | 0.1147 | 0.1421 | 0.053 | 0.053 | 0.0941 | 0.1627 | 0.053 | 0.053 | 0.053 | 0.053 | 0.1147 | 0.1421 | 0.053 | 0.1147 | 0.1421 | 0.053 | 0.053 | 0.2038 | 0.053 | 0.053 | 0.053 | 0.2038 | 0.053 | 0.1832 | 0.0736 | 0.1352 | 0.1215 | 0.053 | 0.2038 | 0.053 | 0.2038 | 0.1547 | 0.2366 | 0.538 | 0.2717 | 0.3054 | 0.6612 | 0.4665 | 0.5478 | 0.3571 | 0.1489 | 0.1078 | 0.053
Load_TR5_F5_32 | customer | 0.17 | 0.044 | 0.1211 | 0.1212 | 0.044 | 0.044 | 0.166 | 0.0763 | 0.0793 | 0.1085 | 0.0985 | 0.0622 | 0.1166 | 0.0989 | 0.1433 | 0.044 | 0.044 | 0.2727 | 0.1325 | 0.2016 | 0.1426 | 0.3202 | 0.1552 | 0.071 | 2.0927 | 2.4575 | 0.6369 | 0.2766 | 0.1412 | 0.1595 | 0.0711 | 0.2251 | 0.044 | 0.0998 | 0.083 | 0.1681 | 0.1445 | 0.1306 | 0.2382 | 1.4194 | 0.3546 | 0.3089 | 0.5048 | 0.4452 | 0.5169 | 0.3493 | 0.6073 | 0.103
Load_TR5_F5_32_dup | customer | 0.0575 | 0.1176 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.0448 | 0.039 | 0.2494 | 0.0973 | 0.0474 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.2583 | 0.1255 | 0.2902 | 1.7171 | 0.4802 | 0.6227 | 0.4372 | 0.4726 | 0.341 | 0.039 | 0.039
Load_TR5_F5_33 | customer | 0.4852 | 0.2503 | 0.051 | 0.1217 | 0.051 | 0.0981 | 0.0746 | 0.051 | 0.051 | 0.1217 | 0.051 | 0.2125 | 0.1838 | 0.179 | 0.1487 | 0.0667 | 0.0811 | 0.051 | 0.0667 | 0.3634 | 0.051 | 0.1217 | 0.051 | 0.051 | 0.051 | 0.1217 | 0.051 | 0.1217 | 0.051 | 0.1217 | 0.051 | 0.1217 | 0.051 | 0.051 | 0.051 | 0.1139 | 0.0589 | 0.0589 | 0.1139 | 0.051 | 0.1217 | 0.051 | 0.1217 | 0.051 | 0.051 | 0.051 | 0.1217 | 0.0667
Load_TR5_F5_33_dup | customer | 0.1343 | 0.1612 | 0.06 | 0.219 | 0.06 | 0.1106 | 0.189 | 0.1136 | 0.2045 | 0.0745 | 0.2354 | 0.1178 | 0.1342 | 0.06 | 0.1869 | 0.1663 | 0.1473 | 0.2764 | 0.0646 | 1.4886 | 0.2469 | 0.5457 | 0.9461 | 0.783 | 0.3354 | 0.221 | 0.3652 | 0.3973 | 0.4853 | 0.3203 | 1.8471 | 0.3626 | 0.5516 | 0.2599 | 0.39 | 2.4855 | 3.1966 | 1.2153 | 0.4016 | 0.4659 | 0.6567 | 0.225 | 0.2845 | 0.3793 | 0.1973 | 0.1559 | 0.154 | 0.1704
Load_TR5_F5_34 | prosumer | 0.1037 | 0.1651 | 0.05 | 0.1037 | 0.1651 | 0.05 | 0.2188 | 0.05 | 0.0628 | 0.4499 | 0.1156 | 0.1575 | 0.4062 | 0.073 | 0.1958 | 0.2489 | 0.5215 | 0.2401 | 0.3431 | 0.532 | 0.1366 | 0.1667 | 0.3249 | 0.7293 | 1.1471 | 0.4587 | 0.1804 | 0.0884 | 0.05 | 0.2937 | 0.3267 | 0.2867 | 0.2925 | 0.2208 | 0.4023 | 1.7972 | 0.6337 | 0.0675 | 0.5995 | 3.1477 | 2.4885 | 0.3661 | 0.749 | 0.3715 | 0.8967 | 0.7588 | 0.4397 | 0.4274
Load_TR5_F5_34_dup | prosumer | 0.056 | 0.2138 | 0.0708 | 0.056 | 0.0634 | 0.2212 | 0.056 | 0.056 | 0.125 | 0.1152 | 0.1004 | 0.056 | 0.3277 | 0.0946 | 0.1185 | 0.1711 | 0.056 | 0.125 | 0.1596 | 0.125 | 0.1596 | 0.056 | 0.1078 | 0.1538 | 0.0965 | 0.2169 | 0.1118 | 0.1131 | 0.6258 | 0.1052 | 0.0905 | 0.1941 | 0.0943 | 0.3256 | 0.2845 | 0.302 | 0.3924 | 0.575 | 0.6936 | 0.5194 | 0.3944 | 0.2492 | 0.2286 | 0.056 | 0.1826 | 0.102 | 0.0752 | 0.2094
Load_TR5_F5_35 | prosumer | 0.2356 | 0.1786 | 0.2801 | 0.1277 | 0.2235 | 0.0446 | 0.205 | 0.0769 | 0.1462 | 0.145 | 0.04 | 0.2431 | 0.085 | 0.0475 | 0.1975 | 0.04 | 0.2281 | 0.1 | 0.1525 | 0.1478 | 0.2246 | 0.5098 | 1.5162 | 2.6247 | 2.1036 | 0.0954 | 0.0873 | 0.2408 | 0.04 | 0.0676 | 0.2967 | 0.1307 | 0.3247 | 1.506 | 2.8617 | 2.5299 | 0.0475 | 0.2066 | 0.2169 | 0.2855 | 0.6941 | 0.4752 | 0.7357 | 0.6275 | 0.651 | 1.0144 | 2.3227 | 1.8771
Load_TR5_F5_35_dup | customer | 0.2314 | 0.1046 | 0.0955 | 0.2405 | 0.056 | 0.0606 | 0.1334 | 0.1787 | 0.0754 | 0.056 | 0.198 | 0.056 | 0.1822 | 0.2125 | 0.1317 | 0.4111 | 0.4463 | 1.5255 | 0.4994 | 0.2675 | 0.2677 | 0.1845 | 0.3079 | 0.0689 | 0.2106 | 0.1695 | 0.2253 | 0.1106 | 0.056 | 0.138 | 0.127 | 0.209 | 0.056 | 0.2348 | 0.1012 | 0.056 | 0.4962 | 0.5658 | 0.3157 | 0.6648 | 0.847 | 0.6374 | 0.7732 | 0.9831 | 0.6347 | 1.1356 | 0.68 | 0.6731
Load_TR5_F5_36 | customer | 0.051 | 0.1352 | 0.2044 | 0.3581 | 0.6405 | 0.3583 | 0.2038 | 0.051 | 0.051 | 0.1492 | 0.1071 | 0.1071 | 0.1492 | 0.051 | 0.1633 | 0.0931 | 0.0721 | 0.2582 | 0.2438 | 0.2538 | 0.1771 | 0.2686 | 0.3668 | 0.0935 | 0.1235 | 0.1886 | 0.4145 | 0.3763 | 0.1823 | 0.1918 | 0.4986 | 0.5802 | 0.3196 | 0.4807 | 0.3247 | 1.6516 | 1.5482 | 0.567 | 0.4906 | 0.5375 | 0.5355 | 0.5846 | 0.7963 | 1.089 | 0.9285 | 0.6705 | 0.7481 | 0.6155
Load_TR5_F5_36_dup | prosumer | 0.9647 | 0.9174 | 0.4081 | 0.0917 | 0.1335 | 0.1754 | 0.052 | 0.1315 | 0.1085 | 0.121 | 0.052 | 0.1551 | 0.1537 | 0.0873 | 0.9808 | 1.1545 | 0.7096 | 1.6166 | 0.3581 | 0.3738 | 0.2475 | 0.3338 | 0.1769 | 0.4383 | 0.413 | 1.2087 | 0.7702 | 0.4834 | 0.5191 | 0.1447 | 0.0652 | 0.1182 | 0.052 | 0.1774 | 0.052 | 0.0917 | 0.2211 | 0.0694 | 0.3929 | 0.5181 | 0.518 | 0.8296 | 0.8599 | 0.6123 | 0.7733 | 0.3407 | 0.052 | 0.1315
Load_TR5_F5_37 | prosumer | 0.3249 | 0.4814 | 0.1134 | 0.1383 | 0.1691 | 0.0653 | 0.1399 | 0.1789 | 0.054 | 0.1983 | 0.1205 | 0.0605 | 0.2583 | 0.054 | 0.2674 | 0.4252 | 0.2332 | 0.2991 | 0.1898 | 0.22 | 0.2276 | 0.3477 | 0.227 | 0.3238 | 0.7303 | 0.543 | 1.5899 | 0.0987 | 0.1902 | 0.1059 | 0.0805 | 0.167 | 0.1254 | 0.0729 | 0.2459 | 0.0918 | 0.0843 | 0.1578 | 0.0929 | 0.0653 | 0.1691 | 0.21 | 0.5342 | 0.4558 | 0.2897 | 0.689 | 0.5219 | 0.3417
Load_TR5_F5_37_dup | prosumer | 0.048 | 0.0628 | 0.1955 | 0.048 | 0.048 | 0.2102 | 0.048 | 0.1807 | 0.0775 | 0.048 | 0.048 | 0.2102 | 0.048 | 0.048 | 0.1439 | 0.4292 | 0.4867 | 0.4323 | 0.3202 | 0.4278 | 0.389 | 0.3181 | 0.3622 | 0.3652 | 0.1194 | 0.5478 | 0.1982 | 0.2231 | 0.0825 | 0.0644 | 0.2222 | 0.3617 | 0.2768 | 0.2268 | 0.145 | 0.3349 | 0.4727 | 1.9223 | 0.9938 | 0.5934 | 0.6979 | 0.5087 | 0.5767 | 0.7225 | 0.5453 | 1.031 | 0.1803 | 0.1955
Load_TR5_F5_38 | customer | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.0585 | 0.0713 | 0.0986 | 0.0868 | 0.0603 | 0.048 | 0.0493 | 0.2447 | 0.2513 | 0.0809 | 0.0936 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.1826 | 0.2109 | 0.2024 | 0.2071 | 0.1984 | 0.184 | 0.2604 | 0.4356 | 0.6481 | 0.2528 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048
Load_TR5_F5_38_dup | prosumer | 0.0607 | 0.134 | 0.2256 | 0.134 | 0.1264 | 0.2018 | 0.1078 | 0.045 | 0.1435 | 0.1271 | 0.1445 | 0.2308 | 0.045 | 0.045 | 0.3198 | 0.0555 | 0.1763 | 0.2132 | 0.0879 | 0.3384 | 0.2652 | 0.0804 | 0.5141 | 0.9816 | 0.5657 | 0.578 | 1.0525 | 1.3449 | 0.4591 | 0.8181 | 0.4925 | 0.1185 | 0.1516 | 0.2801 | 0.1583 | 0.0502 | 0.086 | 0.2892 | 0.062 | 0.2277 | 0.2836 | 0.5303 | 0.3715 | 0.3482 | 0.5414 | 0.337 | 0.1445 | 0.0667
Load_TR5_F5_39 | customer | 0.0994 | 0.1752 | 0.054 | 0.2895 | 0.0923 | 0.054 | 0.1612 | 0.1752 | 0.1607 | 0.1 | 0.2206 | 0.054 | 0.1914 | 0.2826 | 0.11 | 0.2055 | 0.0712 | 0.1917 | 0.2619 | 0.186 | 0.3005 | 0.0675 | 0.2064 | 0.1754 | 0.0617 | 0.3545 | 0.2415 | 0.2543 | 0.2965 | 1.9882 | 3.0798 | 1.7692 | 0.1903 | 0.119 | 0.2928 | 0.6114 | 0.2971 | 0.4226 | 0.2449 | 0.1612 | 0.1222 | 0.1984 | 0.1153 | 0.1676 | 0.107 | 0.2294 | 0.1524 | 0.1612
Load_TR5_F5_39_dup | customer | 0.1864 | 0.1153 | 0.2196 | 0.1398 | 0.2039 | 0.2371 | 0.0966 | 0.2304 | 0.0862 | 0.2467 | 0.2003 | 0.0889 | 0.205 | 0.133 | 0.3203 | 0.0721 | 0.3081 | 0.1236 | 0.078 | 0.2679 | 0.1308 | 0.1189 | 0.3405 | 0.125 | 0.0832 | 0.3295 | 0.1049 | 0.2237 | 0.1442 | 0.2076 | 0.1509 | 0.1449 | 0.2318 | 0.1558 | 0.094 | 0.8496 | 0.1284 | 0.0883 | 0.3769 | 0.4652 | 0.4033 | 0.3212 | 0.2565 | 0.7997 | 0.7917 | 0.5556 | 0.7522 | 0.3126
Load_TR5_F5_3_dup | prosumer | 0.1455 | 0.1247 | 0.1447 | 0.0564 | 0.2131 | 0.04 | 0.114 | 0.1266 | 0.0976 | 0.1217 | 0.1661 | 0.1083 | 0.0893 | 0.1802 | 0.1057 | 0.1637 | 0.1286 | 1.3186 | 0.4122 | 0.255 | 0.1312 | 0.1513 | 0.0812 | 0.1016 | 0.1422 | 0.2055 | 0.1476 | 0.2236 | 0.0647 | 0.1555 | 0.114 | 0.0579 | 0.04 | 0.1602 | 0.1093 | 0.04 | 0.04 | 0.114 | 0.1382 | 0.119 | 0.1216 | 0.0862 | 0.1717 | 0.0978 | 0.1486 | 0.1209 | 0.04 | 0.04
Load_TR5_F5_4 | customer | 0.2224 | 0.242 | 0.288 | 0.2203 | 0.1357 | 0.3266 | 0.2331 | 0.1323 | 0.4174 | 0.053 | 0.1734 | 0.1677 | 0.283 | 0.1991 | 0.1562 | 0.286 | 0.1237 | 0.1271 | 0.3433 | 0.1224 | 0.3039 | 0.2438 | 0.2762 | 0.2382 | 0.3419 | 0.3746 | 0.3101 | 0.3984 | 0.1442 | 0.053 | 0.4539 | 0.0872 | 0.2867 | 0.2545 | 0.1504 | 0.1353 | 0.4798 | 0.6251 | 0.4152 | 0.3822 | 0.6653 | 0.5317 | 0.6584 | 0.414 | 0.1752 | 0.0759 | 0.3044 | 0.154
Load_TR5_F5_40 | prosumer | 0.1792 | 0.1197 | 0.0871 | 0.1615 | 0.0668 | 0.1523 | 0.1432 | 0.1666 | 0.1112 | 0.1986 | 0.1088 | 0.2222 | 0.1147 | 0.049 | 0.1669 | 0.1701 | 0.049 | 0.049 | 0.288 | 0.049 | 0.1488 | 0.1777 | 0.1792 | 0.1578 | 0.2591 | 0.8814 | 0.435 | 0.2776 | 0.3273 | 1.5039 | 1.3588 | 0.2141 | 0.3151 | 0.351 | 0.3927 | 1.9439 | 0.1201 | 1.6837 | 0.1088 | 0.4643 | 0.3534 | 0.4917 | 0.52 | 0.449 | 0.2168 | 0.049 | 0.049 | 0.1437
Load_TR5_F5_40_dup | customer | 0.1454 | 0.13 | 0.053 | 0.2224 | 0.053 | 0.1531 | 0.1223 | 0.053 | 0.2224 | 0.053 | 0.1608 | 0.1146 | 0.053 | 0.2224 | 0.053 | 0.053 | 0.053 | 0.1105 | 0.3346 | 0.834 | 0.6766 | 0.4252 | 0.2297 | 0.0582 | 0.2296 | 0.1592 | 0.1015 | 0.2709 | 0.2703 | 0.0992 | 0.1762 | 0.053 | 0.2263 | 0.3765 | 0.9018 | 2.6901 | 2.9825 | 0.3094 | 0.2794 | 0.4789 | 0.1326 | 0.0761 | 0.1993 | 0.053 | 0.207 | 0.0684 | 0.053 | 0.053
Load_TR5_F5_41 | customer | 0.2516 | 0.05 | 0.1798 | 0.2018 | 0.089 | 0.2121 | 0.0768 | 0.2845 | 0.0769 | 0.2161 | 0.0644 | 0.12 | 0.1022 | 0.2161 | 0.1578 | 0.1692 | 0.1114 | 0.05 | 0.2516 | 0.0548 | 0.1453 | 0.1466 | 0.1416 | 0.2305 | 0.1923 | 0.1237 | 0.2646 | 0.05 | 0.1439 | 0.1367 | 0.1103 | 0.2148 | 0.1132 | 0.116 | 0.2723 | 0.1121 | 0.4599 | 0.1641 | 0.644 | 0.49 | 0.5402 | 0.8766 | 1.2413 | 0.9116 | 1.2695 | 0.6529 | 0.1581 | 0.2868
Load_TR5_F5_41_dup | prosumer | 0.048 | 0.048 | 0.2987 | 0.1493 | 0.048 | 0.3227 | 0.0737 | 0.0995 | 0.3166 | 0.1314 | 0.2822 | 0.0885 | 0.2541 | 0.2012 | 0.286 | 0.308 | 0.3059 | 0.2854 | 0.41 | 0.0569 | 0.2656 | 0.296 | 0.1306 | 0.0823 | 0.2505 | 0.1631 | 0.1062 | 0.3417 | 0.1166 | 0.1646 | 0.2147 | 0.137 | 0.2221 | 0.1608 | 0.2861 | 0.2445 | 0.3328 | 0.0508 | 0.1491 | 0.3157 | 0.4461 | 0.4692 | 0.6545 | 0.5972 | 0.2698 | 0.4471 | 0.1917 | 0.2878
Load_TR5_F5_42 | customer | 0.1287 | 0.2191 | 0.2499 | 0.055 | 0.2128 | 0.2563 | 0.0622 | 0.4069 | 0.055 | 0.2864 | 0.106 | 0.2033 | 0.1411 | 0.0805 | 0.323 | 0.1205 | 0.2256 | 0.3707 | 0.215 | 0.2007 | 0.2158 | 0.1554 | 0.1282 | 0.5925 | 1.3615 | 0.3469 | 1.0059 | 2.6841 | 2.9467 | 0.242 | 0.126 | 0.3441 | 0.3228 | 0.1017 | 0.4305 | 0.1109 | 0.3023 | 0.3309 | 0.1889 | 0.7795 | 0.4929 | 0.5423 | 0.5274 | 0.471 | 0.2128 | 0.1826 | 0.1195 | 0.2219
Load_TR5_F5_42_dup | customer | 0.1449 | 0.044 | 0.1663 | 0.1343 | 0.044 | 0.1449 | 0.044 | 0.0944 | 0.4447 | 0.1222 | 0.1449 | 0.1557 | 0.1304 | 0.1701 | 0.1557 | 0.5215 | 0.1717 | 0.2287 | 0.2147 | 0.0978 | 0.2796 | 0.046 | 0.211 | 0.1708 | 0.161 | 0.171 | 0.1852 | 0.1742 | 0.3476 | 0.2523 | 0.3207 | 0.3302 | 0.1888 | 0.3655 | 0.9982 | 0.199 | 0.3957 | 0.3108 | 0.1995 | 0.3278 | 0.5304 | 0.7611 | 0.7747 | 0.5741 | 0.0944 | 0.5713 | 0.4126 | 0.3044
Load_TR5_F5_43 | prosumer | 0.2094 | 0.0762 | 0.077 | 0.1122 | 0.1421 | 0.045 | 0.2094 | 0.045 | 0.045 | 0.1347 | 0.1197 | 0.045 | 0.1717 | 0.0973 | 0.045 | 0.224 | 0.0847 | 0.0559 | 1.2044 | 0.2224 | 0.2543 | 0.1487 | 1.0008 | 1.6591 | 0.3177 | 0.058 | 0.0954 | 0.172 | 0.045 | 0.172 | 0.14 | 0.1344 | 0.2806 | 0.2671 | 0.2577 | 0.2605 | 0.1344 | 0.4372 | 0.9418 | 1.8316 | 1.3049 | 1.9183 | 0.5488 | 0.7642 | 0.5875 | 0.7421 | 0.5047 | 0.045
Load_TR5_F5_43_dup | prosumer | 0.036 | 0.1856 | 0.036 | 0.036 | 0.07 | 0.1516 | 0.036 | 0.3035 | 0.036 | 0.1788 | 0.0428 | 0.1312 | 0.0904 | 0.0836 | 0.138 | 0.0641 | 0.081 | 1.3977 | 0.3048 | 0.3632 | 0.1363 | 0.1127 | 0.2393 | 0.5616 | 0.4119 | 1.136 | 0.1728 | 0.2972 | 0.1891 | 0.0662 | 0.1482 | 0.0862 | 0.3043 | 0.2036 | 0.462 | 0.0406 | 0.2337 | 0.3328 | 0.1589 | 0.3314 | 0.3407 | 0.568 | 0.5105 | 0.232 | 0.6662 | 0.5491 | 0.036 | 0.036
Load_TR5_F5_44 | prosumer | 0.05 | 0.1839 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1839 | 0.05 | 0.0683 | 0.1656 | 0.05 | 0.05 | 0.05 | 0.0987 | 0.1352 | 0.05 | 0.2757 | 0.1529 | 0.0822 | 0.0521 | 0.0982 | 0.3202 | 0.345 | 0.253 | 1.1269 | 0.7919 | 0.2107 | 0.1839 | 0.05 | 0.1048 | 0.1291 | 0.05 | 0.1413 | 0.0926 | 0.05 | 0.1839 | 0.05 | 0.05 | 0.1839 | 0.05 | 0.05 | 0.0987 | 0.1352 | 0.05 | 0.1839 | 0.05
Load_TR5_F5_44_dup | customer | 0.0592 | 0.046 | 0.1773 | 0.2675 | 0.0699 | 0.1535 | 0.046 | 0.1714 | 0.052 | 0.046 | 0.046 | 0.1654 | 0.0579 | 0.046 | 0.1594 | 0.0639 | 0.052 | 0.1714 | 0.2328 | 0.1581 | 0.1057 | 1.4128 | 1.6998 | 0.4116 | 0.1746 | 1.8548 | 0.1281 | 0.1519 | 0.1535 | 0.046 | 0.046 | 0.046 | 0.1773 | 0.046 | 0.1117 | 0.1117 | 0.046 | 0.1117 | 0.1723 | 0.2206 | 0.6256 | 0.1538 | 0.4089 | 0.5919 | 0.1894 | 0.1195 | 0.1236 | 0.0997
Load_TR5_F5_45 | customer | 0.1091 | 0.2081 | 0.1073 | 0.085 | 0.2944 | 0.045 | 0.045 | 0.3288 | 0.0507 | 0.2317 | 0.1477 | 0.045 | 0.0893 | 0.2901 | 0.045 | 0.0847 | 0.2788 | 0.0667 | 0.2864 | 0.3831 | 0.0463 | 0.2864 | 0.093 | 0.1583 | 0.1678 | 0.1486 | 0.8679 | 0.7424 | 0.2773 | 0.269 | 0.4266 | 0.1381 | 0.2104 | 0.3476 | 0.1688 | 0.5368 | 0.1766 | 0.3126 | 0.4289 | 0.4443 | 0.8191 | 0.4977 | 0.5242 | 0.9325 | 0.6597 | 0.479 | 0.5427 | 0.1971
Load_TR5_F5_45_dup | prosumer | 0.113 | 0.041 | 0.041 | 0.061 | 0.093 | 0.041 | 0.041 | 0.053 | 0.101 | 0.041 | 0.041 | 0.041 | 0.049 | 0.105 | 0.041 | 0.2171 | 0.1216 | 0.041 | 0.1193 | 0.1607 | 0.041 | 0.101 | 0.1059 | 0.0721 | 1.0366 | 0.041 | 0.113 | 0.2792 | 0.1129 | 0.1364 | 0.1622 | 0.1689 | 0.2885 | 0.2064 | 0.2538 | 0.3296 | 0.3494 | 0.2641 | 0.3795 | 0.4981 | 0.6069 | 0.6372 | 0.5202 | 1.4394 | 0.8866 | 0.9127 | 0.8957 | 0.49
Load_TR5_F5_46 | customer | 0.053 | 0.219 | 0.053 | 0.053 | 0.219 | 0.053 | 0.2039 | 0.0681 | 0.1586 | 0.1134 | 0.053 | 0.2349 | 0.2633 | 0.053 | 0.1855 | 0.1491 | 0.0909 | 0.0822 | 1.5151 | 0.3797 | 0.093 | 0.255 | 0.3026 | 0.4949 | 0.3748 | 0.3949 | 0.1493 | 0.219 | 0.0982 | 0.1518 | 0.1431 | 0.2454 | 0.1043 | 0.053 | 0.1662 | 0.1058 | 0.053 | 0.219 | 0.1676 | 0.4726 | 0.5189 | 0.4664 | 0.5374 | 0.3134 | 0.4049 | 0.924 | 0.62 | 0.7521
Load_TR5_F5_46_dup | customer | 0.0759 | 0.1446 | 0.053 | 0.1675 | 0.053 | 0.0644 | 0.156 | 0.053 | 0.0988 | 0.1217 | 0.0644 | 0.156 | 0.053 | 0.1301 | 0.0988 | 0.0549 | 0.0757 | 0.1832 | 0.0715 | 0.1735 | 0.1788 | 0.4654 | 2.7555 | 2.6173 | 0.2616 | 0.1787 | 2.1323 | 0.6103 | 0.307 | 0.1696 | 0.053 | 0.1675 | 0.053 | 0.053 | 0.053 | 0.3039 | 0.2349 | 0.1071 | 0.2075 | 0.3994 | 0.6137 | 0.8044 | 0.7279 | 0.9224 | 0.053 | 0.1102 | 0.1102 | 0.053
Load_TR5_F5_47 | customer | 0.1338 | 0.0798 | 0.1877 | 0.049 | 0.2186 | 0.049 | 0.1261 | 0.1415 | 0.0644 | 0.2032 | 0.049 | 0.2032 | 0.0644 | 0.0844 | 0.1957 | 0.057 | 0.1829 | 0.1032 | 0.1341 | 0.1495 | 0.2437 | 0.1833 | 0.2704 | 0.4445 | 0.2579 | 0.4657 | 0.3124 | 0.2108 | 0.2039 | 0.27 | 0.2509 | 0.2554 | 0.0564 | 0.2204 | 0.112 | 0.0812 | 0.224 | 0.0627 | 0.1395 | 0.3419 | 0.3316 | 0.502 | 0.5706 | 0.6238 | 0.5632 | 0.4505 | 1.5399 | 1.3935
Load_TR5_F5_47_dup | prosumer | 0.1791 | 0.041 | 0.1477 | 0.0724 | 0.041 | 0.1791 | 0.041 | 0.0975 | 0.1226 | 0.041 | 0.154 | 0.0661 | 0.041 | 0.1791 | 0.1298 | 0.0854 | 0.1742 | 0.5131 | 0.1783 | 0.1679 | 0.2388 | 0.2705 | 0.4303 | 0.2884 | 1.1353 | 0.3784 | 0.3552 | 0.1791 | 0.041 | 1.2573 | 0.2097 | 0.5006 | 0.1978 | 0.041 | 0.296 | 0.1605 | 0.2734 | 0.2679 | 0.1729 | 0.041 | 0.1226 | 0.0975 | 0.041 | 0.041 | 0.1791 | 0.041 | 0.041 | 0.1791
Load_TR5_F5_48 | customer | 0.0559 | 0.1044 | 0.085 | 0.051 | 0.1385 | 0.051 | 0.051 | 0.051 | 0.1385 | 0.051 | 0.1142 | 0.0753 | 0.051 | 0.1142 | 0.09 | 0.2492 | 0.0753 | 0.051 | 0.1385 | 0.059 | 0.0654 | 1.4322 | 0.2063 | 0.1613 | 0.051 | 0.1239 | 0.7919 | 0.1296 | 0.1214 | 0.0762 | 0.051 | 0.1385 | 0.051 | 0.2967 | 0.1142 | 0.1605 | 1.3407 | 0.5299 | 0.2993 | 0.4297 | 0.4063 | 0.4243 | 0.4385 | 0.2395 | 0.051 | 0.1385 | 0.051 | 0.051
Load_TR5_F5_48_dup | prosumer | 0.055 | 0.1678 | 0.0609 | 0.055 | 0.2327 | 0.1257 | 0.055 | 0.1729 | 0.1855 | 0.055 | 0.055 | 0.3034 | 0.055 | 0.2326 | 0.1258 | 0.1006 | 0.2234 | 0.2422 | 0.1234 | 0.3172 | 0.9133 | 0.2623 | 0.1943 | 0.2116 | 0.055 | 0.2975 | 0.1891 | 0.2497 | 0.2104 | 0.1266 | 0.3807 | 0.055 | 0.055 | 0.1737 | 0.1846 | 0.055 | 0.0668 | 0.1966 | 0.15 | 0.0903 | 0.1493 | 0.1203 | 0.238 | 0.055 | 0.268 | 0.0903 | 0.0786 | 0.2277
Load_TR5_F5_49 | customer | 0.0654 | 0.3069 | 0.0626 | 0.1488 | 0.2341 | 0.133 | 0.1119 | 0.1483 | 0.3125 | 0.047 | 0.1405 | 0.3203 | 0.123 | 0.3015 | 0.7052 | 0.3999 | 0.6022 | 0.1721 | 0.1069 | 1.3161 | 0.213 | 0.3857 | 0.3492 | 0.352 | 0.2563 | 0.1394 | 0.3222 | 0.176 | 1.2537 | 0.8721 | 1.8246 | 0.1773 | 0.2841 | 0.169 | 0.2017 | 0.1861 | 0.1356 | 0.3252 | 0.12 | 0.2184 | 0.0715 | 0.2153 | 0.4511 | 0.3588 | 0.2873 | 0.3389 | 0.1745 | 0.1694
Load_TR5_F5_49_dup | customer | 0.4169 | 0.2372 | 0.1379 | 0.053 | 0.0603 | 0.2121 | 0.1557 | 0.075 | 0.3002 | 0.053 | 0.0962 | 0.2716 | 0.0928 | 0.2238 | 0.1351 | 0.1449 | 0.0692 | 0.2766 | 0.0823 | 0.1784 | 0.2122 | 0.1385 | 0.3168 | 0.195 | 0.2512 | 0.5363 | 0.0978 | 0.2504 | 0.1255 | 0.3259 | 0.1867 | 0.294 | 0.4029 | 0.639 | 0.633 | 0.4278 | 0.5995 | 1.0593 | 0.3787 | 0.8089 | 0.4508 | 0.7336 | 0.5117 | 0.4122 | 0.6242 | 0.7207 | 0.8571 | 0.7362
Load_TR5_F5_4_dup | customer | 0.2296 | 0.051 | 0.051 | 0.051 | 0.1222 | 0.051 | 0.1222 | 0.051 | 0.1222 | 0.051 | 0.051 | 0.1183 | 0.055 | 0.4834 | 0.1624 | 0.138 | 1.0315 | 0.1428 | 0.2527 | 0.127 | 0.1617 | 0.051 | 0.051 | 0.051 | 0.1636 | 0.0895 | 0.051 | 0.0513 | 0.1214 | 0.1488 | 0.0821 | 0.3355 | 0.2397 | 0.051 | 0.2471 | 0.7566 | 1.0092 | 0.132 | 0.2249 | 0.3401 | 0.055 | 0.1183 | 0.1993 | 0.2414 | 0.2045 | 0.1716 | 0.4337 | 0.6301
Load_TR5_F5_5 | prosumer | 0.6866 | 0.0759 | 0.0861 | 0.1909 | 0.052 | 0.2249 | 0.0554 | 0.1498 | 0.1238 | 0.1133 | 0.1636 | 0.1099 | 0.0873 | 0.1317 | 0.1499 | 0.0598 | 1.7985 | 0.4183 | 0.8945 | 0.4246 | 0.2113 | 0.266 | 0.2508 | 0.1057 | 0.2028 | 1.6249 | 0.4611 | 0.2113 | 0.1059 | 0.0943 | 0.2431 | 0.052 | 0.1839 | 0.1918 | 0.248 | 0.2476 | 0.1662 | 0.1804 | 0.3228 | 0.424 | 0.4384 | 0.4245 | 0.5081 | 0.6196 | 0.5991 | 0.711 | 0.5226 | 0.1133
Load_TR5_F5_50 | customer | 0.1035 | 0.2769 | 0.1729 | 0.1275 | 0.1376 | 0.2251 | 0.0822 | 0.3297 | 0.1035 | 0.1407 | 0.3091 | 0.053 | 0.1887 | 0.1849 | 0.1876 | 0.7051 | 0.5692 | 0.2532 | 0.3412 | 0.2626 | 0.3876 | 0.6917 | 0.4919 | 0.2393 | 0.5656 | 0.2109 | 0.5556 | 0.2722 | 0.2186 | 0.2311 | 0.0719 | 0.3778 | 0.053 | 0.3335 | 0.3263 | 0.2761 | 0.3277 | 0.174 | 0.4915 | 0.3289 | 0.8232 | 0.5864 | 0.7854 | 1.0507 | 0.7897 | 0.9897 | 1.3885 | 0.8405
Load_TR5_F5_50_dup | customer | 0.1434 | 0.1846 | 0.0882 | 0.205 | 0.1294 | 0.1247 | 0.2251 | 0.0597 | 0.1361 | 0.205 | 0.1163 | 0.2335 | 0.051 | 0.1294 | 0.2076 | 1.248 | 0.1551 | 0.4513 | 0.2331 | 0.5342 | 1.2098 | 0.4426 | 0.5634 | 0.2023 | 0.2644 | 0.4784 | 0.6078 | 1.4248 | 0.2859 | 0.7678 | 0.468 | 0.3237 | 0.1252 | 0.2633 | 0.1715 | 0.2677 | 0.3647 | 0.1487 | 0.8741 | 2.0223 | 0.6025 | 1.346 | 2.0001 | 0.5932 | 0.8067 | 0.4621 | 0.0895 | 0.2124
Load_TR5_F5_51 | prosumer | 0.075 | 0.1502 | 0.05 | 0.1752 | 0.05 | 0.1752 | 0.05 | 0.1752 | 0.05 | 0.3254 | 0.1942 | 0.05 | 0.05 | 0.1752 | 0.05 | 0.5177 | 0.6926 | 2.4536 | 2.1126 | 0.121 | 0.2364 | 0.5729 | 0.296 | 0.1251 | 0.0616 | 0.0876 | 0.1377 | 0.0813 | 0.1439 | 0.05 | 0.1752 | 0.05 | 0.1565 | 0.0688 | 0.0993 | 0.2569 | 0.1093 | 0.0795 | 0.3708 | 0.2584 | 0.1964 | 0.404 | 0.2831 | 0.4861 | 0.4755 | 0.2296 | 0.05 | 0.1755
Load_TR5_F5_51_dup | prosumer | 0.1212 | 0.051 | 0.1835 | 0.1522 | 0.051 | 0.2813 | 0.0545 | 0.2241 | 0.1116 | 0.0579 | 0.1999 | 0.129 | 0.1133 | 0.3575 | 0.2373 | 1.2934 | 2.6251 | 1.7237 | 0.612 | 0.3346 | 0.4094 | 0.0595 | 0.0821 | 0.1211 | 0.2269 | 0.3255 | 0.3443 | 0.1599 | 0.0683 | 0.3687 | 0.2635 | 0.1656 | 0.1133 | 0.2225 | 0.089 | 0.161 | 0.1367 | 0.1133 | 0.206 | 0.1606 | 0.1371 | 0.3912 | 0.6079 | 0.5119 | 0.8382 | 0.6389 | 0.0787 | 0.2225
Load_TR5_F5_52 | prosumer | 0.7405 | 0.1203 | 0.058 | 0.1011 | 0.1011 | 0.058 | 0.1442 | 0.058 | 0.1394 | 0.0628 | 0.058 | 0.058 | 0.058 | 0.058 | 0.1394 | 0.0628 | 0.0618 | 0.1442 | 0.0628 | 0.1529 | 0.0997 | 0.1122 | 0.1061 | 0.1268 | 0.1059 | 0.058 | 0.1442 | 0.058 | 0.058 | 0.058 | 0.0835 | 0.073 | 0.3427 | 0.2284 | 0.066 | 0.2219 | 0.2416 | 0.2525 | 0.5765 | 0.4185 | 0.5956 | 0.7327 | 0.973 | 0.4991 | 0.5453 | 0.5244 | 0.2242 | 0.1442
Load_TR5_F5_52_dup | prosumer | 0.1655 | 0.049 | 0.186 | 0.0627 | 0.049 | 0.0627 | 0.186 | 0.049 | 0.1723 | 0.0764 | 0.1107 | 0.1381 | 0.049 | 0.1655 | 0.0833 | 0.049 | 0.0833 | 0.2536 | 0.1437 | 1.1688 | 0.1193 | 0.2743 | 0.2296 | 0.2811 | 0.3824 | 0.3404 | 0.4496 | 0.3467 | 0.328 | 1.2328 | 1.0887 | 0.303 | 0.2598 | 1.4361 | 0.2924 | 0.1855 | 0.1213 | 0.1026 | 0.2418 | 0.2468 | 0.2594 | 0.6508 | 0.9733 | 1.0559 | 0.6012 | 0.4048 | 0.6119 | 0.8393
Load_TR5_F5_53 | customer | 0.5269 | 0.3605 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.3038 | 0.4108 | 0.1397 | 0.0396 | 0.0702 | 0.093 | 0.1565 | 0.085 | 0.2308 | 0.0634 | 0.0555 | 0.069 | 0.077 | 1.2956 | 0.2473 | 0.0573 | 0.062 | 0.1135 | 0.3368 | 0.2897 | 0.3033 | 0.3412 | 0.3029 | 0.2638 | 0.3257 | 0.5164 | 0.3957
Load_TR5_F5_53_dup | prosumer | 0.0983 | 0.5051 | 0.3499 | 0.691 | 0.0548 | 0.04 | 0.2335 | 0.0697 | 0.2017 | 0.1015 | 0.1136 | 0.1896 | 0.0919 | 0.0548 | 0.1822 | 0.3545 | 0.2629 | 0.4769 | 0.3318 | 0.4116 | 0.2757 | 0.2302 | 0.1734 | 0.378 | 0.3371 | 1.0409 | 2.6843 | 2.8651 | 0.2309 | 0.3571 | 1.0247 | 0.1318 | 0.2217 | 0.1395 | 0.1067 | 0.0437 | 0.2097 | 0.0898 | 0.1067 | 0.1324 | 0.104 | 0.04 | 0.04 | 0.2015 | 0.04 | 0.5604 | 0.3171 | 0.103
Load_TR5_F5_54 | customer | 0.5579 | 0.5858 | 0.4305 | 0.5736 | 0.5433 | 0.5567 | 0.2266 | 0.0698 | 0.2081 | 0.0622 | 0.2158 | 0.049 | 0.1845 | 0.0935 | 0.1177 | 0.138 | 0.1549 | 0.049 | 0.0966 | 0.2087 | 0.0714 | 0.1213 | 0.1736 | 0.2371 | 0.1566 | 0.1069 | 0.2378 | 0.2371 | 0.3477 | 0.198 | 0.3092 | 0.3781 | 0.2516 | 0.3337 | 0.3566 | 0.3046 | 0.1823 | 0.3403 | 0.0926 | 0.2723 | 0.3263 | 0.5311 | 0.6371 | 0.4697 | 0.3772 | 0.049 | 0.2022 | 0.0757
Load_TR5_F5_54_dup | prosumer | 0.1635 | 0.0814 | 0.275 | 0.052 | 0.2064 | 0.0788 | 0.2335 | 0.1035 | 0.1426 | 0.0961 | 0.1696 | 0.1426 | 0.1073 | 0.3466 | 0.3105 | 0.3868 | 0.2939 | 0.4501 | 0.059 | 0.3439 | 0.208 | 0.1416 | 0.2162 | 0.0741 | 0.1917 | 0.0908 | 0.1038 | 0.1623 | 0.1799 | 0.1601 | 0.9254 | 0.5356 | 0.1269 | 0.2169 | 0.9458 | 0.2649 | 0.2093 | 0.3459 | 0.3012 | 0.1479 | 0.5106 | 0.1684 | 0.1786 | 0.2472 | 0.1549 | 0.1415 | 0.3315 | 0.302
Load_TR5_F5_55 | customer | 0.1365 | 0.0807 | 0.1848 | 0.1585 | 0.051 | 0.051 | 0.2145 | 0.1585 | 0.1253 | 0.1993 | 0.0994 | 0.2145 | 0.1316 | 0.1448 | 0.3073 | 0.2528 | 0.2622 | 0.3706 | 0.1726 | 0.0662 | 0.1672 | 0.1066 | 0.203 | 0.4792 | 0.3547 | 0.2258 | 0.41 | 0.2463 | 0.3433 | 0.1716 | 0.2042 | 0.542 | 0.3332 | 0.051 | 0.0967 | 0.2155 | 0.1969 | 0.1139 | 0.7395 | 0.2495 | 0.3744 | 0.5988 | 0.3418 | 0.5107 | 0.5664 | 0.3369 | 0.4937 | 0.2022
Load_TR5_F5_55_dup | prosumer | 0.839 | 0.9647 | 0.297 | 0.2788 | 0.4186 | 0.4584 | 0.057 | 0.1866 | 0.0951 | 0.1332 | 0.1485 | 0.0722 | 0.2095 | 0.057 | 0.1392 | 0.3163 | 0.1606 | 0.2736 | 0.154 | 0.6769 | 0.9137 | 0.0769 | 0.3263 | 0.3236 | 0.2247 | 0.057 | 0.057 | 0.2018 | 0.0799 | 0.1408 | 0.1408 | 0.057 | 0.0875 | 0.1942 | 0.5182 | 0.6916 | 0.5188 | 1.7762 | 1.6948 | 1.4267 | 0.581 | 1.7579 | 1.127 | 0.9125 | 0.7115 | 0.731 | 0.5539 | 0.057
Load_TR5_F5_56 | prosumer | 0.1866 | 0.1719 | 0.1412 | 0.1785 | 0.056 | 0.056 | 0.3257 | 0.0792 | 0.2165 | 0.2581 | 0.1189 | 0.2371 | 0.1601 | 0.2264 | 1.1458 | 0.3267 | 0.6397 | 0.6614 | 0.505 | 0.1531 | 0.1111 | 0.1257 | 0.2792 | 0.056 | 0.056 | 0.1102 | 0.2212 | 0.1295 | 0.2632 | 0.1418 | 0.0928 | 0.3122 | 0.056 | 0.056 | 0.3232 | 0.1118 | 0.3479 | 0.391 | 0.2819 | 0.7102 | 0.3651 | 0.3942 | 0.497 | 0.293 | 0.7096 | 1.1335 | 0.6318 | 0.377
Load_TR5_F5_56_dup | prosumer | 0.3382 | 0.2247 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2646 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0575 | 0.0717 | 0.0659 | 0.08 | 0.0846 | 0.0696 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2043 | 0.3043 | 1.0354 | 0.2875 | 0.3045 | 0.4703 | 1.9168 | 0.3212 | 0.3678 | 0.3663 | 0.6528 | 0.5969 | 0.2924 | 0.05 | 0.05 | 0.05 | 0.1054
Load_TR5_F5_57 | customer | 0.054 | 0.1279 | 0.1607 | 0.054 | 0.2346 | 0.054 | 0.1935 | 0.095 | 0.054 | 0.2346 | 0.0578 | 1.7672 | 0.0786 | 0.1032 | 0.1853 | 0.0578 | 0.2477 | 0.8866 | 1.0679 | 0.2264 | 2.0733 | 0.0994 | 0.1105 | 0.2346 | 0.0654 | 0.1227 | 0.1798 | 0.087 | 0.2372 | 0.0667 | 1.4692 | 0.3122 | 0.2042 | 0.1293 | 0.2346 | 0.3823 | 2.9207 | 1.842 | 0.2261 | 0.3571 | 0.4269 | 0.4314 | 0.478 | 0.3774 | 0.2004 | 0.2818 | 0.054 | 0.054
Load_TR5_F5_57_dup | customer | 0.1566 | 0.1386 | 0.1839 | 0.1989 | 0.0504 | 0.2045 | 0.1247 | 0.2243 | 0.037 | 0.1979 | 0.136 | 0.1261 | 0.2379 | 0.1126 | 0.2646 | 0.1906 | 0.9492 | 1.0962 | 0.3479 | 0.3119 | 0.3324 | 0.0483 | 0.2411 | 0.1343 | 0.1011 | 0.1305 | 0.3028 | 0.1695 | 1.1141 | 0.4341 | 0.157 | 0.3962 | 0.2781 | 0.2693 | 0.4989 | 0.0966 | 0.0475 | 0.2492 | 0.4441 | 0.3788 | 0.4852 | 0.6141 | 0.4144 | 0.3724 | 0.2346 | 0.6536 | 1.2621 | 2.6556
Load_TR5_F5_58 | prosumer | 0.1087 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.1931 | 0.8701 | 0.2412 | 0.1305 | 1.4287 | 1.1033 | 0.1522 | 0.2323 | 0.1574 | 0.1556 | 0.1961 | 0.0807 | 0.2326 | 0.056 | 0.1044 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056 | 0.056
Load_TR5_F5_58_dup | customer | 0.2279 | 0.0953 | 0.4465 | 0.098 | 0.1992 | 0.3947 | 0.046 | 0.341 | 0.0528 | 0.3292 | 0.2647 | 0.1915 | 0.3838 | 0.11 | 0.3351 | 0.7838 | 0.3024 | 0.214 | 0.315 | 0.5297 | 0.0709 | 0.5594 | 0.1848 | 0.4803 | 0.6966 | 0.1129 | 0.4052 | 0.6685 | 0.192 | 0.365 | 0.3445 | 0.2401 | 0.2827 | 0.4711 | 1.4996 | 1.2016 | 1.1359 | 0.2132 | 0.2361 | 0.2707 | 0.4936 | 0.4438 | 0.3999 | 0.48 | 0.4684 | 0.514 | 0.9715 | 0.4434
Load_TR5_F5_59 | customer | 0.3303 | 0.046 | 0.053 | 0.1018 | 0.06 | 0.0949 | 0.053 | 0.1018 | 0.046 | 0.06 | 0.0949 | 0.0709 | 0.4658 | 0.2014 | 0.1901 | 0.2615 | 0.195 | 0.1864 | 0.4334 | 0.6397 | 0.8827 | 0.3636 | 0.1783 | 0.2646 | 0.1238 | 0.3652 | 0.1149 | 0.5314 | 0.5091 | 0.2948 | 0.1193 | 0.7642 | 1.4134 | 0.1259 | 0.2949 | 0.1879 | 0.1592 | 0.2135 | 0.1551 | 0.2033 | 0.5473 | 0.431 | 0.3918 | 0.5483 | 0.36 | 0.5209 | 0.4703 | 0.3564
Load_TR5_F5_59_dup | prosumer | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.0851 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.0844 | 0.0611 | 0.052 | 0.064 | 0.058 | 0.066 | 0.1255 | 1.8293 | 0.4306 | 0.0562 | 0.106 | 1.3857 | 1.3312 | 2.0711 | 0.1292 | 0.2989 | 0.164 | 0.2049 | 0.2559 | 0.2493 | 0.2582 | 0.0968 | 1.9758 | 0.2845 | 1.7353 | 1.2306 | 1.03 | 0.2796 | 0.3591 | 0.3944 | 0.4357 | 0.6443 | 0.625 | 0.7265 | 0.5688
Load_TR5_F5_5_dup | prosumer | 0.2337 | 0.0524 | 0.2484 | 0.1891 | 0.1046 | 0.1961 | 0.1891 | 0.1046 | 0.2333 | 0.2129 | 0.0654 | 0.2899 | 0.1519 | 0.1008 | 0.2371 | 0.1417 | 0.2649 | 0.1953 | 0.079 | 0.1296 | 0.2423 | 0.1175 | 0.2897 | 0.135 | 0.2664 | 0.4518 | 0.2041 | 0.1412 | 0.3006 | 0.048 | 0.2274 | 0.156 | 0.1855 | 0.1855 | 0.3034 | 0.1339 | 0.2743 | 0.7619 | 0.4847 | 0.6662 | 0.7544 | 0.3851 | 0.6108 | 0.4037 | 0.5072 | 0.673 | 0.2532 | 0.2376
Load_TR5_F5_6 | customer | 0.5013 | 0.1686 | 0.0646 | 0.2194 | 0.0966 | 0.1367 | 0.1979 | 0.046 | 0.14 | 0.1111 | 0.046 | 0.2051 | 0.1063 | 0.1849 | 0.1489 | 0.1606 | 0.1875 | 0.1558 | 0.2075 | 0.2827 | 0.192 | 0.3188 | 1.3213 | 0.1456 | 0.189 | 0.0532 | 1.0779 | 0.3121 | 0.403 | 0.046 | 0.1152 | 0.2194 | 0.1257 | 0.3756 | 0.2678 | 0.2844 | 0.1783 | 1.4636 | 1.4702 | 0.8325 | 0.3699 | 0.4621 | 0.8137 | 0.8733 | 0.5828 | 0.6821 | 0.6439 | 0.4788
Load_TR5_F5_60 | prosumer | 0.2952 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.0693 | 0.055 | 0.0535 | 0.037 | 0.037 | 0.0422 | 0.0944 | 0.038 | 0.037 | 0.079 | 0.0917 | 0.803 | 0.1791 | 0.399 | 0.2396 | 0.6746 | 0.8523 | 0.2619 | 0.0525 | 0.386 | 0.2049 | 0.3328 | 1.4249 | 0.0578 | 0.0474 | 0.0768 | 0.3171 | 0.496 | 0.3975 | 0.402 | 0.6567 | 0.4172 | 0.3976 | 0.5749 | 0.493
Load_TR5_F5_60_dup | prosumer | 0.6439 | 0.5497 | 0.125 | 0.1446 | 0.05 | 0.1103 | 0.1594 | 0.1004 | 0.1692 | 0.05 | 0.0935 | 0.1761 | 0.05 | 0.2196 | 0.05 | 0.05 | 0.4187 | 0.2481 | 0.2108 | 0.4627 | 0.2747 | 0.2297 | 1.6026 | 1.3049 | 0.8061 | 0.8825 | 1.2875 | 0.6073 | 0.3647 | 0.2206 | 0.3661 | 0.1615 | 0.274 | 1.1556 | 0.913 | 2.1498 | 0.3922 | 0.1739 | 0.284 | 0.3406 | 0.3637 | 1.4284 | 0.6796 | 0.5451 | 0.6436 | 0.2267 | 0.365 | 0.7358
Load_TR5_F5_61 | customer | 0.1617 | 0.1146 | 0.077 | 0.2982 | 0.044 | 0.1429 | 0.2323 | 0.044 | 0.1758 | 0.1923 | 0.0511 | 0.0722 | 0.1843 | 0.4132 | 0.3018 | 0.2828 | 0.1901 | 1.0931 | 0.2401 | 0.1965 | 0.1705 | 1.2431 | 0.4221 | 0.3002 | 1.7056 | 0.164 | 0.1824 | 0.1928 | 0.044 | 0.1626 | 0.0925 | 0.164 | 0.1758 | 0.0722 | 0.5075 | 0.044 | 0.2672 | 0.3204 | 0.3708 | 0.1783 | 0.1842 | 0.5391 | 0.2651 | 0.2447 | 0.6201 | 0.1993 | 0.1626 | 0.0572
Load_TR5_F5_61_dup | prosumer | 0.1264 | 0.0587 | 0.0925 | 0.0925 | 0.049 | 0.049 | 0.136 | 0.049 | 0.0925 | 0.0925 | 0.049 | 0.136 | 0.049 | 0.5669 | 0.3257 | 0.295 | 0.2667 | 0.2845 | 1.0259 | 0.2158 | 0.2276 | 0.049 | 0.0828 | 0.1022 | 0.049 | 0.049 | 0.049 | 0.136 | 0.0683 | 0.149 | 0.1504 | 0.129 | 2.657 | 0.0877 | 0.8074 | 1.9543 | 0.1118 | 0.1564 | 0.2453 | 0.4185 | 0.4903 | 0.3765 | 0.4638 | 0.7153 | 0.4872 | 0.4208 | 0.049 | 0.136
Load_TR5_F5_62 | prosumer | 0.2343 | 0.11 | 0.1761 | 0.14 | 0.0992 | 0.1809 | 0.1676 | 0.056 | 0.4142 | 0.2278 | 0.056 | 0.2925 | 0.056 | 0.056 | 0.2613 | 0.0872 | 0.2238 | 1.1902 | 0.4681 | 0.3507 | 0.8804 | 1.3748 | 1.7412 | 0.0731 | 0.056 | 0.4791 | 0.0632 | 0.1731 | 0.1754 | 0.3265 | 0.1917 | 0.11 | 0.2385 | 0.1588 | 0.2538 | 0.2584 | 0.2122 | 2.1237 | 0.2485 | 0.1946 | 0.5758 | 0.3381 | 0.4172 | 0.543 | 0.056 | 0.0872 | 0.1965 | 0.4342
Load_TR5_F5_62_dup | prosumer | 0.3246 | 0.051 | 0.073 | 0.3044 | 0.0712 | 0.1535 | 0.2172 | 0.0779 | 0.2591 | 0.1385 | 0.0785 | 0.3191 | 0.0975 | 0.305 | 0.295 | 0.2202 | 0.1115 | 0.051 | 0.1954 | 0.4229 | 0.2191 | 0.4852 | 0.2474 | 1.5463 | 0.5358 | 0.4514 | 0.5007 | 0.7419 | 1.4958 | 0.5387 | 0.3852 | 0.3364 | 0.0523 | 0.212 | 0.2718 | 0.394 | 0.2157 | 1.3563 | 0.1052 | 0.5902 | 0.668 | 0.9546 | 1.1319 | 0.8546 | 0.983 | 0.877 | 0.6607 | 0.6104
Load_TR5_F5_63 | customer | 0.048 | 0.2088 | 0.048 | 0.048 | 0.2493 | 0.048 | 0.1211 | 0.1357 | 0.048 | 0.2088 | 0.048 | 0.0919 | 0.165 | 0.048 | 0.2054 | 0.1323 | 0.4533 | 1.0985 | 0.048 | 0.2088 | 0.048 | 0.048 | 0.1065 | 0.1504 | 0.0848 | 1.5092 | 0.1585 | 0.1217 | 0.048 | 0.048 | 0.048 | 0.048 | 0.1869 | 0.0699 | 0.1138 | 0.143 | 0.048 | 0.3492 | 0.5261 | 0.1695 | 0.2705 | 0.8236 | 0.3517 | 0.392 | 0.3044 | 0.1628 | 0.1357 | 0.1211
Load_TR5_F5_63_dup | prosumer | 0.0819 | 0.183 | 0.053 | 0.0819 | 0.183 | 0.053 | 0.1685 | 0.0963 | 0.1681 | 0.1939 | 0.1397 | 0.053 | 0.1397 | 0.1252 | 0.1647 | 0.3331 | 0.053 | 0.1397 | 0.1252 | 0.1853 | 0.1902 | 0.053 | 0.0747 | 0.1902 | 0.053 | 0.3225 | 0.2173 | 0.4724 | 0.0602 | 0.2046 | 0.053 | 0.1685 | 0.0963 | 0.053 | 0.3736 | 0.3553 | 0.2568 | 0.7043 | 0.152 | 0.1541 | 0.1108 | 0.0963 | 0.1685 | 0.053 | 0.053 | 0.053 | 0.2119 | 0.053
Load_TR5_F5_64 | customer | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0881 | 0.1492 | 0.078 | 0.3517 | 0.2393 | 0.7223 | 0.16 | 0.1081 | 0.0654 | 0.063 | 0.2009 | 1.0877 | 0.05 | 0.2947 | 0.1569 | 0.0755 | 0.05 | 0.05 | 0.05 | 0.0764 | 0.0594 | 0.063 | 0.0808 | 0.108 | 0.109 | 0.222 | 0.281 | 0.3875 | 0.3728 | 0.6646 | 0.3971 | 0.4343 | 0.2032 | 0.05
Load_TR5_F5_64_dup | prosumer | 0.051 | 0.1652 | 0.1163 | 0.051 | 0.2305 | 0.051 | 0.051 | 0.2305 | 0.051 | 0.051 | 0.1734 | 0.1081 | 0.1244 | 0.202 | 0.3223 | 0.051 | 0.051 | 0.362 | 0.352 | 0.3273 | 0.2151 | 0.9552 | 1.0559 | 0.278 | 0.2506 | 0.2226 | 0.4168 | 0.2131 | 0.3112 | 0.3958 | 0.222 | 0.0673 | 0.2142 | 0.051 | 0.2305 | 0.235 | 0.0673 | 0.2544 | 1.3146 | 0.3925 | 0.5902 | 0.6028 | 0.1897 | 0.0918 | 0.051 | 0.051 | 0.2305 | 0.051
Load_TR5_F5_65 | customer | 0.1699 | 0.2249 | 0.1342 | 0.0867 | 0.0985 | 0.2172 | 0.1598 | 0.1402 | 0.2249 | 0.1699 | 0.051 | 0.2311 | 0.1637 | 0.1115 | 0.1104 | 0.2249 | 0.1699 | 0.051 | 0.6023 | 0.1242 | 0.0577 | 0.2085 | 0.4226 | 0.1362 | 0.2196 | 0.2776 | 0.3076 | 0.3124 | 0.4497 | 0.2934 | 0.3238 | 0.051 | 0.1699 | 0.051 | 0.3333 | 0.2733 | 0.3436 | 0.2467 | 0.4045 | 0.4927 | 0.2926 | 0.1461 | 0.1617 | 0.1974 | 0.1104 | 0.051 | 0.1699 | 0.051
Load_TR5_F5_65_dup | customer | 0.2515 | 0.047 | 0.047 | 0.047 | 0.0655 | 0.0952 | 0.047 | 0.047 | 0.047 | 0.1137 | 0.047 | 0.047 | 0.0639 | 0.3498 | 0.1454 | 0.3167 | 0.1699 | 0.1632 | 0.051 | 0.047 | 0.1274 | 0.535 | 0.51 | 1.6581 | 0.0838 | 0.0989 | 0.047 | 0.1137 | 0.047 | 0.1137 | 0.047 | 0.11 | 0.0507 | 0.073 | 0.0878 | 0.0804 | 0.0804 | 0.047 | 0.047 | 1.1001 | 0.4985 | 0.361 | 0.3427 | 0.5389 | 0.4685 | 0.047 | 0.047 | 0.047
Load_TR5_F5_66 | customer | 0.212 | 0.045 | 0.045 | 0.0839 | 0.0936 | 0.045 | 0.1325 | 0.045 | 0.1325 | 0.045 | 0.3983 | 0.9126 | 0.045 | 0.0839 | 0.2742 | 0.045 | 0.1325 | 0.045 | 0.1325 | 0.045 | 0.1325 | 0.045 | 0.045 | 0.045 | 0.045 | 0.0577 | 0.1674 | 0.8868 | 0.1131 | 0.0644 | 0.045 | 0.0596 | 0.1179 | 0.045 | 0.7624 | 0.2526 | 0.1846 | 0.3084 | 0.2468 | 0.3808 | 0.3304 | 0.2679 | 0.4425 | 0.2062 | 0.4303 | 0.3578 | 0.4429 | 0.3195
Load_TR5_F5_66_dup | customer | 0.9813 | 0.1472 | 0.1064 | 0.0792 | 0.1744 | 0.052 | 0.2015 | 0.052 | 0.052 | 0.2015 | 0.052 | 0.2482 | 0.375 | 0.3057 | 1.6382 | 0.2557 | 0.1864 | 1.3725 | 0.6005 | 0.336 | 0.2036 | 0.1568 | 0.2116 | 0.4692 | 0.3066 | 1.6178 | 0.4796 | 0.3206 | 0.2178 | 0.4643 | 0.307 | 0.4028 | 0.2773 | 0.3407 | 0.0799 | 0.3014 | 0.4272 | 0.1621 | 0.1815 | 0.1322 | 0.399 | 0.3582 | 0.3164 | 0.427 | 0.3172 | 0.5682 | 0.6157 | 0.3914
Load_TR5_F5_67 | customer | 0.0868 | 0.1328 | 0.1961 | 0.062 | 0.235 | 0.1187 | 0.1396 | 0.2016 | 0.0744 | 0.2172 | 0.0827 | 0.2427 | 0.0902 | 0.0909 | 0.5931 | 0.2416 | 1.2299 | 1.1313 | 0.157 | 1.1015 | 0.1676 | 0.1861 | 0.062 | 0.2916 | 0.062 | 0.062 | 0.062 | 0.2172 | 0.062 | 0.0827 | 0.271 | 0.0868 | 0.1116 | 0.1968 | 0.275 | 0.303 | 0.2302 | 0.2267 | 0.5471 | 0.2549 | 0.6117 | 1.0145 | 0.9037 | 0.7917 | 0.8681 | 0.9868 | 1.0182 | 0.9881
Load_TR5_F5_67_dup | customer | 0.1666 | 0.0791 | 0.206 | 0.1378 | 0.04 | 0.1004 | 0.219 | 0.072 | 0.218 | 0.1183 | 0.1456 | 0.1982 | 0.0475 | 0.2963 | 0.04 | 0.2812 | 0.0626 | 0.04 | 0.345 | 0.1597 | 0.1772 | 0.2766 | 0.1447 | 0.2192 | 0.9425 | 0.0898 | 0.2586 | 0.04 | 0.206 | 0.0449 | 0.2612 | 0.0777 | 0.1657 | 0.2263 | 0.0518 | 0.2835 | 0.0719 | 0.04 | 0.2771 | 0.198 | 0.0987 | 0.2451 | 0.04 | 0.1134 | 0.0645 | 0.206 | 0.1183 | 0.1803
Load_TR5_F5_68 | customer | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.1577 | 2.0225 | 1.3931 | 0.7118 | 0.2069 | 0.3145 | 0.2642 | 0.1365 | 0.0962 | 1.0261 | 0.2863 | 0.3113 | 2.0526 | 0.2112 | 0.2708 | 0.2882 | 1.0688 | 0.5452 | 0.2806 | 0.2161 | 1.5841 | 1.2024 | 2.6879 | 0.3722 | 0.0625 | 1.0314 | 1.0918 | 0.3027 | 0.3777 | 0.6409 | 0.7562 | 0.4878 | 0.5061 | 0.8122 | 0.6285
Load_TR5_F5_68_dup | customer | 0.1542 | 0.1936 | 0.2876 | 0.1937 | 0.2729 | 0.335 | 0.1377 | 0.1892 | 0.3853 | 0.1726 | 0.1126 | 0.3109 | 0.292 | 0.085 | 0.3615 | 0.1524 | 0.6001 | 0.2178 | 0.1806 | 0.3216 | 1.2755 | 0.5241 | 0.1072 | 0.3394 | 0.2124 | 0.288 | 0.2456 | 0.3831 | 0.3012 | 0.2634 | 0.1118 | 0.4961 | 0.2534 | 0.5712 | 0.3361 | 1.9078 | 2.9992 | 1.9639 | 0.5078 | 0.996 | 1.252 | 0.7337 | 0.4937 | 0.4208 | 0.2955 | 0.2408 | 0.251 | 0.1956
Load_TR5_F5_6_dup | prosumer | 0.057 | 0.057 | 0.1625 | 0.057 | 0.1399 | 0.0796 | 0.057 | 0.0796 | 0.1399 | 0.057 | 0.2046 | 0.0574 | 0.057 | 0.057 | 0.1625 | 0.0645 | 0.0899 | 0.1625 | 0.057 | 0.0796 | 0.1399 | 0.147 | 0.3221 | 0.4643 | 0.3853 | 0.4633 | 0.3216 | 0.2816 | 0.3524 | 0.3554 | 0.6279 | 2.4824 | 2.1222 | 0.5001 | 0.7752 | 0.1248 | 0.2147 | 0.1642 | 0.1976 | 0.1857 | 0.3768 | 0.3922 | 0.4722 | 2.0539 | 0.9946 | 0.6454 | 0.7827 | 0.6819
Load_TR5_F5_7 | prosumer | 0.047 | 0.0631 | 0.1033 | 0.047 | 0.1074 | 0.0591 | 0.047 | 0.1194 | 0.047 | 0.047 | 0.3684 | 0.5273 | 0.2392 | 1.2453 | 0.1194 | 0.1157 | 1.1462 | 0.2295 | 0.062 | 0.1223 | 0.047 | 0.0519 | 0.0797 | 0.9226 | 0.1635 | 0.0494 | 1.2649 | 0.7976 | 1.6522 | 0.3978 | 1.3484 | 1.5358 | 0.2534 | 0.0872 | 0.0792 | 0.1114 | 0.055 | 0.1317 | 0.0683 | 0.1784 | 0.2842 | 0.2522 | 0.3941 | 0.5589 | 0.3826 | 0.2853 | 0.1015 | 0.1194
Load_TR5_F5_7_dup | customer | 0.2773 | 0.162 | 0.1682 | 0.2243 | 0.1039 | 0.2886 | 0.1258 | 0.0892 | 0.3761 | 0.053 | 0.1233 | 0.2731 | 0.1516 | 0.2425 | 0.2122 | 0.053 | 0.3141 | 0.2588 | 0.3338 | 0.4755 | 0.2246 | 0.5516 | 0.4198 | 0.3497 | 0.5712 | 0.2435 | 0.053 | 0.3869 | 0.0987 | 0.1924 | 0.2257 | 0.7434 | 0.3385 | 1.583 | 2.4484 | 0.1577 | 0.2075 | 0.3072 | 1.055 | 1.1555 | 0.1326 | 0.4645 | 0.5773 | 0.7764 | 0.1218 | 0.053 | 0.2244 | 0.1455
Load_TR5_F5_8 | customer | 0.1733 | 0.053 | 0.1923 | 0.053 | 0.0743 | 0.3747 | 0.3153 | 0.4052 | 0.072 | 0.1037 | 0.1416 | 0.053 | 0.1923 | 0.053 | 0.186 | 0.0593 | 0.1416 | 0.2863 | 0.263 | 0.167 | 0.053 | 0.3006 | 0.1237 | 0.064 | 0.196 | 0.053 | 0.053 | 0.148 | 0.0973 | 0.053 | 0.1923 | 0.053 | 0.148 | 0.0973 | 0.1054 | 0.2342 | 0.1799 | 0.1909 | 0.3023 | 0.2922 | 0.6109 | 0.4868 | 0.5663 | 0.5397 | 0.4442 | 0.2537 | 0.4055 | 0.2542
Load_TR5_F5_8_dup | customer | 0.2287 | 0.0661 | 0.058 | 0.2369 | 0.058 | 0.0661 | 0.2287 | 0.058 | 0.058 | 0.1799 | 0.1149 | 0.058 | 0.058 | 0.2369 | 0.058 | 1.1757 | 0.9222 | 0.5571 | 0.4049 | 0.3412 | 0.3834 | 0.4632 | 0.058 | 0.2369 | 0.058 | 0.1556 | 0.1393 | 0.1068 | 0.1881 | 0.058 | 0.2043 | 0.0905 | 0.2599 | 0.4005 | 0.1915 | 0.3678 | 1.4582 | 0.1546 | 0.3069 | 0.4141 | 0.7611 | 0.8146 | 0.764 | 0.7544 | 0.8717 | 0.796 | 0.5873 | 0.6957
Load_TR5_F5_9 | customer | 0.0699 | 0.1857 | 0.057 | 0.057 | 0.1986 | 0.057 | 0.057 | 0.1986 | 0.057 | 0.057 | 0.1986 | 0.057 | 0.1986 | 0.057 | 0.0699 | 0.1857 | 0.1775 | 0.1381 | 0.1372 | 0.082 | 0.0932 | 0.1857 | 0.085 | 0.2521 | 0.1276 | 0.2303 | 0.2722 | 1.6293 | 0.1809 | 0.1471 | 0.057 | 0.057 | 0.1986 | 0.057 | 0.057 | 0.1986 | 0.0859 | 1.6308 | 0.2512 | 0.2858 | 0.2759 | 0.4275 | 1.9528 | 3.0319 | 1.9149 | 0.3866 | 0.6175 | 0.2743
Load_TR5_F5_9_dup | customer | 0.048 | 0.2013 | 0.0821 | 0.048 | 0.1076 | 0.1757 | 0.048 | 0.2183 | 0.065 | 0.0906 | 0.1928 | 0.048 | 0.2354 | 0.048 | 0.1928 | 0.0906 | 0.048 | 0.4277 | 0.048 | 0.0565 | 0.2268 | 0.048 | 0.2098 | 0.0735 | 0.048 | 0.048 | 0.2268 | 0.0565 | 0.0821 | 0.2013 | 0.048 | 0.2098 | 0.1506 | 0.2241 | 0.1742 | 0.0803 | 0.2225 | 0.0669 | 0.052 | 0.3594 | 0.2182 | 0.5435 | 0.6771 | 0.5357 | 0.532 | 0.7992 | 0.4225 | 0.5829
Load_TR5_F6_1 | prosumer | 0.0448 | 0.5474 | 0.036 | 0.036 | 0.036 | 0.036 | 0.1156 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.1156 | 0.036 | 0.3255 | 0.5635 | 1.5095 | 0.2534 | 0.1749 | 0.1156 | 0.036 | 0.0493 | 0.1023 | 0.3886 | 0.2418 | 0.2956 | 0.2912 | 0.1618 | 0.1248 | 0.036 | 0.1156 | 0.066 | 0.1375 | 0.179 | 1.3505 | 1.4529 | 0.8498 | 1.4862 | 0.3579 | 0.2689 | 0.6166 | 0.2661 | 0.3264 | 0.3093 | 0.1107 | 0.143 | 0.2253
Load_TR5_F6_10 | customer | 0.045 | 0.2389 | 0.1 | 0.1265 | 0.045 | 0.2412 | 0.0929 | 0.167 | 0.0809 | 0.124 | 0.2101 | 0.045 | 0.2242 | 0.0785 | 0.1982 | 0.136 | 0.0977 | 0.0683 | 0.2269 | 0.1325 | 0.2131 | 0.8326 | 0.3795 | 0.242 | 0.2884 | 0.1309 | 1.4995 | 0.1447 | 0.1455 | 0.1024 | 0.1336 | 0.2006 | 0.0977 | 0.179 | 0.1024 | 0.1313 | 0.1024 | 0.2317 | 0.045 | 0.2342 | 0.2913 | 0.045 | 0.045 | 0.214 | 0.3974 | 0.6843 | 1.0241 | 0.349
Load_TR5_F6_11 | prosumer | 0.2212 | 0.3531 | 0.05 | 0.1677 | 0.1734 | 0.0606 | 0.2375 | 0.0929 | 0.0684 | 0.1665 | 0.05 | 0.1849 | 0.05 | 0.2604 | 0.0807 | 0.119 | 0.222 | 0.05 | 0.1562 | 0.215 | 1.4153 | 0.2488 | 0.2172 | 0.3421 | 0.3044 | 0.1118 | 0.2006 | 0.157 | 0.1968 | 0.2462 | 0.2997 | 0.296 | 0.2588 | 0.3301 | 0.2229 | 0.231 | 0.0978 | 0.1289 | 0.2122 | 0.0623 | 0.1885 | 0.1403 | 0.0807 | 0.2604 | 0.05 | 0.2253 | 0.1158 | 0.119
Load_TR5_F6_12 | prosumer | 0.1915 | 0.1234 | 0.056 | 0.056 | 0.056 | 0.1274 | 0.056 | 0.1274 | 0.056 | 0.056 | 0.056 | 0.1075 | 0.0758 | 0.056 | 0.1274 | 0.056 | 0.1009 | 0.0907 | 0.1548 | 0.1547 | 0.1127 | 0.2574 | 0.0748 | 0.1124 | 0.1378 | 0.1094 | 0.1269 | 0.0838 | 0.0996 | 0.06 | 0.1234 | 0.056 | 0.056 | 0.1234 | 0.0642 | 0.2458 | 0.1797 | 0.1328 | 0.1495 | 0.2801 | 0.4979 | 0.3696 | 0.4218 | 0.6017 | 0.5337 | 0.5687 | 0.2065 | 0.153
Load_TR5_F6_13 | customer | 0.1541 | 0.1652 | 0.1919 | 0.0724 | 0.2847 | 0.048 | 0.1812 | 0.1759 | 0.115 | 0.1382 | 0.1519 | 0.1333 | 0.048 | 0.1119 | 0.2452 | 0.048 | 0.1055 | 0.0845 | 0.2233 | 0.2497 | 0.064 | 0.2079 | 0.048 | 0.1784 | 0.2497 | 0.087 | 0.1537 | 0.3676 | 0.2884 | 0.1419 | 0.2199 | 0.0879 | 0.3228 | 0.2568 | 0.3564 | 0.3397 | 0.4669 | 0.7322 | 0.2445 | 0.7912 | 0.5075 | 0.9449 | 0.5039 | 0.6473 | 0.7359 | 0.5721 | 0.7273 | 0.6422
Load_TR5_F6_14 | prosumer | 0.1529 | 0.2676 | 0.0835 | 0.1167 | 0.057 | 0.2786 | 0.0872 | 0.3091 | 0.1406 | 0.0809 | 0.3805 | 0.1198 | 0.1462 | 0.1846 | 0.1282 | 0.1606 | 1.4699 | 0.4402 | 0.0916 | 0.373 | 0.0756 | 1.3816 | 0.1391 | 0.6021 | 1.2178 | 0.7337 | 1.1142 | 0.1517 | 0.3379 | 1.4759 | 0.3771 | 0.3597 | 0.053 | 0.2252 | 0.1796 | 0.1809 | 0.1972 | 0.1323 | 0.2258 | 0.1979 | 0.1809 | 0.2358 | 0.1127 | 0.1862 | 0.1247 | 0.2825 | 0.1222 | 0.0729
Load_TR5_F6_15 | customer | 0.3685 | 0.5276 | 0.3931 | 0.8988 | 0.7414 | 0.1857 | 0.0699 | 0.2155 | 0.1407 | 0.1705 | 0.1857 | 0.1217 | 0.1895 | 0.1021 | 0.136 | 0.2202 | 0.057 | 0.2284 | 0.1278 | 0.2719 | 0.3669 | 0.1709 | 0.1986 | 0.1576 | 0.1729 | 0.1474 | 0.2109 | 0.4503 | 1.0682 | 1.6791 | 0.4718 | 1.2665 | 2.8557 | 2.4254 | 0.208 | 0.2721 | 0.0914 | 0.136 | 0.057 | 0.2348 | 0.1214 | 0.0763 | 0.2008 | 0.136 | 0.1021 | 0.2541 | 0.057 | 0.1902
Load_TR5_F6_16 | prosumer | 0.059 | 0.059 | 0.2475 | 0.495 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.059 | 0.3497 | 0.274 | 0.2133 | 0.2347 | 0.6435 | 0.4666 | 0.4435 | 0.1548 | 0.2045 | 0.8394 | 0.8519 | 0.5689 | 0.8798 | 1.052 | 0.8887 | 0.6936 | 0.9027 | 0.9848
Load_TR5_F6_17 | prosumer | 0.2391 | 0.2864 | 0.3623 | 0.3464 | 0.2875 | 0.1838 | 0.2102 | 0.049 | 0.1575 | 0.1235 | 0.2277 | 0.2194 | 0.1746 | 0.049 | 0.0645 | 0.3107 | 0.0678 | 0.1723 | 0.2252 | 0.0546 | 0.2033 | 0.1907 | 0.049 | 0.2827 | 1.7341 | 0.201 | 0.2496 | 0.3451 | 0.049 | 0.2221 | 0.6663 | 0.9572 | 1.8108 | 0.0901 | 0.1509 | 0.2614 | 0.1467 | 0.1687 | 0.3086 | 0.2534 | 0.5052 | 0.281 | 0.1607 | 1.0805 | 0.3702 | 0.3643 | 0.3372 | 0.4975
Load_TR5_F6_18 | prosumer | 0.3318 | 0.181 | 0.1156 | 0.3487 | 0.0965 | 0.1867 | 0.3261 | 0.048 | 0.0965 | 0.2681 | 0.2377 | 0.1451 | 0.1243 | 0.1173 | 0.3192 | 0.2066 | 0.884 | 1.2909 | 0.1173 | 0.5455 | 0.1407 | 0.0809 | 0.3972 | 0.0827 | 0.2339 | 0.279 | 0.0896 | 0.1451 | 0.2438 | 0.1303 | 0.2075 | 0.1243 | 0.2724 | 0.2404 | 0.0891 | 0.3405 | 0.1312 | 0.1867 | 0.9113 | 1.1169 | 0.0886 | 0.6369 | 0.2848 | 0.1061 | 0.2283 | 0.2291 | 0.1728 | 0.233
Load_TR5_F6_19 | customer | 0.2038 | 0.2515 | 0.177 | 0.1297 | 0.321 | 0.1342 | 0.292 | 0.1632 | 0.0819 | 0.2898 | 0.1375 | 0.0629 | 0.3923 | 0.0807 | 0.1423 | 0.4946 | 0.1747 | 0.1098 | 0.4392 | 0.248 | 0.3152 | 0.2896 | 0.1117 | 0.2299 | 0.1676 | 0.2074 | 0.5401 | 1.0435 | 0.6218 | 0.5208 | 0.3581 | 0.1525 | 0.3148 | 0.0985 | 0.1237 | 0.3181 | 0.0674 | 0.298 | 0.1572 | 0.054 | 0.2876 | 0.054 | 0.3384 | 0.1168 | 0.213 | 0.0888 | 0.2039 | 0.1712
Load_TR5_F6_2 | prosumer | 0.058 | 0.1538 | 0.058 | 0.0793 | 0.1325 | 0.058 | 0.1272 | 0.0846 | 0.058 | 0.058 | 0.058 | 0.058 | 0.058 | 0.058 | 0.058 | 0.6774 | 0.1014 | 0.058 | 0.1538 | 0.058 | 0.058 | 0.1219 | 0.0899 | 0.1325 | 0.0793 | 0.1538 | 0.058 | 0.1485 | 0.0633 | 0.058 | 0.058 | 0.1538 | 0.0658 | 0.6657 | 0.929 | 3.0564 | 1.2492 | 0.1047 | 0.3848 | 0.9896 | 0.9508 | 0.9615 | 0.9669 | 1.5751 | 1.2932 | 0.5812 | 0.215 | 0.1538
Load_TR5_F6_20 | customer | 0.1441 | 0.2408 | 0.0931 | 0.2692 | 0.087 | 0.0882 | 0.1762 | 0.2076 | 0.052 | 0.1424 | 0.2422 | 0.0874 | 0.2124 | 0.1911 | 0.2761 | 0.1 | 2.6083 | 0.7384 | 0.3578 | 0.1544 | 0.1265 | 0.4636 | 0.15 | 0.3697 | 0.2912 | 0.0661 | 0.122 | 0.2485 | 0.1015 | 0.0746 | 0.1198 | 0.2076 | 0.107 | 0.3043 | 0.1085 | 0.1884 | 0.2423 | 0.3052 | 0.2754 | 0.4409 | 0.2707 | 0.4665 | 0.6354 | 0.5129 | 0.4493 | 0.2126 | 0.159 | 0.3062
Load_TR5_F6_21 | prosumer | 0.0876 | 0.2484 | 0.2156 | 0.2134 | 0.107 | 0.2323 | 0.1418 | 0.2692 | 0.3493 | 0.1423 | 0.105 | 0.3866 | 0.06 | 0.2979 | 0.1108 | 0.2639 | 0.1816 | 0.2726 | 0.1308 | 0.2974 | 0.1974 | 1.6122 | 2.2364 | 2.7946 | 1.935 | 0.1849 | 0.1944 | 0.1599 | 0.244 | 0.23 | 0.0776 | 0.2958 | 0.1958 | 0.06 | 0.314 | 0.1776 | 0.2218 | 0.1711 | 1.1823 | 0.4092 | 0.7101 | 0.5787 | 0.3714 | 0.3351 | 0.642 | 0.4748 | 0.6255 | 0.3495
Load_TR5_F6_22 | prosumer | 0.4529 | 0.7211 | 0.049 | 0.1174 | 0.177 | 0.049 | 0.1062 | 0.2492 | 1.12 | 0.049 | 0.129 | 0.0833 | 0.1999 | 0.3737 | 0.2004 | 0.0547 | 0.1576 | 0.1043 | 0.5314 | 1.0759 | 0.8968 | 0.2926 | 0.2218 | 0.0639 | 0.3191 | 0.1533 | 0.1389 | 0.2308 | 0.4381 | 0.4737 | 0.4057 | 0.203 | 0.207 | 0.3757 | 0.329 | 0.7066 | 1.7498 | 0.2189 | 0.4275 | 0.4256 | 0.6883 | 0.6409 | 0.4875 | 0.5374 | 0.4898 | 0.5953 | 0.5859 | 0.2508
Load_TR5_F6_23 | customer | 0.1969 | 0.123 | 0.2061 | 0.1955 | 0.2973 | 0.1224 | 0.2607 | 0.1028 | 0.2665 | 0.048 | 0.2486 | 0.2442 | 0.1715 | 0.1945 | 0.2983 | 0.048 | 0.3017 | 1.1671 | 0.3453 | 0.1976 | 0.2474 | 0.2911 | 0.2973 | 0.2483 | 1.3149 | 0.2858 | 0.6155 | 0.4623 | 0.1458 | 0.2907 | 0.0789 | 0.3023 | 0.167 | 0.1468 | 0.1432 | 0.4045 | 0.4175 | 0.4893 | 0.4644 | 0.4778 | 0.6627 | 0.8628 | 0.6131 | 0.4316 | 1.5221 | 0.5488 | 0.4713 | 0.3625
Load_TR5_F6_24 | prosumer | 0.058 | 0.2154 | 0.1399 | 0.1485 | 0.1504 | 0.045 | 0.251 | 0.0827 | 0.1757 | 0.158 | 0.11 | 0.2161 | 0.1088 | 0.156 | 0.3082 | 0.3454 | 0.0926 | 0.4006 | 0.0957 | 0.4303 | 2.8929 | 4.0691 | 0.3716 | 0.3012 | 0.1815 | 0.1805 | 0.0839 | 0.466 | 0.1951 | 0.1973 | 0.2963 | 0.0617 | 0.115 | 0.2925 | 0.3449 | 0.315 | 0.4297 | 0.6731 | 0.4026 | 0.8174 | 0.5706 | 0.5609 | 1.0507 | 0.7091 | 1.0106 | 0.8502 | 0.8704 | 0.7288
Load_TR5_F6_25 | customer | 0.2062 | 0.071 | 0.1245 | 0.2212 | 0.056 | 0.1837 | 0.0936 | 0.1092 | 0.2366 | 0.056 | 0.056 | 0.1131 | 0.1951 | 0.0936 | 0.1245 | 0.1536 | 0.1921 | 0.1086 | 0.1687 | 0.056 | 0.2212 | 0.1245 | 0.2102 | 0.1501 | 0.0785 | 0.2672 | 0.056 | 0.2212 | 0.1207 | 0.1349 | 0.1461 | 0.1245 | 0.2212 | 0.0788 | 0.2294 | 0.1111 | 0.2172 | 0.2192 | 0.3209 | 0.3431 | 0.3085 | 0.3239 | 0.5697 | 0.6771 | 0.4264 | 0.1762 | 0.1131 | 0.2176
Load_TR5_F6_26 | prosumer | 0.1526 | 0.1 | 0.054 | 0.1788 | 0.0737 | 0.054 | 0.0934 | 0.1591 | 0.054 | 0.1328 | 0.1197 | 0.0671 | 0.1854 | 0.054 | 0.1985 | 0.054 | 0.054 | 0.1985 | 0.054 | 0.0939 | 0.1985 | 0.054 | 0.2163 | 0.3116 | 0.121 | 0.3437 | 0.6174 | 1.0944 | 0.2013 | 0.1589 | 0.2923 | 1.5798 | 0.6559 | 0.1468 | 0.6136 | 0.8583 | 0.1985 | 0.2046 | 0.5671 | 0.5117 | 0.4292 | 0.6287 | 0.1024 | 0.0934 | 0.1591 | 0.054 | 0.1985 | 0.054
Load_TR5_F6_27 | customer | 0.054 | 0.0731 | 0.1038 | 0.054 | 0.054 | 0.1229 | 0.054 | 0.054 | 0.1229 | 0.054 | 0.077 | 0.1 | 0.054 | 0.1229 | 0.054 | 0.054 | 0.054 | 0.1277 | 0.0687 | 0.2579 | 0.1916 | 0.4242 | 0.1533 | 0.2119 | 0.054 | 0.3318 | 0.0691 | 1.7571 | 0.8319 | 0.3411 | 0.071 | 0.1409 | 1.2843 | 0.2309 | 1.2933 | 0.2684 | 1.1482 | 1.3834 | 1.1703 | 0.2139 | 0.4556 | 0.3473 | 0.3088 | 0.3942 | 0.2872 | 0.4668 | 0.2846 | 0.5773
Load_TR5_F6_28 | customer | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.2087 | 0.4588 | 0.2181 | 0.3272 | 0.039 | 0.039 | 0.56 | 0.0443 | 0.0594 | 0.1097 | 0.0657 | 0.039 | 0.039 | 0.0433 | 0.2464 | 0.052 | 0.0429 | 0.0395 | 0.1041 | 0.0557 | 0.039 | 0.0403 | 0.2639 | 0.4199 | 0.1892 | 0.039 | 0.1486 | 0.2908
Load_TR5_F6_29 | customer | 0.1284 | 0.7642 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.05 | 0.0533 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.0586 | 0.079 | 0.0862 | 0.0901 | 0.1878 | 0.0948 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045
Load_TR5_F6_3 | prosumer | 0.047 | 0.1129 | 0.2229 | 0.047 | 0.2025 | 0.1333 | 0.1276 | 0.1129 | 0.1423 | 0.1935 | 0.047 | 0.1423 | 0.1495 | 0.0909 | 0.1452 | 0.7776 | 0.6193 | 0.2526 | 0.2022 | 1.1421 | 0.2015 | 0.142 | 0.3084 | 0.1824 | 0.0898 | 0.109 | 1.2372 | 0.0568 | 0.2318 | 0.104 | 0.1202 | 0.3321 | 0.0989 | 0.2108 | 0.1891 | 0.2989 | 0.8841 | 0.5946 | 0.2669 | 0.2912 | 0.717 | 0.9735 | 1.0996 | 0.6205 | 0.8204 | 1.0617 | 0.6889 | 0.8118
Load_TR5_F6_30 | prosumer | 0.5043 | 0.2554 | 0.0737 | 0.1518 | 0.0737 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057 | 0.1629 | 0.0626 | 0.1072 | 0.2167 | 0.2087 | 0.0846 | 0.0622 | 0.1109 | 0.7985 | 0.4939 | 0.3321 | 0.2551 | 0.2757 | 0.2329 | 0.3484 | 0.195 | 0.1685 | 0.057 | 0.057 | 0.1685 | 0.057 | 0.1685 | 0.057 | 1.6375 | 0.2988 | 0.2232 | 0.2614 | 1.7822 | 0.4019 | 0.3161 | 0.5133 | 0.4884 | 0.4682 | 0.7278 | 0.383 | 0.4021 | 2.9514 | 0.1183
Load_TR5_F6_31 | prosumer | 0.04 | 0.04 | 0.2795 | 0.0599 | 0.04 | 0.2674 | 0.072 | 0.1757 | 0.1638 | 0.04 | 0.0996 | 0.0638 | 0.12 | 0.2194 | 0.1485 | 0.4513 | 0.497 | 1.4364 | 0.484 | 0.3591 | 0.08 | 0.173 | 0.221 | 0.3028 | 0.04 | 0.2994 | 0.1282 | 1.318 | 0.2844 | 0.065 | 0.279 | 0.239 | 0.1708 | 0.3545 | 0.1764 | 0.2868 | 0.3024 | 0.1614 | 0.3896 | 0.5299 | 0.3562 | 0.9073 | 0.6125 | 0.7045 | 0.5039 | 0.4965 | 1.3449 | 1.1192
Load_TR5_F6_32 | prosumer | 0.06 | 0.06 | 0.0762 | 0.1519 | 0.06 | 0.1682 | 0.06 | 0.087 | 0.1411 | 0.06 | 0.06 | 0.1682 | 0.06 | 0.0816 | 0.1465 | 0.06 | 0.1682 | 0.06 | 0.1682 | 0.06 | 0.288 | 0.0886 | 0.0734 | 0.2233 | 0.2644 | 0.24 | 0.3487 | 0.0708 | 0.0708 | 0.1574 | 0.06 | 0.1682 | 0.06 | 0.06 | 0.1682 | 0.06 | 0.1465 | 0.0816 | 0.0979 | 0.1303 | 0.5365 | 0.3591 | 0.3156 | 0.711 | 1.0468 | 0.6216 | 0.3007 | 0.06
Load_TR5_F6_33 | customer | 0.0511 | 0.2532 | 0.047 | 0.1955 | 0.1088 | 0.047 | 0.184 | 0.104 | 0.0633 | 0.1702 | 0.1342 | 0.0674 | 0.2369 | 0.0918 | 0.0942 | 0.2305 | 0.0551 | 0.1155 | 0.1888 | 0.0719 | 0.2324 | 0.047 | 0.2286 | 0.0758 | 0.049 | 0.1767 | 0.2606 | 0.9466 | 0.1574 | 0.5748 | 1.0192 | 0.2326 | 0.0717 | 1.141 | 0.5292 | 0.1868 | 0.2777 | 0.1204 | 0.1507 | 0.7296 | 0.5665 | 0.5426 | 0.533 | 0.5947 | 0.7596 | 0.5536 | 0.307 | 0.3636
Load_TR5_F6_34 | prosumer | 0.2428 | 0.1656 | 0.1179 | 0.2981 | 0.0662 | 0.199 | 0.2641 | 0.1656 | 0.2096 | 0.1511 | 0.1551 | 0.2394 | 0.1776 | 0.182 | 0.2293 | 0.1019 | 0.1253 | 0.3416 | 0.054 | 0.2905 | 0.1764 | 0.2261 | 0.1853 | 0.2493 | 1.6693 | 0.3631 | 0.2478 | 0.2691 | 0.1564 | 0.1437 | 0.2668 | 0.1834 | 0.4272 | 0.2346 | 0.1416 | 0.187 | 0.1947 | 0.246 | 0.5057 | 0.2185 | 0.2973 | 1.3056 | 1.3146 | 0.4875 | 0.4787 | 0.4399 | 0.5752 | 0.3877
Load_TR5_F6_35 | prosumer | 0.4891 | 0.5625 | 0.2211 | 0.0815 | 0.1952 | 0.1362 | 0.0995 | 0.05 | 0.3568 | 0.2387 | 0.1447 | 0.05 | 0.3114 | 0.1652 | 0.1223 | 1.0395 | 1.2127 | 0.1489 | 0.287 | 1.1096 | 0.4016 | 0.4204 | 0.6723 | 0.2471 | 0.2318 | 0.0995 | 0.05 | 0.3213 | 0.131 | 0.1593 | 0.2858 | 0.1944 | 0.1867 | 0.05 | 0.1252 | 0.2017 | 0.0545 | 0.1993 | 0.132 | 0.122 | 0.1957 | 0.1447 | 0.05 | 0.05 | 0.2003 | 0.05 | 0.0725 | 0.2042
Load_TR5_F6_36 | customer | 0.042 | 0.161 | 0.042 | 0.161 | 0.042 | 0.042 | 0.3236 | 0.4503 | 0.042 | 0.127 | 0.076 | 0.042 | 0.161 | 0.042 | 0.144 | 0.059 | 0.042 | 0.127 | 0.076 | 0.042 | 0.161 | 0.042 | 0.1355 | 0.0675 | 0.042 | 0.11 | 0.093 | 0.042 | 0.161 | 0.042 | 0.144 | 0.0888 | 0.093 | 0.0453 | 0.4517 | 1.3812 | 0.1567 | 0.1786 | 0.075 | 0.4192 | 0.4132 | 0.1967 | 0.2087 | 0.2496 | 0.161 | 0.042 | 0.042 | 0.144
Load_TR5_F6_37 | customer | 0.046 | 0.1513 | 0.192 | 0.046 | 0.2032 | 0.14 | 0.0946 | 0.1108 | 0.1588 | 0.1844 | 0.1087 | 0.1212 | 0.1594 | 0.1839 | 0.1027 | 0.1027 | 0.1651 | 0.3529 | 0.4281 | 0.2837 | 0.677 | 1.4753 | 0.4508 | 0.2195 | 1.0768 | 3.1819 | 2.5924 | 0.154 | 0.2346 | 0.1087 | 0.0648 | 0.2716 | 0.0762 | 0.2553 | 0.3393 | 0.596 | 0.4252 | 0.4603 | 1.7345 | 0.4796 | 0.3892 | 0.6534 | 0.5008 | 0.4201 | 0.5736 | 0.752 | 0.4463 | 0.1808
Load_TR5_F6_38 | prosumer | 0.268 | 0.051 | 0.0654 | 0.1954 | 0.051 | 0.2099 | 0.051 | 0.051 | 0.1954 | 0.0654 | 0.051 | 0.051 | 0.051 | 0.2099 | 0.051 | 0.1232 | 0.1377 | 0.0727 | 0.1882 | 0.3513 | 0.2743 | 0.0653 | 0.1883 | 0.3346 | 0.0731 | 1.3607 | 0.4651 | 0.1136 | 0.1088 | 0.1521 | 0.0654 | 0.2002 | 0.1037 | 1.0912 | 0.7906 | 0.1085 | 0.1088 | 0.1521 | 0.051 | 0.2099 | 0.051 | 0.1593 | 0.1016 | 0.051 | 0.051 | 0.1449 | 0.116 | 0.0871
Load_TR5_F6_39 | prosumer | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.0852 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.1094 | 0.0783 | 0.052 | 0.052 | 0.0696 | 0.0849 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.082 | 1.2447 | 0.0629 | 1.393 | 1.1352 | 0.9096 | 0.1507 | 0.2499 | 0.4295 | 0.4142 | 0.2332 | 0.3313 | 0.5001 | 0.052
Load_TR5_F6_4 | customer | 0.04 | 0.04 | 0.1157 | 0.04 | 0.04 | 0.04 | 0.1157 | 0.04 | 0.1157 | 0.04 | 0.04 | 0.0694 | 0.0863 | 0.0694 | 0.0863 | 0.04 | 0.0905 | 0.2748 | 0.0758 | 0.1057 | 0.0694 | 0.0863 | 0.0905 | 0.0652 | 0.04 | 0.1398 | 0.1021 | 0.2664 | 0.1229 | 0.0427 | 0.04 | 0.04 | 0.0675 | 0.1743 | 0.182 | 0.1983 | 0.4952 | 0.2202 | 0.2605 | 0.2996 | 0.4752 | 0.4464 | 0.4569 | 0.4989 | 0.0989 | 0.0484 | 0.1073 | 0.04
Load_TR5_F6_40 | prosumer | 0.1222 | 0.0988 | 0.0724 | 0.112 | 0.1566 | 0.1252 | 0.046 | 0.2226 | 0.046 | 0.046 | 0.2138 | 0.0548 | 0.0669 | 0.1226 | 0.0724 | 0.1962 | 0.0822 | 1.6775 | 0.2348 | 0.2783 | 0.2247 | 0.2024 | 0.0944 | 0.2006 | 0.068 | 0.0599 | 0.2186 | 0.0687 | 0.2285 | 0.046 | 0.1353 | 0.1361 | 0.1566 | 0.112 | 0.0947 | 0.0947 | 0.0724 | 0.1962 | 0.046 | 0.2852 | 0.5555 | 0.6093 | 0.5494 | 0.5034 | 0.6523 | 0.6255 | 0.5886 | 0.297
Load_TR5_F6_41 | prosumer | 0.1878 | 0.0934 | 0.0789 | 0.2422 | 0.0749 | 0.0989 | 0.2182 | 0.0749 | 0.0829 | 0.1009 | 0.1443 | 0.051 | 0.2661 | 0.0704 | 0.1735 | 0.1226 | 0.0505 | 0.0909 | 0.2262 | 0.043 | 0.043 | 0.2741 | 0.043 | 0.2162 | 0.1009 | 0.043 | 0.1878 | 0.0934 | 0.1368 | 0.1443 | 0.043 | 0.2023 | 0.043 | 0.043 | 0.1516 | 0.0937 | 0.0789 | 0.2382 | 0.078 | 0.3092 | 0.5685 | 0.6423 | 0.5837 | 0.6877 | 0.777 | 0.1995 | 0.2154 | 0.1017
Load_TR5_F6_42 | customer | 0.2955 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.0746 | 0.0772 | 1.3101 | 0.0548 | 0.059 | 0.8867 | 0.1616 | 0.1514 | 0.9392 | 0.1708 | 0.229 | 0.2835 | 0.3332 | 0.3157 | 0.3673 | 0.3171 | 0.7157 | 1.2626 | 1.8529 | 0.9155 | 0.5827 | 0.0893 | 0.387 | 0.2997 | 0.2483 | 0.3013 | 0.4079 | 0.1858 | 0.2151 | 0.2907 | 0.5497 | 0.869 | 0.568 | 0.4183
Load_TR5_F6_43 | customer | 0.05 | 0.1099 | 0.2372 | 0.05 | 0.0873 | 0.246 | 0.0638 | 0.2069 | 0.1402 | 0.0546 | 0.1283 | 0.05 | 0.0926 | 0.2545 | 0.05 | 0.2594 | 0.3872 | 0.2143 | 0.6635 | 0.2055 | 0.3645 | 0.3433 | 0.2278 | 2.507 | 2.9783 | 1.1211 | 0.1022 | 0.05 | 0.2598 | 0.0873 | 0.1817 | 0.1654 | 0.05 | 0.4112 | 0.4021 | 0.304 | 0.2329 | 0.122 | 0.7709 | 0.6864 | 0.542 | 0.6702 | 0.6488 | 0.6512 | 0.9717 | 0.8049 | 0.9231 | 0.643
Load_TR5_F6_44 | prosumer | 0.1688 | 0.058 | 0.4248 | 0.058 | 0.3454 | 0.1467 | 0.1617 | 0.3118 | 0.058 | 0.3285 | 0.0703 | 0.2342 | 0.2487 | 0.0725 | 0.4103 | 0.058 | 0.4856 | 0.298 | 0.3029 | 0.4455 | 0.1514 | 0.142 | 0.2105 | 0.0884 | 0.242 | 0.2177 | 0.1196 | 0.2684 | 0.2021 | 0.1754 | 0.2395 | 0.0767 | 0.1233 | 0.3884 | 0.5153 | 0.6219 | 0.4736 | 0.5993 | 0.386 | 0.584 | 0.7459 | 0.5167 | 0.5461 | 0.8996 | 0.8048 | 0.4731 | 0.1244 | 0.1835
Load_TR5_F6_45 | prosumer | 0.043 | 0.1998 | 0.181 | 0.0914 | 0.2023 | 0.2237 | 0.3398 | 0.3605 | 0.0606 | 0.2615 | 0.1194 | 0.043 | 0.3379 | 0.043 | 0.3144 | 0.0665 | 0.085 | 0.3966 | 0.146 | 0.2293 | 0.1558 | 0.1488 | 0.2321 | 0.1722 | 1.5675 | 0.1161 | 0.1371 | 0.2557 | 0.2127 | 0.1036 | 0.4396 | 0.0645 | 0.3205 | 0.1138 | 0.1906 | 0.4306 | 0.2453 | 0.3648 | 0.1564 | 0.3106 | 0.2503 | 0.2203 | 0.1344 | 0.467 | 0.3449 | 0.539 | 0.5155 | 0.3261
Load_TR5_F6_46 | customer | 0.0978 | 0.1695 | 0.1861 | 0.0693 | 0.1506 | 0.1765 | 0.0909 | 0.1506 | 0.0978 | 0.2293 | 0.0883 | 0.1073 | 0.1865 | 0.1406 | 0.055 | 0.2721 | 0.1377 | 0.4332 | 1.3541 | 0.9047 | 1.6645 | 0.1649 | 0.2112 | 0.6779 | 0.0807 | 0.5309 | 0.3194 | 0.4152 | 0.2753 | 0.3498 | 0.2516 | 0.2724 | 0.4144 | 1.2455 | 1.3787 | 2.0517 | 0.4016 | 0.6731 | 1.4612 | 1.2282 | 1.4504 | 0.3198 | 0.3123 | 0.4672 | 0.4559 | 0.5478 | 0.3485 | 0.0729
Load_TR5_F6_47 | prosumer | 0.1016 | 0.048 | 0.048 | 0.2166 | 0.048 | 0.1476 | 0.117 | 0.0557 | 0.2089 | 0.048 | 0.048 | 0.2166 | 0.0549 | 0.0556 | 0.1246 | 0.1597 | 0.3059 | 0.3049 | 0.0922 | 0.0633 | 0.3028 | 0.168 | 0.048 | 0.048 | 0.2166 | 0.048 | 0.0708 | 0.2066 | 0.0935 | 0.3235 | 1.0794 | 0.5226 | 0.3778 | 0.2274 | 0.0637 | 0.4245 | 0.0527 | 0.1543 | 0.2387 | 0.2672 | 0.6498 | 0.1989 | 0.117 | 0.1476 | 0.048 | 0.1399 | 0.1246 | 0.048
Load_TR5_F6_48 | prosumer | 0.1984 | 0.1035 | 0.1084 | 0.1844 | 0.1399 | 0.058 | 0.2303 | 0.108 | 0.1633 | 0.175 | 0.058 | 0.1263 | 0.191 | 0.0791 | 0.058 | 1.0468 | 0.1975 | 0.8388 | 2.7298 | 1.4084 | 1.1466 | 0.1258 | 0.058 | 0.2257 | 0.1126 | 0.058 | 0.1399 | 0.058 | 0.2758 | 0.0625 | 0.2159 | 0.3684 | 2.6048 | 3.6959 | 0.8332 | 1.2521 | 1.0929 | 0.497 | 1.2892 | 0.6479 | 0.6251 | 0.6133 | 0.7108 | 1.3103 | 0.5324 | 0.072 | 0.1399 | 0.1633
Load_TR5_F6_49 | prosumer | 0.1077 | 0.2179 | 0.1512 | 0.1345 | 0.1136 | 0.2555 | 0.1166 | 0.1762 | 0.2287 | 0.1166 | 0.2318 | 0.1373 | 0.2314 | 0.2183 | 0.1301 | 0.2224 | 0.5668 | 0.2629 | 0.278 | 0.5524 | 0.2177 | 0.4499 | 1.2439 | 0.3316 | 0.3648 | 0.2832 | 0.072 | 0.3338 | 1.1642 | 0.687 | 0.5987 | 0.1819 | 0.3528 | 0.2609 | 0.4649 | 0.5612 | 0.4065 | 0.3829 | 0.3577 | 1.0278 | 0.5388 | 0.8286 | 0.9611 | 0.806 | 0.9789 | 0.8859 | 0.5611 | 0.2179
Load_TR5_F6_5 | prosumer | 0.036 | 0.1573 | 0.0926 | 0.0683 | 0.1815 | 0.036 | 0.1734 | 0.0764 | 0.1007 | 0.1492 | 0.036 | 0.2138 | 0.036 | 0.036 | 0.0845 | 0.1653 | 0.1652 | 0.5642 | 0.2376 | 0.036 | 0.0522 | 0.31 | 0.3893 | 0.1253 | 0.2153 | 1.5114 | 1.4464 | 1.0613 | 0.1814 | 0.2808 | 0.0558 | 0.2058 | 0.036 | 0.1896 | 0.0603 | 0.036 | 0.2058 | 0.0441 | 0.1411 | 0.1088 | 0.036 | 0.2138 | 0.036 | 0.1249 | 0.1249 | 0.036 | 0.1168 | 0.133
Load_TR5_F6_50 | customer | 0.1511 | 0.053 | 0.1338 | 0.1738 | 0.0626 | 0.245 | 0.053 | 0.1626 | 0.145 | 0.128 | 0.0934 | 0.053 | 0.0913 | 0.1528 | 0.1164 | 0.3901 | 1.6791 | 0.3605 | 0.0961 | 0.0961 | 0.1626 | 0.145 | 0.1048 | 0.2028 | 0.1771 | 0.3361 | 0.169 | 0.369 | 0.4967 | 0.2816 | 0.2714 | 0.261 | 0.2144 | 0.3201 | 0.4811 | 1.987 | 0.476 | 0.489 | 0.5899 | 0.3989 | 0.5475 | 0.7321 | 0.8959 | 0.7866 | 0.8829 | 0.6127 | 0.7845 | 0.7728
Load_TR5_F6_51 | prosumer | 0.053 | 0.1758 | 0.053 | 0.053 | 0.1758 | 0.053 | 0.053 | 0.1758 | 0.053 | 0.053 | 0.053 | 0.1758 | 0.053 | 0.1407 | 0.2489 | 0.2321 | 0.2674 | 0.053 | 0.1462 | 0.3138 | 0.2293 | 1.6797 | 0.2026 | 0.0713 | 0.423 | 0.1073 | 0.053 | 0.1758 | 0.053 | 0.053 | 0.0881 | 0.1407 | 0.053 | 0.1758 | 0.053 | 0.1065 | 0.1444 | 0.053 | 0.2392 | 0.3087 | 0.053 | 0.1758 | 0.053 | 0.1495 | 0.0793 | 0.053 | 0.2126 | 0.053
Load_TR5_F6_52 | customer | 0.2156 | 0.3656 | 0.1385 | 0.1914 | 0.0974 | 0.031 | 0.1013 | 0.1661 | 0.0523 | 0.031 | 0.031 | 0.1021 | 0.1164 | 0.1013 | 0.0505 | 0.2382 | 0.031 | 0.031 | 0.207 | 0.0818 | 0.1092 | 0.1795 | 0.0523 | 0.1661 | 0.0896 | 0.0427 | 0.2461 | 0.2436 | 0.3104 | 1.2154 | 2.9165 | 2.937 | 0.4152 | 1.2565 | 0.2344 | 0.0892 | 0.3764 | 0.0842 | 0.1725 | 0.3593 | 0.4959 | 2.7017 | 2.8166 | 1.049 | 0.5892 | 0.6445 | 0.4453 | 0.2627
Load_TR5_F6_53 | customer | 0.055 | 0.1961 | 0.1514 | 0.1442 | 0.2032 | 0.055 | 0.2089 | 0.1385 | 0.1232 | 0.0917 | 0.1875 | 0.16 | 0.1755 | 0.067 | 0.3292 | 0.508 | 0.1527 | 0.3826 | 0.3562 | 0.2254 | 0.2633 | 0.4062 | 2.4724 | 0.5551 | 0.309 | 0.4202 | 0.2322 | 0.055 | 0.055 | 0.2295 | 0.118 | 0.055 | 0.055 | 0.2744 | 0.0731 | 0.118 | 0.097 | 0.1574 | 0.1691 | 0.076 | 0.2715 | 0.076 | 0.2437 | 0.1038 | 0.055 | 0.2925 | 0.055 | 0.1543
Load_TR5_F6_54 | prosumer | 0.1557 | 0.2685 | 0.047 | 0.2959 | 0.1283 | 0.047 | 0.2122 | 0.212 | 0.121 | 0.3032 | 0.2212 | 0.047 | 0.3772 | 0.047 | 0.5938 | 0.1957 | 0.0744 | 0.2667 | 0.1383 | 0.2349 | 0.1956 | 0.4257 | 0.3818 | 0.3392 | 0.369 | 0.3706 | 1.3617 | 0.3984 | 0.2994 | 0.4895 | 0.645 | 0.3716 | 0.6448 | 0.3664 | 0.3933 | 0.2118 | 0.3502 | 1.1651 | 0.4069 | 0.4458 | 0.4843 | 1.7828 | 0.9028 | 0.9534 | 1.1418 | 0.5304 | 0.1327 | 0.149
Load_TR5_F6_55 | prosumer | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.0872 | 0.053 | 0.053 | 0.057 | 0.0679 | 0.3133 | 0.0716 | 0.0684 | 0.1249 | 0.0975 | 2.1441 | 3.131 | 1.1457 | 0.1541 | 0.1197 | 0.1892 | 0.1211 | 0.2664 | 0.0763 | 1.8736 | 0.3135 | 0.0686 | 0.0621 | 0.1165 | 0.1294 | 0.3901 | 0.4536 | 0.4394 | 0.4734 | 0.5895 | 0.7889 | 0.5556 | 0.3834 | 0.1775
Load_TR5_F6_56 | prosumer | 0.047 | 0.1015 | 0.1427 | 0.064 | 0.1378 | 0.047 | 0.047 | 0.1954 | 0.1742 | 0.1039 | 0.0936 | 0.1421 | 0.1191 | 0.1378 | 0.1233 | 0.047 | 0.2258 | 0.0606 | 0.0502 | 0.2401 | 0.1869 | 0.1739 | 0.2318 | 0.2177 | 0.2014 | 0.0597 | 0.0682 | 0.1929 | 0.047 | 0.1833 | 0.0779 | 0.0809 | 0.1621 | 0.0906 | 0.1615 | 0.0742 | 0.0894 | 0.1717 | 0.047 | 0.0906 | 0.1705 | 0.047 | 0.1218 | 0.1393 | 0.047 | 0.0767 | 0.1481 | 0.1342
Load_TR5_F6_57 | prosumer | 0.1356 | 0.1182 | 0.1004 | 0.2192 | 0.0881 | 0.2046 | 0.1027 | 0.0634 | 0.1868 | 0.104 | 0.047 | 0.0989 | 0.2084 | 0.047 | 0.1507 | 0.1565 | 0.047 | 0.2603 | 0.047 | 0.1169 | 0.1461 | 0.0913 | 0.1522 | 0.2791 | 0.1852 | 0.2254 | 0.3016 | 0.136 | 0.123 | 0.1103 | 0.047 | 0.1526 | 0.1546 | 0.047 | 0.121 | 0.1823 | 0.1553 | 0.3007 | 0.1982 | 0.1624 | 0.4542 | 0.3085 | 0.3416 | 0.3791 | 0.1389 | 0.1891 | 0.1182 | 0.047
Load_TR5_F6_58 | customer | 0.046 | 0.1016 | 0.1433 | 0.046 | 0.185 | 0.0599 | 0.0599 | 0.185 | 0.046 | 0.185 | 0.0599 | 0.0668 | 0.178 | 0.046 | 0.1989 | 0.046 | 0.1641 | 0.0807 | 0.046 | 0.0529 | 0.1919 | 0.046 | 0.1989 | 0.046 | 0.1016 | 0.1433 | 0.094 | 0.2389 | 0.0727 | 0.263 | 0.0911 | 0.0513 | 0.185 | 0.0599 | 0.046 | 0.1989 | 0.126 | 0.1958 | 0.1467 | 0.2411 | 0.3453 | 0.3172 | 0.33 | 0.6456 | 0.3712 | 0.4887 | 0.2446 | 0.046
Load_TR5_F6_59 | customer | 0.044 | 0.312 | 0.0681 | 0.1323 | 0.1323 | 0.044 | 0.044 | 0.2207 | 0.044 | 0.0681 | 0.1966 | 0.044 | 0.2207 | 0.044 | 0.0929 | 0.3768 | 0.3589 | 0.1064 | 0.044 | 0.4066 | 0.044 | 0.1926 | 0.1805 | 0.044 | 0.1564 | 0.1082 | 0.044 | 0.168 | 1.3747 | 0.1505 | 0.0809 | 0.2702 | 1.4161 | 1.2153 | 1.0759 | 0.1615 | 1.5715 | 1.7873 | 1.686 | 0.1821 | 0.2761 | 0.2207 | 0.656 | 1.6456 | 0.5689 | 0.5224 | 0.2207 | 0.044
Load_TR5_F6_6 | customer | 0.7861 | 0.6663 | 0.6352 | 0.4939 | 0.059 | 0.0936 | 0.2467 | 0.0734 | 0.1065 | 0.241 | 0.0662 | 0.124 | 0.1529 | 0.1368 | 0.137 | 0.2962 | 0.2024 | 0.1543 | 0.3399 | 0.3158 | 0.3518 | 0.1112 | 0.1042 | 0.4289 | 2.1407 | 0.6574 | 0.2445 | 1.5061 | 0.2054 | 0.0732 | 0.2583 | 0.2921 | 0.1263 | 0.2062 | 0.1601 | 0.1368 | 0.0995 | 0.1031 | 0.3234 | 0.2109 | 0.5359 | 0.2454 | 0.2606 | 0.3823 | 0.3302 | 0.6439 | 0.5457 | 0.2419
Load_TR5_F6_60 | prosumer | 0.1299 | 0.2487 | 0.049 | 0.1689 | 0.2799 | 0.1214 | 0.2318 | 0.2594 | 0.1629 | 0.0762 | 0.3071 | 0.049 | 0.4542 | 0.049 | 0.049 | 0.2486 | 0.1421 | 0.2061 | 0.1947 | 0.2881 | 0.1979 | 0.081 | 0.4163 | 0.055 | 0.1347 | 0.1689 | 0.2677 | 0.1164 | 1.6856 | 0.1823 | 0.2251 | 0.4137 | 0.7382 | 1.0905 | 0.2096 | 0.2938 | 0.4534 | 0.3623 | 0.8103 | 0.1862 | 0.6541 | 1.4099 | 0.599 | 0.5418 | 0.9406 | 0.1761 | 0.2196 | 0.3954
Load_TR5_F6_61 | customer | 0.052 | 0.2201 | 0.052 | 0.2201 | 0.052 | 0.052 | 0.2201 | 0.052 | 0.159 | 0.1131 | 0.052 | 0.2201 | 0.052 | 0.052 | 0.1972 | 0.1476 | 0.3412 | 0.1972 | 0.0749 | 0.1594 | 0.1548 | 0.052 | 0.1021 | 0.1079 | 0.2834 | 0.2287 | 0.0773 | 1.7815 | 2.3874 | 0.7615 | 0.2166 | 0.052 | 0.2201 | 0.052 | 0.052 | 0.2283 | 0.0662 | 0.142 | 0.2583 | 0.4763 | 0.6481 | 0.3668 | 0.5597 | 0.4477 | 0.3987 | 0.5758 | 0.44 | 0.3787
Load_TR5_F6_62 | prosumer | 0.1242 | 0.1114 | 0.2282 | 0.0604 | 0.1373 | 0.1989 | 0.057 | 0.1183 | 0.2213 | 0.0877 | 0.0877 | 0.057 | 0.1407 | 0.1989 | 0.2979 | 0.1132 | 0.2951 | 0.1627 | 0.1324 | 0.2888 | 0.3918 | 0.2502 | 0.6001 | 0.2577 | 0.3259 | 0.3172 | 0.2725 | 0.4422 | 0.2719 | 0.3138 | 0.4464 | 0.2944 | 1.7018 | 0.2638 | 0.2284 | 0.4166 | 0.2469 | 0.369 | 0.3789 | 0.3034 | 0.6699 | 0.3941 | 0.4944 | 0.4638 | 0.8722 | 0.6405 | 0.41 | 0.4862
Load_TR5_F6_63 | customer | 0.3288 | 1.2593 | 1.1119 | 0.375 | 0.3229 | 0.042 | 0.2196 | 0.042 | 0.155 | 0.1066 | 0.042 | 0.2034 | 0.0581 | 0.1388 | 0.1227 | 0.0824 | 0.1792 | 0.042 | 0.0581 | 0.2034 | 0.042 | 0.042 | 0.1953 | 0.0662 | 0.1308 | 0.1308 | 0.042 | 0.042 | 0.2196 | 0.042 | 0.155 | 0.1066 | 0.042 | 0.4204 | 0.0873 | 0.369 | 1.3991 | 0.2964 | 0.4248 | 0.3989 | 0.6369 | 0.5658 | 0.3346 | 0.3445 | 0.7907 | 0.4818 | 0.042 | 0.042
Load_TR5_F6_64 | prosumer | 0.056 | 0.2264 | 0.056 | 0.087 | 0.1954 | 0.056 | 0.2186 | 0.0637 | 0.056 | 0.1567 | 0.1257 | 0.056 | 0.2264 | 0.056 | 0.0739 | 0.2141 | 0.1425 | 0.2957 | 0.7186 | 0.2945 | 0.1527 | 0.2212 | 0.0715 | 0.056 | 0.2264 | 0.056 | 0.056 | 0.2264 | 0.0819 | 0.2337 | 0.1293 | 0.1831 | 1.0096 | 1.3749 | 0.2425 | 0.1218 | 0.2714 | 0.2782 | 0.3586 | 0.358 | 0.519 | 0.5095 | 0.674 | 0.3212 | 0.4912 | 0.4388 | 0.5568 | 0.2031
Load_TR5_F6_65 | prosumer | 0.041 | 0.2005 | 0.041 | 0.1353 | 0.1062 | 0.041 | 0.2005 | 0.041 | 0.041 | 0.2005 | 0.041 | 0.1353 | 0.1062 | 0.041 | 0.041 | 0.2005 | 0.041 | 0.1353 | 0.1385 | 0.0483 | 0.1933 | 0.041 | 0.1787 | 0.0628 | 0.041 | 0.1933 | 0.0483 | 0.1207 | 0.1229 | 0.2072 | 0.1497 | 1.3622 | 0.7117 | 0.211 | 0.2234 | 0.325 | 0.1803 | 0.2042 | 1.1491 | 0.9051 | 0.6389 | 0.4771 | 0.458 | 0.5938 | 0.4533 | 0.2551 | 0.041 | 0.128
Load_TR5_F6_66 | customer | 0.0543 | 0.2869 | 0.2038 | 0.1142 | 0.1136 | 0.3301 | 0.0885 | 0.2869 | 0.1257 | 0.216 | 0.0883 | 0.305 | 0.05 | 0.2759 | 0.1291 | 0.2055 | 0.2903 | 0.1316 | 0.2516 | 0.5473 | 0.3535 | 0.2182 | 1.3119 | 0.4972 | 0.5473 | 0.379 | 0.4574 | 0.5127 | 0.8285 | 1.1845 | 0.3348 | 0.2603 | 0.3267 | 0.2994 | 0.1649 | 0.0543 | 0.3506 | 1.2545 | 1.0504 | 0.8673 | 1.3455 | 1.2048 | 1.2686 | 2.2031 | 0.8773 | 0.8523 | 0.9986 | 0.1563
Load_TR5_F6_67 | prosumer | 0.1193 | 0.047 | 0.1503 | 0.047 | 0.047 | 0.1503 | 0.047 | 0.1503 | 0.047 | 0.0935 | 0.1038 | 0.047 | 0.1503 | 0.047 | 0.2368 | 0.047 | 0.1503 | 0.2314 | 0.1046 | 0.1014 | 0.0496 | 0.1503 | 0.4611 | 0.097 | 0.047 | 0.1452 | 1.3133 | 1.0308 | 1.0636 | 0.047 | 0.1503 | 0.047 | 0.047 | 0.078 | 0.1193 | 0.057 | 0.4804 | 0.6568 | 0.3001 | 0.5446 | 0.39 | 0.4682 | 0.352 | 0.4273 | 0.3507 | 0.396 | 0.2999 | 0.2991
Load_TR5_F6_68 | customer | 0.1038 | 0.1038 | 0.093 | 0.1146 | 0.05 | 0.1253 | 0.0823 | 0.05 | 0.1576 | 0.05 | 0.1361 | 0.0715 | 0.05 | 0.1199 | 0.0877 | 0.0814 | 0.1352 | 0.05 | 0.4912 | 2.4598 | 2.1854 | 0.1038 | 0.05 | 0.0877 | 2.0455 | 0.0654 | 0.1716 | 0.05 | 0.1415 | 0.0794 | 0.05 | 0.1504 | 0.0874 | 0.1352 | 1.0118 | 4.1557 | 0.3276 | 0.1478 | 0.371 | 0.4414 | 0.2283 | 0.2312 | 0.4286 | 0.05 | 0.1588 | 0.1576 | 0.05 | 0.05
Load_TR5_F6_69 | prosumer | 0.2545 | 0.057 | 0.2287 | 0.123 | 0.057 | 0.057 | 0.1892 | 0.1624 | 0.057 | 0.2302 | 0.1879 | 0.1013 | 0.2284 | 0.1232 | 0.0771 | 0.2746 | 0.057 | 0.2435 | 0.2472 | 0.0918 | 0.3648 | 0.2953 | 0.5076 | 0.6931 | 0.5959 | 0.3169 | 0.2869 | 0.3155 | 0.4928 | 0.2841 | 0.4343 | 0.2388 | 0.2161 | 0.2289 | 1.1064 | 1.4074 | 0.7093 | 0.3314 | 0.4079 | 0.245 | 1.6318 | 0.6727 | 0.6562 | 0.5481 | 0.5906 | 0.5077 | 0.5819 | 0.1473
Load_TR5_F6_7 | customer | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.0692 | 0.642 | 0.6611 | 0.068 | 0.064 | 0.064 | 0.0603 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.1186 | 0.1112 | 0.2998 | 0.1821 | 0.0878 | 0.4335 | 0.3486 | 0.6506 | 0.549 | 0.5401 | 0.6702 | 0.796 | 0.8242 | 0.8489 | 0.053
Load_TR5_F6_70 | customer | 0.1924 | 0.1528 | 0.0622 | 0.2831 | 0.053 | 0.1354 | 0.0887 | 0.1742 | 0.1033 | 0.2134 | 0.141 | 0.1401 | 0.1457 | 0.0601 | 0.2028 | 0.053 | 0.1457 | 0.1996 | 0.053 | 0.0988 | 0.1895 | 0.1101 | 0.5001 | 0.5747 | 0.0895 | 0.1171 | 1.5275 | 0.9927 | 1.0242 | 1.4733 | 1.3423 | 2.2272 | 1.3476 | 0.4834 | 0.2904 | 0.3592 | 0.1218 | 0.2028 | 0.1354 | 0.0815 | 0.1814 | 0.573 | 0.7886 | 0.4454 | 0.4836 | 0.3804 | 0.0744 | 0.1171
Load_TR5_F6_71 | prosumer | 0.1581 | 0.1208 | 0.0836 | 0.1545 | 0.1267 | 0.1034 | 0.353 | 0.4732 | 0.051 | 0.2395 | 0.0743 | 0.1301 | 0.0615 | 0.1732 | 0.051 | 0.2162 | 0.1046 | 0.1082 | 0.1815 | 0.051 | 0.2628 | 0.051 | 0.1755 | 0.1383 | 0.1433 | 0.1096 | 0.1325 | 0.0882 | 0.1965 | 0.0801 | 0.051 | 0.0917 | 0.222 | 0.051 | 0.1522 | 0.1616 | 0.051 | 0.179 | 0.1068 | 0.1604 | 0.1534 | 0.0964 | 0.1616 | 0.1347 | 0.179 | 0.1347 | 0.1267 | 0.1452
Load_TR5_F6_72 | prosumer | 0.1499 | 0.2523 | 0.1298 | 0.319 | 0.2051 | 0.1141 | 0.3591 | 0.1049 | 0.2291 | 0.2349 | 0.068 | 0.3015 | 0.1395 | 0.068 | 0.3284 | 0.1126 | 0.0871 | 0.2789 | 0.9842 | 1.5578 | 1.0884 | 0.3004 | 0.2013 | 0.1917 | 0.8563 | 1.7964 | 0.2361 | 0.1247 | 0.0977 | 0.5592 | 0.2718 | 0.3863 | 0.2205 | 0.1707 | 0.1053 | 0.2104 | 0.1432 | 0.2631 | 0.4126 | 0.3886 | 0.4025 | 0.6037 | 0.4965 | 0.4407 | 0.4818 | 0.217 | 0.1801 | 0.0588
Load_TR5_F6_73 | customer | 0.0606 | 0.121 | 0.1512 | 0.053 | 0.2192 | 0.053 | 0.1814 | 0.0908 | 0.053 | 0.2192 | 0.053 | 0.121 | 0.1512 | 0.053 | 0.2192 | 0.053 | 0.1512 | 0.121 | 0.053 | 0.053 | 0.2456 | 0.1028 | 0.053 | 0.1588 | 0.1134 | 0.053 | 0.2041 | 0.0681 | 0.053 | 0.1814 | 0.0908 | 0.053 | 0.1739 | 0.0983 | 0.0934 | 0.4482 | 0.1781 | 0.4358 | 0.2313 | 0.4782 | 0.7828 | 0.7097 | 0.3528 | 0.0908 | 0.1134 | 0.1588 | 0.053 | 0.2192
Load_TR5_F6_74 | customer | 0.2237 | 0.1093 | 0.0753 | 0.1929 | 0.0849 | 0.0965 | 0.142 | 0.1825 | 0.1178 | 0.1851 | 0.1691 | 0.054 | 0.3003 | 0.054 | 0.1697 | 0.1989 | 0.1675 | 0.1894 | 0.1306 | 0.1234 | 0.2308 | 0.054 | 0.3003 | 0.054 | 0.054 | 0.1763 | 0.1779 | 0.054 | 0.2277 | 0.1306 | 0.1559 | 1.3684 | 0.2737 | 0.3281 | 0.7473 | 0.7276 | 0.3457 | 0.1937 | 0.3019 | 0.8116 | 0.5341 | 0.7773 | 0.8102 | 3.0038 | 3.0426 | 0.7599 | 0.1774 | 0.054
Load_TR5_F6_75 | prosumer | 0.9659 | 0.7091 | 0.7327 | 0.6199 | 0.1304 | 0.1319 | 0.2517 | 0.048 | 0.2498 | 0.1338 | 0.0995 | 0.0995 | 0.2326 | 0.151 | 0.6792 | 0.2038 | 0.048 | 0.3047 | 0.0789 | 0.146 | 0.2376 | 0.0545 | 0.252 | 0.3812 | 0.3785 | 0.1291 | 0.1253 | 0.2326 | 0.151 | 0.2074 | 0.0732 | 0.151 | 0.048 | 0.1407 | 0.0583 | 0.4447 | 0.1748 | 0.084 | 0.5357 | 2.9788 | 1.3306 | 0.7944 | 0.9049 | 1.0392 | 2.7245 | 0.673 | 0.4898 | 0.048
Load_TR5_F6_76 | prosumer | 0.058 | 0.1499 | 0.169 | 0.058 | 0.2608 | 0.058 | 0.2091 | 0.1097 | 0.1097 | 0.1485 | 0.1052 | 0.2136 | 0.0985 | 0.0782 | 0.1937 | 0.1251 | 1.1831 | 0.9453 | 0.3636 | 3.5693 | 4.5056 | 4.487 | 1.2215 | 0.6869 | 1.6771 | 0.0917 | 0.2204 | 0.0985 | 0.6056 | 0.5266 | 0.8439 | 0.5932 | 2.1797 | 1.2322 | 2.7371 | 2.5635 | 0.9771 | 0.085 | 0.1721 | 0.1468 | 0.398 | 0.8309 | 1.3415 | 1.427 | 1.3171 | 0.7973 | 0.4291 | 0.1808
Load_TR5_F6_77 | customer | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.0524 | 0.0642 | 0.0886 | 0.1018 | 0.0878 | 0.0747 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.1331 | 0.1052 | 1.0754 | 0.9668 | 0.9951 | 0.1672 | 1.0067 | 0.6529 | 0.0769 | 0.3514 | 0.3221 | 0.3285 | 0.5638 | 0.3574 | 1.1599 | 0.5862 | 0.345 | 0.052
Load_TR5_F6_78 | customer | 0.784 | 0.053 | 0.1056 | 0.0732 | 0.1259 | 0.053 | 0.1056 | 0.0732 | 0.0773 | 0.1016 | 0.053 | 0.053 | 0.1259 | 0.053 | 0.1259 | 0.053 | 0.053 | 0.1178 | 0.0611 | 0.1259 | 0.053 | 0.1259 | 0.053 | 0.1259 | 0.053 | 0.1016 | 0.0773 | 0.7289 | 1.7624 | 0.3254 | 0.1772 | 0.4553 | 0.1421 | 0.1548 | 0.4289 | 1.018 | 0.9281 | 1.9349 | 0.5188 | 0.6233 | 0.7525 | 0.5928 | 0.5661 | 0.4968 | 0.7421 | 0.5816 | 0.3416 | 0.0773
Load_TR5_F6_79 | customer | 0.2011 | 0.057 | 0.051 | 0.2609 | 0.057 | 0.051 | 0.2669 | 0.051 | 0.051 | 0.261 | 0.057 | 0.0751 | 0.1412 | 0.1527 | 0.1354 | 0.1766 | 0.069 | 0.1233 | 0.051 | 0.2669 | 0.051 | 0.1655 | 0.3119 | 0.0582 | 0.9157 | 0.2796 | 0.2107 | 0.1287 | 0.1354 | 0.051 | 0.1826 | 0.1576 | 0.1855 | 0.1825 | 1.2626 | 0.1754 | 0.257 | 0.3848 | 0.5305 | 0.2451 | 0.2574 | 0.5503 | 0.3174 | 0.4366 | 0.4199 | 0.277 | 0.1354 | 0.1826
Load_TR5_F6_8 | prosumer | 0.0905 | 0.2246 | 0.042 | 0.1613 | 0.1537 | 0.042 | 0.2582 | 0.0569 | 0.042 | 0.0719 | 0.2432 | 0.042 | 0.1762 | 0.1388 | 0.042 | 0.1612 | 0.1016 | 0.1237 | 0.1537 | 0.1613 | 0.1197 | 0.1421 | 0.2093 | 0.0468 | 0.1251 | 0.146 | 0.1537 | 0.299 | 0.2105 | 0.3304 | 0.1285 | 0.3248 | 0.2395 | 0.0756 | 0.1277 | 0.2097 | 0.0532 | 0.0643 | 0.1835 | 0.1092 | 0.1389 | 0.1762 | 0.0494 | 0.1984 | 0.042 | 0.1837 | 0.1314 | 0.042
Load_TR5_F6_80 | prosumer | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.0657 | 0.0604 | 0.0543 | 0.0785 | 0.1291 | 0.0937 | 0.11 | 0.9794 | 0.4038 | 0.1315 | 0.077 | 0.049 | 0.049 | 0.055 | 0.1121 | 0.1334 | 0.1442 | 0.109 | 0.109 | 0.073 | 2.8447 | 3.3198 | 0.5103 | 0.3799 | 0.249 | 0.2436 | 0.228 | 0.3136 | 1.2369 | 0.5058 | 0.5801 | 0.1344 | 0.049
Load_TR5_F6_81 | customer | 0.1241 | 0.1618 | 0.1763 | 0.05 | 0.2434 | 0.0947 | 0.1077 | 0.2081 | 0.0724 | 0.0731 | 0.265 | 0.05 | 0.1768 | 0.0873 | 0.0986 | 0.2395 | 0.05 | 0.1241 | 0.05 | 0.2429 | 0.0953 | 0.1094 | 0.2287 | 0.05 | 0.1991 | 0.139 | 0.1469 | 0.1171 | 0.05 | 0.1241 | 0.05 | 0.05 | 0.05 | 0.3926 | 0.3773 | 0.1427 | 0.3142 | 0.2503 | 0.1568 | 0.5662 | 0.3901 | 0.4412 | 0.3894 | 0.585 | 0.7057 | 0.3302 | 0.3246 | 0.05
Load_TR5_F6_82 | customer | 0.055 | 0.2276 | 0.055 | 0.1806 | 0.1021 | 0.055 | 0.2276 | 0.055 | 0.055 | 0.2276 | 0.055 | 0.1413 | 0.1413 | 0.0628 | 0.3673 | 0.1833 | 0.1355 | 0.2226 | 0.296 | 0.6105 | 3.215 | 5.2109 | 0.9654 | 1.9253 | 0.602 | 1.0204 | 0.1125 | 0.3026 | 0.17 | 0.1692 | 0.1289 | 0.1249 | 0.4145 | 0.1275 | 0.3923 | 1.8706 | 1.1808 | 1.7797 | 0.37 | 0.5913 | 0.2919 | 0.2464 | 0.5238 | 0.6852 | 0.9283 | 0.8029 | 0.44 | 0.4329
Load_TR5_F6_83 | customer | 0.2851 | 0.3776 | 0.1366 | 0.049 | 0.2558 | 0.0733 | 0.049 | 0.2801 | 0.049 | 0.0816 | 0.2134 | 0.0831 | 0.0555 | 0.2736 | 0.049 | 0.363 | 0.2227 | 0.216 | 0.3546 | 2.7965 | 2.768 | 0.5651 | 0.2565 | 0.2653 | 0.3191 | 0.2337 | 0.0989 | 0.1469 | 0.3095 | 0.1147 | 0.3833 | 0.0837 | 1.6691 | 0.1607 | 0.1561 | 0.3234 | 1.3435 | 0.407 | 0.3695 | 0.1604 | 0.5729 | 0.4881 | 0.5721 | 0.4783 | 0.6418 | 0.5548 | 0.1599 | 0.0816
Load_TR5_F6_9 | customer | 0.355 | 0.047 | 0.0522 | 0.3033 | 0.1144 | 0.047 | 0.3651 | 0.0579 | 0.2334 | 0.1896 | 0.0522 | 0.3137 | 0.104 | 0.0545 | 0.2615 | 0.1539 | 0.1308 | 0.4246 | 0.2639 | 0.3151 | 0.5501 | 0.1765 | 0.4663 | 0.2602 | 0.162 | 0.2752 | 0.047 | 0.1851 | 0.2379 | 0.0582 | 0.3505 | 0.0837 | 0.1711 | 0.382 | 0.3423 | 0.377 | 0.3121 | 0.1502 | 0.516 | 0.3792 | 0.6393 | 0.6386 | 0.8143 | 0.711 | 0.7843 | 0.8469 | 0.7927 | 0.2547

## 5. Raw batt charge
Raw batt charge
Verbatim copy of Charge_kW (TR5_analysis_data.xlsx). One row per half-hour, one column per battery (kW).
period | hour | BES_TR5_one38_B | BES_TR5_one195_C | BES_TR5_one195_dup_C | BES_TR5_one235_A | BES_TR5_one235_dup_A | BES_TR5_one242_dup_B | BES_TR5_one252_C | BES_TR5_one252_dup_C | BES_TR5_one260_dup_C | BES_TR5_one280_A | BES_TR5_one287_B | BES_TR5_one299_B | BES_TR5_one299_dup_B | BES_TR5_one313_A | BES_TR5_one313_dup_A | BES_TR5_one42_B | BES_TR5_one320_B | BES_TR5_one321_C | BES_TR5_one328_A | BES_TR5_one345_dup_A | BES_TR5_one346_C | BES_TR5_one366_dup_B | BES_TR5_one375_C | BES_TR5_one375_dup_C | BES_TR5_one410_B | BES_TR5_one410_dup_B | BES_TR5_one50_A | BES_TR5_one416_C | BES_TR5_one416_dup_C | BES_TR5_one423_dup_B | BES_TR5_one446_dup_B | BES_TR5_one469_A | BES_TR5_one477_A | BES_TR5_one477_dup_A | BES_TR5_one480_A | BES_TR5_one480_dup_A | BES_TR5_one521_dup_C | BES_TR5_one528_C | BES_TR5_one528_dup_C | BES_TR5_one61_dup_A | BES_TR5_one544_A | BES_TR5_one544_dup_A | BES_TR5_one559_C | BES_TR5_one590_A | BES_TR5_one590_dup_A | BES_TR5_one605_A | BES_TR5_one605_dup_A | BES_TR5_one614_B | BES_TR5_one617_dup_A | BES_TR5_one73_A | BES_TR5_one73_dup_A | BES_TR5_one76_A | BES_TR5_one133_A | BES_TR5_one137_A | BES_TR5_one176_A | BES_TR5_four1252_C | BES_TR5_four171_A | BES_TR5_four180_A | BES_TR5_four184_B | BES_TR5_four200_A | BES_TR5_four239_A | BES_TR5_four259_B | BES_TR5_four54_C | BES_TR5_four279_B | BES_TR5_four288_B | BES_TR5_four301_C | BES_TR5_four326_A | BES_TR5_four352_A | BES_TR5_four354_B | BES_TR5_four358_C | BES_TR5_four381_A | BES_TR5_four385_A | BES_TR5_four396_B | BES_TR5_four423_C | BES_TR5_four446_B | BES_TR5_four451_C | BES_TR5_four532_A | BES_TR5_four548_B | BES_TR5_four553_B | BES_TR5_four562_C | BES_TR5_four70_B | BES_TR5_four659_B | BES_TR5_four675_C | BES_TR5_four704_B | BES_TR5_four710_C | BES_TR5_four734_A | BES_TR5_four763_A | BES_TR5_four797_C | BES_TR5_four840_A | BES_TR5_four854_A | BES_TR5_four926_B | BES_TR5_four958_C | BES_TR5_four1027_A | BES_TR5_four1063_C | BES_TR5_four1091_B | BES_TR5_four1103_C | BES_TR5_four1132_C | BES_TR5_four1140_A | BES_TR5_four126_A | BES_TR5_four1187_A | BES_TR5_four1207_B | BES_TR5_four1216_C | BES_TR5_four1220_C | BES_TR5_four1226_A | BES_TR5_four1244_B | BES_TR5_five58_dup_C | BES_TR5_five147_dup_C | BES_TR5_five149_A | BES_TR5_five149_dup_A | BES_TR5_five160_C | BES_TR5_five160_dup_C | BES_TR5_five168_A | BES_TR5_five170_A | BES_TR5_five177_A | BES_TR5_five194_C | BES_TR5_five194_dup_C | BES_TR5_five220_C | BES_TR5_five220_dup_C | BES_TR5_five223_dup_A | BES_TR5_five242_dup_A | BES_TR5_five243_dup_B | BES_TR5_five284_C | BES_TR5_five284_dup_C | BES_TR5_five285_B | BES_TR5_five309_C | BES_TR5_five324_B | BES_TR5_five345_A | BES_TR5_five355_A | BES_TR5_five78_dup_A | BES_TR5_five394_C | BES_TR5_five421_A | BES_TR5_five421_dup_A | BES_TR5_five457_B | BES_TR5_five457_dup_B | BES_TR5_five466_A | BES_TR5_five472_dup_A | BES_TR5_five488_B | BES_TR5_five488_dup_B | BES_TR5_five494_dup_B | BES_TR5_five512_A | BES_TR5_five513_dup_B | BES_TR5_five537_C | BES_TR5_five537_dup_C | BES_TR5_five540_A | BES_TR5_five545_dup_B | BES_TR5_five585_dup_A | BES_TR5_five588_dup_A | BES_TR5_five108_B | BES_TR5_five108_dup_B | BES_TR5_five663_C | BES_TR5_five663_dup_C | BES_TR5_five670_C | BES_TR5_five670_dup_C | BES_TR5_five685_dup_B | BES_TR5_five695_dup_A | BES_TR5_five704_dup_A | BES_TR5_five719_A | BES_TR5_five719_dup_A | BES_TR5_five735_A | BES_TR5_five748_dup_B | BES_TR5_five117_dup_B | BES_TR5_five750_B | BES_TR5_five750_dup_B | BES_TR5_five778_dup_B | BES_TR5_five793_A | BES_TR5_five793_dup_A | BES_TR5_five799_dup_C | BES_TR5_five801_dup_C | BES_TR5_five118_B | BES_TR5_six64_A | BES_TR5_six173_C | BES_TR5_six186_A | BES_TR5_six203_A | BES_TR5_six238_A | BES_TR5_six249_B | BES_TR5_six254_B | BES_TR5_six68_C | BES_TR5_six317_C | BES_TR5_six326_A | BES_TR5_six342_A | BES_TR5_six350_B | BES_TR5_six75_A | BES_TR5_six385_B | BES_TR5_six387_A | BES_TR5_six392_C | BES_TR5_six431_C | BES_TR5_six441_A | BES_TR5_six512_B | BES_TR5_six518_B | BES_TR5_six523_C | BES_TR5_six534_B | BES_TR5_six591_C | BES_TR5_six595_B | BES_TR5_six643_A | BES_TR5_six646_B | BES_TR5_six651_C | BES_TR5_six87_A | BES_TR5_six665_B | BES_TR5_six718_C | BES_TR5_six721_A | BES_TR5_six723_B | BES_TR5_six740_A | BES_TR5_six799_B | BES_TR5_six807_A | BES_TR5_six852_B | BES_TR5_six860_C | BES_TR5_six885_A | BES_TR5_six909_C | BES_TR5_six921_B | BES_TR5_six929_A | BES_TR5_six952_A | BES_TR5_six967_B | BES_TR5_six111_C | BES_TR5_six1006_C
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008 | 0
10 | 4.5 | 0 | 0 | 0 | 0.057 | 0.068 | 0.05 | 0.056 | 0.039 | 0 | 0.04 | 0.023 | 0.127 | 0.036 | 0.182 | 0 | 0.016 | 0.143 | 0.017 | 0.093 | 0 | 0.093 | 0.073 | 0.123 | 0.052 | 0.158 | 0.038 | 0.09 | 0.063 | 0 | 0.074 | 0.189 | 0.118 | 0.123 | 0.035 | 0 | 0.182 | 0.184 | 0.145 | 0.09 | 0 | 0.181 | 0.067 | 0.039 | 0 | 0.149 | 0.068 | 0.027 | 0.044 | 0 | 0 | 0.087 | 0 | 0 | 0.153 | 0.185 | 0.028 | 0.007 | 0.027 | 0.049 | 0.088 | 0.068 | 0 | 0 | 0.026 | 0 | 0.008 | 0.011 | 0.176 | 0 | 0.088 | 0.032 | 0.189 | 0.01 | 0.086 | 0 | 0.183 | 0.032 | 0.12 | 0.181 | 0.066 | 0.051 | 0.003 | 0.156 | 0.046 | 0.127 | 0 | 0.002 | 0.12 | 0 | 0.091 | 0 | 0.121 | 0 | 0.016 | 0.156 | 0.181 | 0.185 | 0 | 0 | 0.177 | 0.102 | 0 | 0.005 | 0.02 | 0.069 | 0.044 | 0.086 | 0 | 0 | 0.003 | 0.073 | 0.091 | 0.003 | 0 | 0 | 0.001 | 0 | 0.041 | 0.157 | 0 | 0 | 0.004 | 0 | 0.023 | 0.03 | 0.104 | 0.085 | 0 | 0.053 | 0.187 | 0 | 0.109 | 0 | 0.088 | 0.088 | 0.112 | 0 | 0.156 | 0 | 0.034 | 0.014 | 0 | 0.054 | 0.066 | 0.046 | 0.192 | 0.061 | 0.119 | 0 | 0 | 0.175 | 0.083 | 0.069 | 0.102 | 0.02 | 0 | 0 | 0.124 | 0.177 | 0.064 | 0.176 | 0.079 | 0.183 | 0.082 | 0 | 0.007 | 0 | 0.123 | 0.069 | 0.109 | 0.008 | 0.089 | 0.064 | 0.086 | 0.022 | 0 | 0.116 | 0.09 | 0.038 | 0.075 | 0.013 | 0.039 | 0.147 | 0.105 | 0.173 | 0 | 0 | 0.08 | 0.181 | 0.07 | 0.015 | 0 | 0 | 0.185 | 0.058 | 0.116 | 0.025 | 0.18 | 0 | 0.092 | 0.041 | 0.041 | 0.156 | 0.087 | 0.018 | 0.032 | 0.081 | 0 | 0 | 0 | 0.012 | 0.084 | 0.161 | 0.125
11 | 5 | 0.236 | 0.391 | 0.413 | 0.189 | 0.183 | 0.136 | 0.209 | 0.091 | 0 | 0.332 | 0.288 | 0.164 | 0.122 | 0.41 | 0.128 | 0.43 | 0.308 | 0 | 0.236 | 0.27 | 0.183 | 0.023 | 0.295 | 0.291 | 0.358 | 0.124 | 0.233 | 0.034 | 0.369 | 0.344 | 0.417 | 0.29 | 0.168 | 0.343 | 0 | 0.278 | 0.412 | 0.297 | 0.233 | 0.074 | 0.257 | 0.184 | 0.087 | 0.408 | 0.349 | 0.37 | 0.199 | 0.158 | 0.156 | 0.127 | 0.356 | 0.067 | 0 | 0.319 | 0.203 | 0.406 | 0.399 | 0.343 | 0.287 | 0.231 | 0.183 | 0.12 | 0.216 | 0.082 | 0.118 | 0 | 0.389 | 0.404 | 0.061 | 0.231 | 0.018 | 0.417 | 0.135 | 0.411 | 0.061 | 0.411 | 0.09 | 0.252 | 0.409 | 0.181 | 0.218 | 0.18 | 0.281 | 0.29 | 0.192 | 0.125 | 0.29 | 0.209 | 0.101 | 0.306 | 0 | 0.19 | 0.352 | 0 | 0.349 | 0.261 | 0.413 | 0.417 | 0.124 | 0.405 | 0.148 | 0.268 | 0.295 | 0.239 | 0.316 | 0 | 0.353 | 0 | 0.235 | 0.387 | 0.355 | 0.115 | 0.226 | 0.177 | 0.41 | 0.209 | 0.057 | 0.296 | 0.287 | 0.176 | 0.296 | 0.385 | 0 | 0 | 0.412 | 0.144 | 0.256 | 0 | 0.18 | 0.415 | 0.256 | 0.241 | 0.346 | 0.303 | 0.421 | 0.409 | 0.226 | 0.356 | 0.086 | 0.353 | 0.006 | 0.111 | 0.419 | 0.162 | 0.132 | 0.307 | 0.176 | 0.298 | 0.281 | 0.152 | 0.261 | 0.23 | 0.178 | 0.29 | 0.061 | 0.082 | 0.342 | 0.081 | 0.405 | 0.179 | 0.257 | 0.194 | 0.368 | 0.297 | 0.29 | 0.21 | 0.149 | 0.173 | 0 | 0.252 | 0.296 | 0.232 | 0 | 0.229 | 0.061 | 0 | 0.288 | 0.356 | 0.044 | 0.351 | 0.169 | 0.414 | 0.241 | 0.189 | 0.401 | 0.018 | 0.086 | 0.237 | 0.409 | 0.017 | 0.086 | 0.16 | 0.054 | 0.413 | 0.403 | 0.23 | 0.31 | 0.408 | 0.182 | 0.235 | 0.195 | 0.241 | 0.154 | 0.258 | 0.22 | 0.42 | 0.242 | 0.158 | 0.156 | 0.393 | 0.189 | 0.356 | 0.218 | 0.297
12 | 5.5 | 0.412 | 0.592 | 0.579 | 0.19 | 0.323 | 0.241 | 0.347 | 0.154 | 0 | 0.687 | 0.503 | 0.509 | 0.227 | 0.691 | 0 | 0.595 | 0.562 | 0.231 | 0.272 | 0.501 | 0.332 | 0.232 | 0.362 | 0.476 | 0.603 | 0.229 | 0.409 | 0.311 | 0.596 | 0.554 | 0.698 | 0.5 | 0.572 | 0.634 | 0.106 | 0.691 | 0.693 | 0.7 | 0.409 | 0.229 | 0.589 | 0.19 | 0.153 | 0.511 | 0.594 | 0.573 | 0.497 | 0.17 | 0.192 | 0.351 | 0.601 | 0.327 | 0.124 | 0.556 | 0.62 | 0.687 | 0.639 | 0.639 | 0.497 | 0.407 | 0.323 | 0.23 | 0.693 | 0.042 | 0.122 | 0.226 | 0.565 | 0.685 | 0.252 | 0.407 | 0.223 | 0.582 | 0.321 | 0.671 | 0.129 | 0.611 | 0.291 | 0.453 | 0.69 | 0.172 | 0.406 | 0.07 | 0.662 | 0.605 | 0.322 | 0.073 | 0.492 | 0.458 | 0.216 | 0.597 | 0.077 | 0.444 | 0.597 | 0.029 | 0.6 | 0.69 | 0.694 | 0.585 | 0.04 | 0.686 | 0.489 | 0.549 | 0.353 | 0.415 | 0.51 | 0.149 | 0.692 | 0.148 | 0.503 | 0.393 | 0.6 | 0.505 | 0.257 | 0.27 | 0.659 | 0.372 | 0.414 | 0.442 | 0.422 | 0.138 | 0.448 | 0.52 | 0.23 | 0.227 | 0.597 | 0.375 | 0.597 | 0.143 | 0.448 | 0.696 | 0.511 | 0.596 | 0.584 | 0.593 | 0.499 | 0.587 | 0.496 | 0.439 | 0.14 | 0.52 | 0.375 | 0.326 | 0.611 | 0.205 | 0.237 | 0.676 | 0.068 | 0.632 | 0.266 | 0.506 | 0.613 | 0.406 | 0.326 | 0.46 | 0.228 | 0.299 | 0.505 | 0.506 | 0.686 | 0.319 | 0.684 | 0.334 | 0.566 | 0.42 | 0.264 | 0.145 | 0.411 | 0.448 | 0 | 0.428 | 0.372 | 0.356 | 0.344 | 0.405 | 0.244 | 0.133 | 0.498 | 0.355 | 0.195 | 0.526 | 0.397 | 0.6 | 0.587 | 0.4 | 0.574 | 0.039 | 0.321 | 0.413 | 0.69 | 0.316 | 0.32 | 0.137 | 0.235 | 0.525 | 0.616 | 0.605 | 0.343 | 0.566 | 0.602 | 0.411 | 0.322 | 0.365 | 0.693 | 0.499 | 0.5 | 0.607 | 0.509 | 0.455 | 0.241 | 0.44 | 0.364 | 0.528 | 0.7 | 0.507
13 | 6 | 0.428 | 0.873 | 0.852 | 0.616 | 0.476 | 0.356 | 0.73 | 0.468 | 0.213 | 0.951 | 0.709 | 0.603 | 0.342 | 0.997 | 0.243 | 0.942 | 1.007 | 0.402 | 0.581 | 0.576 | 0.557 | 0.348 | 0.721 | 0.7 | 0.871 | 0.344 | 0.558 | 0.382 | 0.825 | 0.822 | 1.004 | 0.706 | 0.866 | 0.975 | 0.258 | 0.973 | 0.999 | 0.922 | 0.561 | 0.2 | 0.996 | 0.603 | 0.475 | 0.935 | 0.862 | 0.919 | 0.55 | 0.476 | 0.417 | 0.304 | 0.738 | 0.252 | 0.427 | 0.866 | 1 | 0.857 | 0.863 | 0.892 | 0.453 | 0.598 | 0.372 | 0.381 | 0.843 | 0.317 | 0.32 | 0.242 | 0.798 | 0.991 | 0.357 | 0.598 | 0.248 | 0.998 | 0.392 | 0.922 | 0.179 | 0.988 | 0.575 | 0.663 | 0.996 | 0.441 | 0.549 | 0 | 0.898 | 0.793 | 0.678 | 0.345 | 0.299 | 0.732 | 0.38 | 0.812 | 0.345 | 0.733 | 0.627 | 0.324 | 1 | 0 | 1 | 0.856 | 0.344 | 0.992 | 0.554 | 0.817 | 0.735 | 0.606 | 0.982 | 0.46 | 0.845 | 0.211 | 0.677 | 0.839 | 0.868 | 0.621 | 0.612 | 0.477 | 0.736 | 0.524 | 0.51 | 0.717 | 0.875 | 0.36 | 0.652 | 0.988 | 0.271 | 0.24 | 0.873 | 0.614 | 0.74 | 0.109 | 0.697 | 1.002 | 0.474 | 0.864 | 0.642 | 0.589 | 0.963 | 0.894 | 0.528 | 0.869 | 0.479 | 0.933 | 0.401 | 0.352 | 0.958 | 0.474 | 0.344 | 1.007 | 0.469 | 0.961 | 0.634 | 0.736 | 0.935 | 0.597 | 0.606 | 0.825 | 0.417 | 0.315 | 0.888 | 0.736 | 0.992 | 0.472 | 0.991 | 0.487 | 0.998 | 0.737 | 0.73 | 0.557 | 0.515 | 0.662 | 0.285 | 0.619 | 0.736 | 0.579 | 0.509 | 0.596 | 0.48 | 0.269 | 0.728 | 0.988 | 0.193 | 0.939 | 0.47 | 0.898 | 0.81 | 0.535 | 0.988 | 0.215 | 0.213 | 0.604 | 0.996 | 0.457 | 0.258 | 0.275 | 0.055 | 0.993 | 0.857 | 0.817 | 0.75 | 0.995 | 0.54 | 0.602 | 0.536 | 0.447 | 0.594 | 0.645 | 0.56 | 0.942 | 0.636 | 0.558 | 0.462 | 0.908 | 0.422 | 0.949 | 0.872 | 0.737
14 | 6.5 | 0.788 | 1.197 | 1.31 | 0.765 | 0.631 | 0.472 | 0.876 | 0.623 | 0.138 | 1.042 | 1.033 | 0.971 | 0.411 | 1.307 | 0.464 | 1.246 | 1.317 | 0.426 | 0.701 | 0.963 | 0.71 | 0.538 | 0.967 | 0.996 | 1.142 | 0.46 | 0.442 | 0.564 | 1.282 | 1.089 | 1.314 | 0.954 | 1.071 | 1.115 | 0.426 | 1.114 | 1.309 | 1.232 | 0.71 | 0.419 | 1.135 | 0.666 | 0.461 | 1.104 | 1.034 | 1.317 | 0.959 | 0.441 | 0.457 | 0.799 | 0.046 | 0.635 | 0.571 | 1.137 | 1.205 | 1.289 | 1.304 | 1.31 | 0.952 | 0.792 | 0.41 | 0.67 | 1.309 | 0.404 | 0.308 | 0.362 | 1.195 | 1.077 | 0.459 | 0.792 | 0.444 | 0.707 | 0.608 | 1.308 | 0.337 | 1.232 | 0.743 | 0.944 | 1.306 | 0.546 | 0.738 | 0.503 | 1.227 | 1.269 | 0.728 | 0.461 | 0.696 | 0.837 | 0.563 | 1.083 | 0.375 | 0.877 | 0.958 | 0.243 | 1.231 | 1.106 | 1.31 | 1.314 | 0 | 1.302 | 0.965 | 1.138 | 0.868 | 0.8 | 1.059 | 0.346 | 1.308 | 0.278 | 1.073 | 1.151 | 1.139 | 0.87 | 0.773 | 0.79 | 1.242 | 0.809 | 0.641 | 0.908 | 0.16 | 0.556 | 0.955 | 1.11 | 0.29 | 0.411 | 1.309 | 0.684 | 1.099 | 0.272 | 0.838 | 1.312 | 0.973 | 1.135 | 1.285 | 1.093 | 1.31 | 1.27 | 0.964 | 1.14 | 0.634 | 1.309 | 0.647 | 0.582 | 1.274 | 0.629 | 0.404 | 1.179 | 0.446 | 1.226 | 0.918 | 0.843 | 1 | 0.791 | 0.683 | 1.133 | 0.332 | 0.622 | 1.131 | 0.968 | 1.302 | 0.594 | 1.301 | 0.61 | 1.138 | 0.451 | 0.962 | 0.544 | 0.723 | 0.816 | 0 | 0.733 | 0.758 | 0.793 | 0.664 | 0.79 | 0.8 | 0.392 | 0.96 | 1.06 | 0.135 | 1.202 | 0.795 | 1.267 | 0.971 | 0.629 | 1.276 | 0.327 | 0.514 | 0.639 | 1.306 | 0.556 | 0.608 | 0.606 | 0.466 | 1.302 | 1.279 | 1.139 | 0.982 | 1.217 | 1.141 | 0.796 | 0.711 | 0.802 | 1.309 | 0.819 | 0.962 | 1.317 | 0.971 | 0.895 | 0.506 | 1.29 | 0.698 | 1.28 | 1.219 | 0.969
15 | 7 | 0.796 | 1.43 | 1.618 | 0.783 | 0.517 | 0.588 | 1.126 | 0.432 | 0.148 | 1.583 | 1.296 | 1.067 | 0.574 | 1.615 | 0.565 | 1.518 | 1.472 | 0.78 | 0.923 | 1.11 | 0.955 | 0.668 | 1.084 | 1.296 | 1.412 | 0.576 | 0.94 | 0.779 | 1.373 | 1.367 | 1.622 | 1.193 | 1.312 | 1.577 | 0.526 | 1.607 | 1.617 | 1.624 | 0.986 | 0.576 | 1.614 | 0.846 | 0.593 | 1.447 | 1.403 | 1.48 | 1.046 | 0.777 | 0.751 | 0.654 | 0.532 | 0.586 | 0.741 | 1.351 | 1.44 | 1.271 | 1.432 | 1.448 | 1.049 | 0.984 | 0.76 | 0.84 | 1.539 | 0.411 | 0.505 | 0.519 | 1.558 | 0.951 | 0.764 | 0.984 | 0.488 | 0.765 | 0.783 | 1.616 | 0.575 | 1.601 | 0.801 | 1.156 | 1.614 | 0.684 | 0.808 | 0.708 | 1.521 | 1.429 | 1.208 | 0.288 | 1.035 | 1.195 | 0.643 | 1.181 | 0.442 | 1.123 | 1.406 | 0 | 1.539 | 1.594 | 1.618 | 1.56 | 0.161 | 1.61 | 1.13 | 1.316 | 1.115 | 0.888 | 1.533 | 0.471 | 1.616 | 0.506 | 1.213 | 1.323 | 1.382 | 1.178 | 1.105 | 0.904 | 1.259 | 0.74 | 0.909 | 1.176 | 1.416 | 0.68 | 1.07 | 1.541 | 0.507 | 0.574 | 0.279 | 0.959 | 1.396 | 0.175 | 1.144 | 1.62 | 1.108 | 1.405 | 1.47 | 1.339 | 1.468 | 0.685 | 0.982 | 1.314 | 0.513 | 1.499 | 0.755 | 0.788 | 1.528 | 0.783 | 0.584 | 1.536 | 0.707 | 1.516 | 1.012 | 1.199 | 1.429 | 0.902 | 0.958 | 1.276 | 0.523 | 0.694 | 0.52 | 1.199 | 1.61 | 0.772 | 1.503 | 0.778 | 1.616 | 0.924 | 0.988 | 0.746 | 0.877 | 0.927 | 0.714 | 1.005 | 1.169 | 0.914 | 0.913 | 0.982 | 0.977 | 0.306 | 1.191 | 1.555 | 0.424 | 1.358 | 0.843 | 1.521 | 1.249 | 0.893 | 1.519 | 0.395 | 0.711 | 0.99 | 1.581 | 0.761 | 0.659 | 0.423 | 0.31 | 1.541 | 1.608 | 1.536 | 1.165 | 1.417 | 0.864 | 0.954 | 0.918 | 0.89 | 1.617 | 0.952 | 1.176 | 1.625 | 1.013 | 1.172 | 0.782 | 1.338 | 0.362 | 1.472 | 1.624 | 1.2
16 | 7.5 | 0.145 | 1.775 | 1.924 | 1.116 | 0.762 | 0.703 | 1.018 | 0.909 | 0.417 | 1.689 | 1.411 | 1.434 | 0.689 | 0.562 | 0.356 | 1.38 | 1.756 | 0.729 | 1.131 | 0.992 | 1.039 | 0.641 | 1.351 | 1.443 | 1.178 | 0.691 | 1.069 | 0.601 | 1.913 | 1.668 | 1.042 | 1.425 | 1.662 | 1.901 | 0.858 | 1.359 | 0.53 | 1.831 | 1.149 | 0.575 | 1.84 | 1.176 | 0.727 | 1.922 | 1.574 | 1.759 | 1.39 | 0 | 0.771 | 1.061 | 0 | 0.918 | 0.724 | 0.777 | 1.832 | 1.763 | 1.921 | 1.865 | 1.232 | 1.125 | 0.875 | 0 | 1.662 | 0.686 | 0.594 | 0.577 | 1.67 | 1.54 | 0.803 | 1.177 | 0 | 1.886 | 0.848 | 1.149 | 0.69 | 0.932 | 1.179 | 1.377 | 0.578 | 0.937 | 0.995 | 0 | 1.908 | 1.874 | 1.212 | 0.529 | 1.4 | 1.306 | 0.704 | 1.459 | 0.621 | 1.428 | 1.597 | 0.378 | 1.782 | 1.923 | 0.514 | 1.62 | 0.462 | 0.642 | 1.313 | 1.246 | 1.41 | 1.185 | 1.75 | 0.614 | 1.531 | 0.509 | 1.677 | 1.893 | 1.514 | 1.302 | 1.344 | 0.857 | 1.725 | 0.831 | 0.889 | 1.348 | 1.585 | 0.853 | 1.431 | 1.859 | 0.526 | 0.53 | 1.814 | 1.147 | 1.667 | 0.259 | 1.317 | 0.482 | 1.355 | 1.613 | 1.726 | 1.557 | 1.935 | 0.82 | 1.056 | 1.299 | 0.932 | 1.805 | 0.926 | 0.763 | 1.402 | 0.889 | 0.523 | 1.381 | 0.887 | 1.915 | 1.339 | 0.963 | 0.681 | 1.171 | 1.185 | 1.373 | 0.601 | 0.671 | 1.648 | 1.423 | 0.701 | 0.935 | 1.263 | 0.934 | 1.925 | 1.186 | 1.394 | 1.014 | 0.901 | 1.43 | 0.872 | 0.909 | 1.362 | 1.178 | 1.074 | 1.175 | 0.923 | 0.534 | 0.804 | 1.711 | 0.686 | 1.629 | 1.18 | 1.197 | 1.643 | 0.783 | 1.283 | 0.639 | 0 | 1.111 | 0.611 | 0.791 | 0.865 | 0.929 | 0.674 | 1.395 | 0.928 | 1.752 | 1.316 | 1.41 | 1.532 | 1.181 | 1.187 | 1.078 | 1.726 | 1.368 | 1.267 | 1.254 | 1.434 | 1.206 | 0.771 | 1.862 | 1.03 | 1.849 | 1.651 | 1.415
17 | 8 | 1.189 | 1.711 | 0 | 0.996 | 1.056 | 0.812 | 0.646 | 1.015 | 0.179 | 0.542 | 1.898 | 1.314 | 0.798 | 0 | 0 | 0 | 0 | 0.929 | 1.253 | 1.616 | 0.652 | 0.955 | 1.618 | 0.94 | 0 | 0.572 | 1.138 | 0 | 1.057 | 1.886 | 0 | 1.146 | 0.801 | 0 | 0.414 | 0 | 0 | 1.21 | 1.312 | 0.8 | 0 | 1.096 | 0.695 | 0.885 | 0.287 | 0 | 1.446 | 0.959 | 0.983 | 1.235 | 1.038 | 1.088 | 0 | 0 | 0.31 | 0 | 1.405 | 0.935 | 1.489 | 0 | 0.966 | 1.166 | 1.706 | 0.747 | 0.675 | 0.629 | 0.912 | 0 | 0.912 | 1.358 | 0.138 | 0.553 | 0 | 0 | 0.265 | 0 | 1.184 | 1.644 | 0 | 0.857 | 1.182 | 0.631 | 0.544 | 1.398 | 1.579 | 0.56 | 1.534 | 1.377 | 1.072 | 1.816 | 0.685 | 1.483 | 0.774 | 0 | 0 | 0.803 | 0 | 0 | 0.59 | 0 | 1.643 | 1.303 | 1.277 | 1.29 | 1.714 | 0.661 | 0 | 0.484 | 1.759 | 1.396 | 0 | 1.647 | 1.213 | 1.097 | 1.044 | 0.076 | 1.025 | 1.304 | 1.656 | 0.892 | 1.413 | 0.107 | 0.617 | 0.596 | 1.818 | 1.234 | 0.877 | 0 | 1.57 | 0 | 1.555 | 0.163 | 0.519 | 0.718 | 0.256 | 1.555 | 1.465 | 0.71 | 0.956 | 0.121 | 1.109 | 1.048 | 0 | 0.997 | 0.728 | 0 | 0.909 | 0.415 | 1.433 | 1.006 | 0 | 1.353 | 1.332 | 1.718 | 0.838 | 0.972 | 1.625 | 1.243 | 0 | 1.068 | 0 | 1.095 | 0.741 | 1.432 | 1.474 | 1.304 | 1.362 | 1.647 | 0 | 0.852 | 1.476 | 1.314 | 0 | 1.356 | 1.347 | 0 | 1.582 | 1.21 | 0.692 | 0.581 | 1.361 | 0.593 | 1.044 | 0.918 | 0 | 0.724 | 0 | 1.278 | 0 | 1.05 | 1.082 | 0.647 | 0.764 | 0 | 0.944 | 0.728 | 1.402 | 0 | 1.907 | 1.362 | 1.189 | 1.368 | 0.84 | 1.403 | 1.556 | 0 | 1.277 | 1.641 | 1.028 | 1.095 | 1.367 | 0.048 | 0 | 0.506
18 | 8.5 | 1.22 | 0 | 0 | 1.34 | 0.757 | 0.411 | 0.578 | 0.657 | 0.508 | 0 | 0.808 | 0 | 0.9 | 0 | 0 | 0 | 0 | 1.215 | 1.143 | 0.905 | 1.401 | 1.065 | 0.744 | 1.019 | 0 | 0.018 | 1.192 | 0 | 0 | 0.166 | 0 | 0 | 0 | 0 | 0.328 | 0 | 0 | 0 | 0.723 | 0.902 | 0 | 1.533 | 0.977 | 0 | 0 | 0 | 0.333 | 1.185 | 1.078 | 1.146 | 2.048 | 1.083 | 0.914 | 0.063 | 0 | 0 | 0 | 0 | 0.525 | 1.03 | 0.948 | 1.418 | 0 | 0.629 | 0.805 | 0.428 | 0 | 0 | 1.175 | 0.21 | 0 | 0 | 0.91 | 0 | 0.878 | 0 | 1.446 | 1.359 | 0 | 1.117 | 1.058 | 0 | 0 | 0 | 0.835 | 0 | 1.772 | 0 | 0.365 | 0.622 | 0 | 1.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0.683 | 0 | 0.156 | 0 | 0.267 | 0.493 | 0 | 0 | 0 | 0.4 | 0.832 | 0 | 0 | 0.026 | 1.644 | 1.416 | 0 | 1.364 | 0.499 | 0 | 0 | 0.994 | 0 | 0 | 0 | 0.817 | 0 | 0.76 | 0 | 0 | 0.203 | 0 | 0.477 | 0 | 0 | 0 | 0 | 0.92 | 1.429 | 0 | 1.055 | 0 | 1.3 | 1.212 | 0 | 1.218 | 0.91 | 0 | 1.026 | 0 | 1.151 | 0 | 0.813 | 1.433 | 1.031 | 0.577 | 0.818 | 0.995 | 0.191 | 0 | 0 | 1.21 | 0 | 1.231 | 0 | 0.568 | 0.712 | 1.534 | 1.446 | 0.15 | 1.039 | 0.076 | 0.675 | 0.764 | 1.145 | 0.94 | 1.413 | 0 | 0 | 0 | 0.847 | 0 | 1.072 | 0 | 0 | 0.149 | 0 | 0.61 | 1.119 | 1.189 | 0 | 0 | 1.177 | 0.97 | 0.555 | 0 | 0 | 0 | 0 | 0 | 0.256 | 0.172 | 1.24 | 1.325 | 0 | 0.633 | 0.137 | 0 | 0 | 0.562 | 1.16 | 0 | 1.281 | 0 | 0 | 0
19 | 9 | 1.293 | 0 | 0 | 1.008 | 0.078 | 0 | 0.958 | 1.279 | 0.555 | 0 | 0 | 0 | 0.987 | 0 | 0.309 | 0 | 0 | 1.063 | 0 | 0 | 0.463 | 1.316 | 0 | 0 | 0 | 0.391 | 0.834 | 0.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037 | 0 | 0 | 0 | 0 | 0.873 | 0 | 0.53 | 1.152 | 0 | 0 | 0 | 0 | 0 | 1.18 | 1.292 | 0.894 | 1.235 | 0.458 | 2.289 | 0 | 0 | 0 | 0 | 0 | 1.532 | 0.153 | 1.34 | 0 | 0.818 | 0.978 | 0.133 | 0 | 0 | 1.074 | 0 | 0.655 | 0 | 1.289 | 0 | 0.897 | 0 | 0.5 | 0 | 0 | 0.082 | 0 | 1.312 | 0 | 0 | 0 | 0 | 0.449 | 0 | 0 | 0 | 0.99 | 0 | 0 | 0.187 | 0 | 0 | 0 | 0 | 0.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.661 | 0 | 1.089 | 0.877 | 0 | 0 | 1.152 | 0 | 0 | 0.601 | 0.085 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.717 | 0 | 0 | 1.296 | 0 | 1.302 | 0.18 | 0 | 0.657 | 0.919 | 0 | 1.261 | 0 | 0 | 0 | 1.114 | 0 | 0 | 0 | 1.325 | 1.23 | 0 | 0 | 0 | 0.226 | 0 | 0.198 | 0 | 0 | 0.266 | 0.917 | 0 | 0 | 1.322 | 1.319 | 0 | 0 | 1.639 | 0 | 1.366 | 0.921 | 0 | 0 | 0.507 | 0 | 0 | 0 | 0 | 1.246 | 0 | 0.984 | 1.097 | 0 | 0 | 1.149 | 1.158 | 1.081 | 0.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073 | 0 | 0 | 0 | 0 | 0 | 0 | 1.203 | 0 | 1.651 | 0 | 0 | 0
20 | 9.5 | 0 | 0 | 0 | 0.03 | 1.11 | 0.956 | 0 | 0.969 | 0.475 | 0 | 0 | 0 | 0.916 | 0 | 0.826 | 0 | 0 | 1.254 | 0 | 0 | 0 | 1.081 | 0 | 0 | 0 | 0 | 0 | 0.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0.938 | 0 | 0 | 1.103 | 0 | 1.063 | 0 | 0 | 1.277 | 0 | 0 | 0 | 0 | 0.391 | 0.732 | 1.001 | 0 | 0.587 | 0 | 0.427 | 0 | 0 | 0 | 0 | 0 | 0.249 | 0.705 | 1.227 | 0 | 0.879 | 0.852 | 0.897 | 0 | 0 | 1 | 0 | 0.916 | 0 | 1.241 | 0 | 0.804 | 0 | 0 | 0 | 0 | 1.417 | 0 | 1.432 | 0 | 0 | 0 | 1.062 | 0 | 0 | 0 | 0 | 0.037 | 0 | 0 | 0.817 | 0 | 0 | 0 | 0 | 0.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.641 | 0 | 0 | 1.256 | 0 | 0 | 0.942 | 0 | 0 | 0 | 0 | 0.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.513 | 0 | 0 | 1.01 | 0 | 0 | 0.952 | 0 | 0.507 | 0 | 0 | 1.74 | 0 | 0 | 0 | 0 | 1.139 | 0.806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.361 | 0 | 0 | 0 | 0.746 | 0 | 0 | 0.567 | 0 | 0 | 0.037 | 0 | 0 | 0 | 0 | 0.693 | 0 | 0.822 | 0.374 | 0 | 0 | 1.205 | 0.334 | 1.038 | 0.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.916 | 0 | 0.593 | 0 | 0 | 0
21 | 10 | 0 | 0 | 0 | 0 | 0.131 | 1.038 | 0 | 0.271 | 0.621 | 0 | 0 | 0 | 0 | 0 | 0.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.129 | 0 | 0.586 | 0 | 0 | 0 | 0 | 0 | 0 | 1.247 | 0 | 0 | 0.2 | 0 | 0.486 | 0 | 0 | 0.183 | 0 | 0 | 0 | 0 | 0.692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.243 | 0 | 0.988 | 1.117 | 1.037 | 0 | 0 | 0 | 0 | 1.001 | 0 | 0 | 0 | 0.866 | 0 | 0 | 0 | 0 | 0.088 | 0 | 1.276 | 0 | 0 | 0 | 0.972 | 0 | 0 | 1.426 | 0 | 1.013 | 0 | 0 | 0.923 | 0 | 0 | 0 | 0 | 0.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.197 | 0 | 0 | 0 | 0.303 | 0 | 0 | 0 | 0 | 0 | 0.901 | 0 | 0 | 0 | 0 | 0.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.466 | 0.656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.305 | 0 | 0 | 0 | 0 | 0 | 0 | 1.037 | 0 | 0 | 0.281 | 0 | 0 | 0 | 0 | 0 | 0 | 1.001 | 1.168 | 0 | 0 | 0.478 | 0 | 1.178 | 1.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 10.5 | 0 | 0 | 0 | 0 | 0 | 1.085 | 0 | 0 | 0.493 | 0 | 0 | 0 | 0 | 0 | 1.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.182 | 0 | 0.714 | 0 | 0 | 0 | 0 | 0 | 0 | 1.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.477 | 0 | 0 | 0 | 0 | 1.507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79 | 1.161 | 1.071 | 0 | 0 | 0 | 0 | 1.176 | 0 | 0 | 0 | 0.858 | 0 | 0 | 0 | 0 | 0 | 0 | 1.591 | 0 | 0 | 0 | 1.183 | 0 | 0 | 0.881 | 0 | 1.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.928 | 0 | 0 | 0 | 0 | 0 | 0 | 1.195 | 0 | 1.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.628 | 0 | 0 | 0 | 0.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.15 | 0 | 0 | 0.939 | 0 | 0 | 0 | 0 | 0 | 0 | 1.005 | 1.221 | 0 | 0 | 0 | 0 | 0 | 1.082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 11 | 0 | 0 | 0 | 0 | 0 | 0.391 | 0 | 0 | 0.43 | 0 | 0 | 0 | 0 | 0 | 1.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.713 | 0 | 1.346 | 0 | 0 | 0 | 0 | 0 | 0 | 1.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32 | 0 | 1.17 | 0 | 0 | 1.641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.082 | 0.619 | 0 | 0 | 0 | 0 | 1.134 | 0 | 0 | 0 | 0.342 | 0 | 0 | 0 | 0 | 0 | 0 | 1.586 | 0 | 0 | 0 | 1.221 | 0 | 0 | 0 | 0 | 0.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.049 | 0 | 0 | 0 | 0 | 0 | 0 | 1.09 | 0 | 0.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.872 | 0 | 0 | 1.048 | 0.873 | 0 | 0 | 0 | 0 | 0 | 0.503 | 1.02 | 0 | 0 | 0 | 0 | 0 | 0.383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.163 | 0 | 0
24 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.621 | 0 | 0 | 0 | 0.167 | 0 | 1.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.863 | 0 | 0 | 1.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.246 | 0 | 0 | 0 | 1.208 | 0 | 0 | 1.17 | 0 | 0.058 | 0 | 0 | 0.578 | 0 | 0 | 0 | 0 | 0.612 | 0 | 0 | 0 | 0 | 0 | 0 | 0.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.242 | 0 | 0 | 0.127 | 0.344 | 0 | 0 | 0 | 1.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.203 | 0 | 0 | 1.222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.361 | 0 | 0
25 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.759 | 0 | 0 | 0 | 0 | 0 | 0.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.156 | 0 | 0 | 1.521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.473 | 0 | 0 | 1.028 | 0 | 0.32 | 0 | 0 | 0.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23 | 0 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.519 | 0 | 0 | 0.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.906 | 0 | 0 | 0.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056 | 0 | 0.972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.751 | 0 | 0 | 0 | 0.299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.831 | 0 | 0 | 0.638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.007 | 0 | 0.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.271 | 0 | 0 | 0 | 0.552 | 0.01 | 0 | 0 | 0 | 0.978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.343 | 0 | 0.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.151 | 0 | 0 | 0 | 0 | 0.601 | 0 | 0 | 0 | 0.989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.913 | 0 | 0 | 0 | 0.802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.136 | 0 | 0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.805 | 0 | 0.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.377 | 0 | 0.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81 | 0 | 0 | 0 | 0.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076 | 0 | 0.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.668 | 0 | 0 | 0 | 0.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.988 | 0 | 0 | 0 | 0 | 0 | 0.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.641 | 0 | 0 | 0 | 0.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011 | 0 | 0
35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034 | 0 | 0 | 0.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026 | 0.138 | 0 | 0 | 0 | 0 | 0 | 0.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.274 | 0 | 0 | 0 | 0 | 0 | 0 | 0.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.706 | 0 | 0 | 0 | 0 | 0.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 17.5 | 0.486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.377 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.594 | 0 | 0 | 0.656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 18 | 0.193 | 0 | 0 | 0.159 | 0 | 0 | 0.193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.166 | 0 | 0.053 | 0 | 0.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.264 | 0 | 0.222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021 | 0.359 | 0 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.378 | 0.143 | 0 | 0 | 0.487 | 0 | 0 | 0.318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.289 | 0 | 0.875 | 0 | 0 | 0 | 0 | 0.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.177 | 0 | 0.404 | 0.531 | 0.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.168 | 0.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0.115 | 0.148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.249 | 0 | 0.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32 | 0 | 0 | 0.093 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.268 | 0 | 0 | 0.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0.345 | 0 | 0.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.268 | 0.457 | 0.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.368 | 0 | 0.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.142 | 0 | 0 | 0 | 0.546 | 0 | 0
39 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.177 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0 | 0 | 0.154 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.071 | 0 | 0 | 0 | 0 | 0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013 | 0 | 0 | 0 | 0 | 0.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.151 | 0 | 0 | 0 | 0 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.107 | 0.039 | 0.031 | 0.028 | 0.125 | 0.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.196 | 0 | 0
40 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 6. Raw batt discharge
Raw batt discharge
Verbatim copy of Discharge_kW (TR5_analysis_data.xlsx). One row per half-hour, one column per battery (kW).
period | hour | BES_TR5_one38_B | BES_TR5_one195_C | BES_TR5_one195_dup_C | BES_TR5_one235_A | BES_TR5_one235_dup_A | BES_TR5_one242_dup_B | BES_TR5_one252_C | BES_TR5_one252_dup_C | BES_TR5_one260_dup_C | BES_TR5_one280_A | BES_TR5_one287_B | BES_TR5_one299_B | BES_TR5_one299_dup_B | BES_TR5_one313_A | BES_TR5_one313_dup_A | BES_TR5_one42_B | BES_TR5_one320_B | BES_TR5_one321_C | BES_TR5_one328_A | BES_TR5_one345_dup_A | BES_TR5_one346_C | BES_TR5_one366_dup_B | BES_TR5_one375_C | BES_TR5_one375_dup_C | BES_TR5_one410_B | BES_TR5_one410_dup_B | BES_TR5_one50_A | BES_TR5_one416_C | BES_TR5_one416_dup_C | BES_TR5_one423_dup_B | BES_TR5_one446_dup_B | BES_TR5_one469_A | BES_TR5_one477_A | BES_TR5_one477_dup_A | BES_TR5_one480_A | BES_TR5_one480_dup_A | BES_TR5_one521_dup_C | BES_TR5_one528_C | BES_TR5_one528_dup_C | BES_TR5_one61_dup_A | BES_TR5_one544_A | BES_TR5_one544_dup_A | BES_TR5_one559_C | BES_TR5_one590_A | BES_TR5_one590_dup_A | BES_TR5_one605_A | BES_TR5_one605_dup_A | BES_TR5_one614_B | BES_TR5_one617_dup_A | BES_TR5_one73_A | BES_TR5_one73_dup_A | BES_TR5_one76_A | BES_TR5_one133_A | BES_TR5_one137_A | BES_TR5_one176_A | BES_TR5_four1252_C | BES_TR5_four171_A | BES_TR5_four180_A | BES_TR5_four184_B | BES_TR5_four200_A | BES_TR5_four239_A | BES_TR5_four259_B | BES_TR5_four54_C | BES_TR5_four279_B | BES_TR5_four288_B | BES_TR5_four301_C | BES_TR5_four326_A | BES_TR5_four352_A | BES_TR5_four354_B | BES_TR5_four358_C | BES_TR5_four381_A | BES_TR5_four385_A | BES_TR5_four396_B | BES_TR5_four423_C | BES_TR5_four446_B | BES_TR5_four451_C | BES_TR5_four532_A | BES_TR5_four548_B | BES_TR5_four553_B | BES_TR5_four562_C | BES_TR5_four70_B | BES_TR5_four659_B | BES_TR5_four675_C | BES_TR5_four704_B | BES_TR5_four710_C | BES_TR5_four734_A | BES_TR5_four763_A | BES_TR5_four797_C | BES_TR5_four840_A | BES_TR5_four854_A | BES_TR5_four926_B | BES_TR5_four958_C | BES_TR5_four1027_A | BES_TR5_four1063_C | BES_TR5_four1091_B | BES_TR5_four1103_C | BES_TR5_four1132_C | BES_TR5_four1140_A | BES_TR5_four126_A | BES_TR5_four1187_A | BES_TR5_four1207_B | BES_TR5_four1216_C | BES_TR5_four1220_C | BES_TR5_four1226_A | BES_TR5_four1244_B | BES_TR5_five58_dup_C | BES_TR5_five147_dup_C | BES_TR5_five149_A | BES_TR5_five149_dup_A | BES_TR5_five160_C | BES_TR5_five160_dup_C | BES_TR5_five168_A | BES_TR5_five170_A | BES_TR5_five177_A | BES_TR5_five194_C | BES_TR5_five194_dup_C | BES_TR5_five220_C | BES_TR5_five220_dup_C | BES_TR5_five223_dup_A | BES_TR5_five242_dup_A | BES_TR5_five243_dup_B | BES_TR5_five284_C | BES_TR5_five284_dup_C | BES_TR5_five285_B | BES_TR5_five309_C | BES_TR5_five324_B | BES_TR5_five345_A | BES_TR5_five355_A | BES_TR5_five78_dup_A | BES_TR5_five394_C | BES_TR5_five421_A | BES_TR5_five421_dup_A | BES_TR5_five457_B | BES_TR5_five457_dup_B | BES_TR5_five466_A | BES_TR5_five472_dup_A | BES_TR5_five488_B | BES_TR5_five488_dup_B | BES_TR5_five494_dup_B | BES_TR5_five512_A | BES_TR5_five513_dup_B | BES_TR5_five537_C | BES_TR5_five537_dup_C | BES_TR5_five540_A | BES_TR5_five545_dup_B | BES_TR5_five585_dup_A | BES_TR5_five588_dup_A | BES_TR5_five108_B | BES_TR5_five108_dup_B | BES_TR5_five663_C | BES_TR5_five663_dup_C | BES_TR5_five670_C | BES_TR5_five670_dup_C | BES_TR5_five685_dup_B | BES_TR5_five695_dup_A | BES_TR5_five704_dup_A | BES_TR5_five719_A | BES_TR5_five719_dup_A | BES_TR5_five735_A | BES_TR5_five748_dup_B | BES_TR5_five117_dup_B | BES_TR5_five750_B | BES_TR5_five750_dup_B | BES_TR5_five778_dup_B | BES_TR5_five793_A | BES_TR5_five793_dup_A | BES_TR5_five799_dup_C | BES_TR5_five801_dup_C | BES_TR5_five118_B | BES_TR5_six64_A | BES_TR5_six173_C | BES_TR5_six186_A | BES_TR5_six203_A | BES_TR5_six238_A | BES_TR5_six249_B | BES_TR5_six254_B | BES_TR5_six68_C | BES_TR5_six317_C | BES_TR5_six326_A | BES_TR5_six342_A | BES_TR5_six350_B | BES_TR5_six75_A | BES_TR5_six385_B | BES_TR5_six387_A | BES_TR5_six392_C | BES_TR5_six431_C | BES_TR5_six441_A | BES_TR5_six512_B | BES_TR5_six518_B | BES_TR5_six523_C | BES_TR5_six534_B | BES_TR5_six591_C | BES_TR5_six595_B | BES_TR5_six643_A | BES_TR5_six646_B | BES_TR5_six651_C | BES_TR5_six87_A | BES_TR5_six665_B | BES_TR5_six718_C | BES_TR5_six721_A | BES_TR5_six723_B | BES_TR5_six740_A | BES_TR5_six799_B | BES_TR5_six807_A | BES_TR5_six852_B | BES_TR5_six860_C | BES_TR5_six885_A | BES_TR5_six909_C | BES_TR5_six921_B | BES_TR5_six929_A | BES_TR5_six952_A | BES_TR5_six967_B | BES_TR5_six111_C | BES_TR5_six1006_C
1 | 0 | 0.236 | 0.758 | 0.171 | 0.29 | 0.122 | 0.38 | 0.056 | 0.162 | 0.049 | 0.279 | 0.7 | 0.162 | 0.156 | 0.051 | 0.193 | 0.045 | 0.145 | 0.167 | 0.096 | 0.733 | 0.185 | 0.389 | 0.051 | 0.083 | 0.046 | 0.142 | 0.604 | 0.114 | 0.084 | 2.027 | 0.347 | 0.51 | 0.153 | 0.13 | 0.592 | 0.051 | 0.049 | 0.684 | 0.133 | 0.049 | 0.261 | 0.13 | 0.122 | 0.083 | 0.139 | 0.191 | 0.059 | 0.397 | 0.065 | 0.799 | 0.048 | 0.258 | 0.051 | 0.102 | 0.148 | 0.055 | 0.939 | 0.533 | 0.059 | 0.794 | 0.048 | 0.233 | 2.391 | 0.249 | 0.462 | 0.3 | 0.246 | 0.057 | 0.151 | 0.057 | 0.155 | 0.105 | 0.05 | 0.05 | 0.05 | 0.05 | 0.11 | 1.059 | 0.052 | 0.231 | 0.145 | 0.051 | 0.864 | 0.333 | 0.041 | 0.048 | 0.589 | 0.054 | 0.155 | 1.341 | 0.166 | 0.376 | 0.209 | 0.25 | 0.048 | 0.174 | 0.048 | 0.044 | 0.238 | 0.056 | 0.146 | 0.134 | 0.051 | 0.049 | 0.244 | 0.198 | 0.202 | 0.275 | 0.441 | 0.201 | 0.049 | 0.083 | 0.257 | 0.112 | 0.178 | 0.06 | 0.098 | 0.059 | 0.055 | 0.15 | 0.193 | 0.106 | 0.168 | 0.2 | 0.115 | 0.041 | 0.41 | 0.212 | 0.146 | 0.046 | 0.074 | 0.101 | 0.104 | 0.056 | 0.236 | 0.965 | 0.325 | 0.048 | 0.061 | 0.179 | 0.048 | 0.209 | 0.036 | 0.05 | 0.113 | 0.179 | 0.055 | 0.687 | 0.234 | 0.075 | 0.121 | 0.741 | 0.165 | 0.098 | 0.163 | 0.839 | 0.187 | 0.338 | 0.109 | 0.052 | 0.057 | 0.295 | 0.644 | 0.126 | 0.234 | 0.325 | 0.082 | 0.051 | 0.047 | 0.045 | 0.221 | 0.192 | 0.153 | 0.059 | 0.239 | 0.332 | 0.058 | 0.088 | 0.453 | 0.058 | 0.153 | 0.047 | 0.504 | 0.04 | 0.06 | 0.243 | 0.489 | 0.268 | 0.052 | 0.122 | 0.188 | 0.169 | 0.043 | 0.102 | 0.198 | 0.108 | 0.036 | 0.053 | 0.156 | 0.053 | 0.047 | 0.136 | 0.13 | 0.124 | 0.056 | 0.041 | 0.119 | 0.254 | 0.158 | 0.15 | 0.966 | 0.058 | 0.09 | 0.049
2 | 0.5 | 0.052 | 0.628 | 0.188 | 0.06 | 0.048 | 0.037 | 0.291 | 0.195 | 0.4 | 0.12 | 0.598 | 0.067 | 0.102 | 0.051 | 0.137 | 0.085 | 0.041 | 0.29 | 0.169 | 0.055 | 0.052 | 0.036 | 0.426 | 0.3 | 0.046 | 0.049 | 0.478 | 0.053 | 0.198 | 0.364 | 0.273 | 0.056 | 0.19 | 0.096 | 0.374 | 0.183 | 0.049 | 0.042 | 0.055 | 0.124 | 0.089 | 0.235 | 0.343 | 0.245 | 0.07 | 0.157 | 0.059 | 0.048 | 0.092 | 0.318 | 0.098 | 0.058 | 0.107 | 0.077 | 0.102 | 0.17 | 0.803 | 0.463 | 0.114 | 0.057 | 0.048 | 0.314 | 0 | 0.076 | 0.533 | 0.052 | 0.143 | 0.057 | 0.236 | 0.057 | 0.055 | 0.105 | 0.132 | 0.133 | 0.222 | 0.141 | 0.189 | 0.818 | 0.052 | 0.05 | 0.046 | 0.126 | 0.103 | 0.11 | 0.213 | 0.127 | 0.579 | 0.054 | 0.158 | 1.05 | 0.151 | 0.91 | 0.052 | 0.081 | 0.048 | 0.079 | 0.048 | 0.044 | 0.165 | 0.056 | 0.14 | 0.194 | 0.1 | 0.049 | 0.34 | 0.23 | 0.064 | 0.058 | 0.643 | 0.209 | 0.13 | 0.076 | 0.134 | 0.195 | 0.201 | 0.04 | 0.043 | 0.124 | 0.115 | 0.177 | 0.05 | 0.169 | 0.153 | 0.051 | 0.444 | 0.192 | 0.177 | 0.105 | 0.125 | 0.046 | 0.267 | 0.156 | 0.165 | 0.214 | 0.179 | 0.917 | 0.481 | 0.063 | 0.134 | 0.12 | 0.048 | 0.076 | 0.186 | 0.184 | 0.041 | 0.041 | 0.168 | 0.076 | 0.052 | 0.15 | 0.051 | 0.12 | 0.049 | 0.505 | 0.081 | 0.965 | 0.172 | 0.225 | 0.056 | 0.052 | 0.057 | 0.037 | 0.55 | 0.059 | 0.11 | 0.051 | 0.183 | 0.165 | 0.063 | 0.547 | 0.353 | 0.123 | 0.268 | 0.059 | 0.286 | 0.181 | 0.154 | 0.248 | 0.721 | 0.215 | 0.1 | 0.113 | 0.255 | 0.04 | 0.06 | 0.166 | 0.562 | 0.051 | 0.052 | 0.099 | 0.093 | 0.058 | 0.2 | 0.048 | 0.104 | 0.218 | 0.157 | 0.176 | 0.269 | 0.053 | 0.101 | 0.118 | 0.249 | 0.111 | 0.226 | 0.201 | 0.047 | 0.057 | 0.121 | 0.252 | 0.709 | 0.15 | 0.225 | 0.049
3 | 1 | 0.16 | 0.777 | 0.115 | 0.361 | 0.122 | 0.037 | 0.056 | 0.056 | 0.098 | 0.166 | 0.702 | 0.122 | 0.078 | 0.051 | 0.045 | 0.168 | 0.216 | 0.126 | 0.052 | 0.055 | 0.138 | 0.066 | 0.402 | 0.12 | 0.046 | 0.049 | 0.055 | 0.155 | 0.129 | 0 | 0.044 | 0.056 | 0.051 | 0.166 | 0.448 | 0.051 | 0.049 | 0.175 | 0.072 | 0.09 | 0.084 | 0.111 | 0.049 | 0.198 | 0.055 | 0.041 | 0.236 | 0.225 | 0.274 | 0.263 | 0.135 | 0.236 | 0.097 | 0.051 | 0.235 | 0.089 | 0.649 | 0.093 | 0.27 | 0.057 | 0.048 | 0.06 | 0 | 0.214 | 0.216 | 0.052 | 0.056 | 0.057 | 0.069 | 0.057 | 0.055 | 0.044 | 0.07 | 0.092 | 0.172 | 0.05 | 0.055 | 0.054 | 0.052 | 0.05 | 0.046 | 0.219 | 0.177 | 0.13 | 0.175 | 0.127 | 0.751 | 0.06 | 0.16 | 0 | 0.064 | 1.104 | 0.052 | 0.057 | 0.199 | 0.072 | 0.048 | 0.044 | 0.133 | 0.056 | 0.146 | 0.079 | 0.155 | 0.125 | 0.335 | 0.252 | 0.189 | 0.324 | 0.665 | 0.05 | 0.049 | 0.09 | 0.227 | 0.059 | 0.091 | 0.04 | 0.292 | 0.05 | 0.196 | 0.213 | 0.05 | 0.134 | 0.258 | 0.105 | 0.358 | 0.041 | 0.089 | 0.344 | 0.145 | 0.046 | 0.06 | 0.053 | 0.05 | 0.071 | 0.28 | 0.408 | 0.113 | 0.196 | 0.226 | 0.087 | 0.299 | 0.077 | 0.036 | 0.05 | 0.041 | 0.148 | 0.061 | 0.086 | 0.248 | 0.05 | 0.184 | 0.058 | 0.186 | 0.35 | 0.275 | 0.297 | 0.141 | 0.05 | 0.056 | 0.052 | 0.163 | 0.037 | 0.125 | 0.093 | 0.176 | 0.073 | 0.053 | 0.116 | 0.103 | 0.036 | 0.05 | 0.056 | 0.084 | 0.247 | 0.362 | 0.116 | 0.058 | 0.216 | 0.049 | 0.14 | 0.054 | 0.223 | 0.074 | 0.28 | 0.076 | 0.118 | 0.221 | 0.065 | 0.052 | 0.072 | 0.079 | 0.425 | 0.181 | 0.048 | 0.108 | 0.151 | 0.093 | 0.053 | 0.047 | 0.053 | 0.143 | 0.1 | 0.049 | 0.228 | 0.056 | 0.041 | 0.15 | 0.229 | 0.084 | 0.13 | 0.716 | 0.169 | 0.042 | 0.049
4 | 1.5 | 0.127 | 0.228 | 0.115 | 0.039 | 0.048 | 0.037 | 0.056 | 0.262 | 0.162 | 0.219 | 0.351 | 0.108 | 0.051 | 0.051 | 0.195 | 0.031 | 0.118 | 0.175 | 0.052 | 0.21 | 0.098 | 0.28 | 0.347 | 0.186 | 0.046 | 0.049 | 0.055 | 0.101 | 0.062 | 0 | 0.044 | 0.056 | 0.248 | 0.081 | 0.207 | 0.051 | 0.049 | 1.147 | 0.116 | 0.049 | 0.103 | 0.15 | 0.086 | 0.237 | 0.129 | 0.257 | 0.059 | 0.048 | 0.045 | 0.201 | 0.06 | 0.08 | 0.077 | 0.051 | 0.095 | 0.13 | 0 | 0.235 | 0.075 | 0.057 | 0.048 | 0.256 | 0 | 0.117 | 0.176 | 0.192 | 0.371 | 0.057 | 0.167 | 0.057 | 0.155 | 0.138 | 0.05 | 0.1 | 0.05 | 0.05 | 0.169 | 0.069 | 0.052 | 0.231 | 0.046 | 0.051 | 0.057 | 0.208 | 0.112 | 0.055 | 0.472 | 0.175 | 0.096 | 0 | 0.103 | 0 | 0.145 | 0.38 | 0.055 | 0.18 | 0.048 | 0.17 | 0.16 | 0.056 | 0.125 | 0.192 | 0.051 | 0.049 | 0.211 | 0.242 | 0.05 | 0.135 | 0.642 | 0.251 | 0.049 | 0.085 | 0.232 | 0.089 | 0.362 | 0.04 | 0.06 | 0.05 | 0.075 | 0.184 | 0.05 | 0.051 | 0.048 | 0.146 | 0.087 | 0.096 | 0.052 | 0.161 | 0.056 | 0.046 | 0.052 | 0.053 | 0.104 | 0.056 | 0.128 | 0.092 | 0.138 | 0.048 | 0.134 | 0.161 | 0.149 | 0.112 | 0.036 | 0.05 | 0.061 | 0.072 | 0.055 | 0.191 | 0.189 | 0.175 | 0.152 | 0.101 | 0.063 | 0.691 | 0.052 | 0.279 | 0.179 | 0.05 | 0.056 | 0.052 | 0.057 | 0.037 | 0.145 | 0.093 | 0.14 | 0.304 | 0.082 | 0.051 | 0.047 | 0.036 | 0.168 | 0.056 | 0.117 | 0.495 | 0.346 | 0.349 | 0.079 | 0.213 | 0.117 | 0.149 | 0.179 | 0.047 | 0.152 | 0.06 | 0.152 | 0.298 | 0.081 | 0.195 | 0.052 | 0.112 | 0.242 | 0.058 | 0.091 | 0.217 | 0.184 | 0.135 | 0.068 | 0.053 | 0.296 | 0.053 | 0.064 | 0.219 | 0.169 | 0.06 | 0.087 | 0.135 | 0.047 | 0.123 | 0.155 | 0.319 | 0 | 0.058 | 0.161 | 0.049
5 | 2 | 0.052 | 0 | 0.176 | 0.103 | 0.048 | 0.037 | 0.171 | 0.095 | 0.226 | 0.055 | 0.04 | 0.047 | 0.051 | 0.051 | 0.241 | 0.222 | 0.118 | 0.218 | 0.214 | 0.055 | 0.112 | 0.036 | 0.051 | 0.264 | 0.046 | 0.049 | 0.055 | 0.073 | 0.071 | 0 | 0.044 | 0.056 | 0.095 | 0.201 | 0.17 | 0.117 | 0.049 | 0.057 | 0.055 | 0.165 | 0.075 | 0.098 | 0.277 | 0.235 | 0.08 | 0.041 | 0.195 | 0.177 | 0.285 | 0.089 | 0.172 | 0.076 | 0.128 | 0.051 | 0.209 | 0.13 | 0 | 0.048 | 0.059 | 0.057 | 0.048 | 0.143 | 0 | 0.196 | 0.119 | 0.16 | 0.094 | 0.057 | 0.237 | 0.057 | 0.055 | 0.072 | 0.05 | 0.147 | 0.214 | 0.05 | 0.202 | 0.128 | 0.052 | 0.05 | 0.118 | 0.076 | 0.091 | 0.094 | 0.143 | 0.198 | 0 | 0.054 | 0.13 | 0 | 0.16 | 0 | 0.116 | 0.057 | 0.192 | 0.052 | 0.048 | 0.178 | 0.082 | 0.056 | 0.101 | 0.165 | 0.204 | 0.049 | 0.702 | 0.283 | 0.161 | 0.125 | 0 | 0.295 | 0.13 | 0.204 | 0.22 | 0.242 | 0.167 | 0.151 | 0.105 | 0.173 | 0.117 | 0.145 | 0.102 | 0.134 | 0.288 | 0.051 | 0.21 | 0.137 | 0.177 | 0.25 | 0.213 | 0.046 | 0.304 | 0.053 | 0.165 | 0.063 | 0.223 | 0.009 | 0.169 | 0.048 | 0.126 | 0.067 | 0.048 | 0.142 | 0.07 | 0.05 | 0.093 | 0.041 | 0.233 | 0.052 | 0.105 | 0.05 | 0.051 | 0.101 | 0.049 | 0.055 | 0.206 | 0.011 | 0.056 | 0.05 | 0.056 | 0.052 | 0.14 | 0.037 | 0.05 | 0.049 | 0.099 | 0.071 | 0.183 | 0.23 | 0.107 | 0.036 | 0.173 | 0.056 | 0.057 | 0.059 | 0.287 | 0.097 | 0.133 | 0.107 | 0.177 | 0.15 | 0.074 | 0.202 | 0.074 | 0.04 | 0.06 | 0.066 | 0.195 | 0.051 | 0.052 | 0.157 | 0.075 | 0.345 | 0.202 | 0.048 | 0.14 | 0.114 | 0.182 | 0.176 | 0.128 | 0.053 | 0.138 | 0.088 | 0.28 | 0.137 | 0.195 | 0.106 | 0.047 | 0.057 | 0.127 | 0.205 | 0 | 0.261 | 0.154 | 0.049
6 | 2.5 | 0.094 | 0 | 0.048 | 0.266 | 0.077 | 0.037 | 0.09 | 0.152 | 0.175 | 0.097 | 0 | 0.047 | 0.051 | 0.051 | 0.062 | 0.031 | 0.215 | 0.155 | 0.052 | 0.076 | 0.125 | 0.251 | 0.108 | 0.053 | 0.046 | 0.049 | 0.055 | 0.183 | 0.119 | 0 | 0.044 | 0.056 | 0.051 | 0.138 | 0.064 | 0.117 | 0.049 | 0.195 | 0.133 | 0.049 | 0.2 | 0.078 | 0.049 | 0.142 | 0.124 | 0.041 | 0.099 | 0.096 | 0.08 | 0.265 | 0.048 | 0.24 | 0.051 | 0.119 | 0.171 | 0.055 | 0 | 0.12 | 0.059 | 0.057 | 0.048 | 0.175 | 0 | 0.124 | 0.096 | 0.109 | 0.201 | 0.057 | 0.052 | 0.057 | 0.155 | 0.044 | 0.152 | 0.05 | 0.143 | 0.05 | 0.093 | 0.054 | 0.052 | 0.083 | 0.046 | 0.116 | 0.151 | 0.249 | 0.148 | 0.048 | 0 | 0.182 | 0.232 | 0 | 0.172 | 0 | 0.081 | 0.181 | 0.274 | 0.18 | 0.048 | 0.077 | 0.116 | 0.056 | 0.113 | 0.07 | 0.051 | 0.049 | 0.096 | 0.178 | 0.092 | 0.223 | 0 | 0.066 | 0.049 | 0.076 | 0.067 | 0.073 | 0.051 | 0.073 | 0.214 | 0.179 | 0.15 | 0.13 | 0.141 | 0.138 | 0.048 | 0.2 | 0.109 | 0.041 | 0.089 | 0.206 | 0.04 | 0.046 | 0.045 | 0.115 | 0.05 | 0.221 | 0.045 | 0 | 0.065 | 0.21 | 0.202 | 0.152 | 0.323 | 0.045 | 0.152 | 0.05 | 0.041 | 0.179 | 0.126 | 0.225 | 0.196 | 0.175 | 0.281 | 0.058 | 0.063 | 0.04 | 0.079 | 0 | 0.056 | 0.05 | 0.056 | 0.085 | 0.08 | 0.037 | 0.11 | 0.049 | 0.181 | 0.153 | 0.053 | 0.051 | 0.059 | 0.036 | 0.061 | 0.127 | 0.279 | 0.059 | 0.184 | 0.187 | 0.058 | 0.232 | 0.049 | 0.045 | 0.054 | 0.133 | 0.057 | 0.267 | 0.168 | 0.199 | 0.136 | 0.21 | 0.052 | 0.125 | 0.099 | 0.147 | 0.224 | 0.148 | 0.058 | 0.256 | 0.036 | 0.053 | 0.047 | 0.053 | 0.047 | 0.205 | 0.121 | 0.199 | 0.056 | 0.041 | 0.15 | 0.057 | 0.103 | 0.114 | 0 | 0.058 | 0.042 | 0.049
7 | 3 | 0.194 | 0 | 0.311 | 0.092 | 0.093 | 0.037 | 0.142 | 0.204 | 0.242 | 0.249 | 0 | 0.122 | 0.051 | 0.051 | 0.253 | 0.121 | 0.041 | 0.064 | 0.052 | 0.189 | 0.052 | 0.095 | 0.151 | 0.397 | 0.046 | 0.049 | 0.055 | 0.053 | 0.081 | 0 | 0.044 | 0.056 | 0.219 | 0.089 | 0.354 | 0.075 | 0.049 | 0.042 | 0.055 | 0.066 | 0.135 | 0.3 | 0.237 | 0.238 | 0.085 | 0.257 | 0.131 | 0.048 | 0.123 | 0.16 | 0.154 | 0.044 | 0.051 | 0.06 | 0.048 | 0.116 | 0 | 0.208 | 0.291 | 0.057 | 0.048 | 0.295 | 0 | 0.072 | 0.177 | 0.095 | 0.264 | 0.057 | 0.234 | 0.057 | 0.055 | 0.127 | 0.05 | 0.091 | 0.094 | 0.05 | 0.278 | 0.143 | 0.052 | 0.198 | 0.046 | 0.204 | 0.129 | 0.393 | 0.24 | 0.191 | 0 | 0.054 | 0.052 | 0 | 0.107 | 0 | 0.181 | 0.242 | 0.221 | 0.072 | 0.048 | 0.272 | 0.16 | 0.056 | 0.053 | 0.165 | 0.169 | 0.096 | 0.202 | 0.171 | 0.05 | 0.091 | 0 | 0.341 | 0.049 | 0.076 | 0.158 | 0.12 | 0.294 | 0.079 | 0.2 | 0.05 | 0.119 | 0.177 | 0.056 | 0.221 | 0.048 | 0.051 | 0.084 | 0.041 | 0.052 | 0.14 | 0.114 | 0.046 | 0.045 | 0.142 | 0.219 | 0.056 | 0.205 | 0 | 0.14 | 0.048 | 0.108 | 0.143 | 0.074 | 0.209 | 0.036 | 0.05 | 0.041 | 0.041 | 0.055 | 0.055 | 0.189 | 0.05 | 0.054 | 0.144 | 0.186 | 0.233 | 0.233 | 0 | 0.326 | 0.05 | 0.056 | 0.052 | 0.057 | 0.037 | 0.159 | 0.136 | 0.168 | 0.217 | 0.169 | 0.051 | 0.047 | 0.116 | 0.238 | 0.056 | 0.087 | 0.059 | 0.21 | 0.326 | 0.127 | 0.142 | 0.106 | 0.251 | 0.093 | 0.128 | 0.057 | 0.072 | 0.06 | 0.264 | 0.099 | 0.051 | 0.052 | 0.046 | 0.218 | 0.162 | 0.34 | 0.117 | 0.23 | 0.117 | 0.173 | 0.053 | 0.212 | 0.053 | 0.047 | 0.103 | 0.232 | 0.057 | 0.219 | 0.201 | 0.047 | 0.189 | 0.353 | 0.359 | 0 | 0.209 | 0.258 | 0.049
8 | 3.5 | 0.05 | 0 | 0.045 | 0.287 | 0.046 | 0.036 | 0.053 | 0.085 | 0.239 | 0.119 | 0 | 0.105 | 0.05 | 0.048 | 0.164 | 0.043 | 0.038 | 0.178 | 0.123 | 0.052 | 0.156 | 0.143 | 0.056 | 0.05 | 0.043 | 0.048 | 0.053 | 0.181 | 1.102 | 0 | 0.041 | 0.053 | 0.121 | 0.205 | 0.181 | 0.156 | 0.046 | 0.049 | 0.053 | 0.147 | 0.049 | 0.05 | 0.123 | 0.141 | 0.072 | 0.038 | 0.161 | 0.046 | 0.077 | 0.191 | 0.076 | 0.196 | 0.049 | 0.048 | 0.061 | 0.14 | 0 | 0.045 | 0.106 | 0.055 | 0.046 | 0.096 | 0 | 0.096 | 0.101 | 0.139 | 0.053 | 0.054 | 0.168 | 0.055 | 0.064 | 0.079 | 0.13 | 0.102 | 0.212 | 0.138 | 0.053 | 0.051 | 0.049 | 0.048 | 0.116 | 0.14 | 0.117 | 0.337 | 0.038 | 0.061 | 0 | 0.077 | 0.257 | 0 | 0.047 | 0 | 0.049 | 0.124 | 0.045 | 0.076 | 0.045 | 0.041 | 0.127 | 0.053 | 0.158 | 0.169 | 0.083 | 0.077 | 0.192 | 0.18 | 0.199 | 0.367 | 0 | 0.186 | 0.046 | 0.188 | 0.131 | 0.149 | 0.114 | 0.142 | 0.048 | 0.131 | 0.222 | 0.218 | 0.184 | 0.048 | 0.115 | 0.179 | 0.164 | 0.039 | 0.159 | 0.27 | 0.124 | 0.043 | 0.309 | 0.05 | 0.047 | 0.053 | 0.073 | 0 | 0.176 | 0.178 | 0.043 | 0.163 | 0.097 | 0.043 | 0.3 | 0.048 | 0.052 | 0.094 | 0.171 | 0.146 | 0.102 | 0.173 | 0.221 | 0.056 | 0.047 | 0.067 | 0.102 | 0 | 0.076 | 0.047 | 0.053 | 0.05 | 0.076 | 0.035 | 0.097 | 0.046 | 0.053 | 0.076 | 0.094 | 0.228 | 0.118 | 0.034 | 0.09 | 0.125 | 0.307 | 0.057 | 0.047 | 0.047 | 0.082 | 0.266 | 0.248 | 0.079 | 0.157 | 0.109 | 0.054 | 0.174 | 0.084 | 0.164 | 0.048 | 0.049 | 0.049 | 0.221 | 0.073 | 0.31 | 0.359 | 0.052 | 0.105 | 0.173 | 0.074 | 0.172 | 0.209 | 0.051 | 0.193 | 0.061 | 0.256 | 0.116 | 0.061 | 0.038 | 0.148 | 0.16 | 0.472 | 0.101 | 0 | 0.106 | 0.053 | 0.046
9 | 4 | 0.021 | 0 | 0 | 0.102 | 0.097 | 0.018 | 0.192 | 0.224 | 0.174 | 0.095 | 0 | 0.01 | 0.032 | 0.001 | 0.026 | 0 | 0.194 | 0.143 | 0.109 | 0.018 | 0.047 | 0.169 | 0.164 | 0.255 | 0.002 | 0.03 | 0.024 | 0.049 | 0.002 | 0 | 0 | 0.019 | 0.007 | 0.035 | 0 | 0.001 | 0 | 0 | 0.102 | 0.03 | 0.173 | 0.269 | 0.069 | 0.152 | 0.091 | 0.034 | 0.022 | 0.176 | 0.189 | 0.019 | 0.073 | 0.094 | 0.394 | 0.084 | 0.265 | 0.005 | 0 | 0.188 | 0.066 | 0.026 | 0.023 | 0.2 | 0 | 0.211 | 0.096 | 0.094 | 0.177 | 0.007 | 0.068 | 0.026 | 0.126 | 0 | 0.046 | 0.0003 | 0.135 | 0.0003 | 0.226 | 0.014 | 0.002 | 0.207 | 0.015 | 0.116 | 0.007 | 0.298 | 0.303 | 0.087 | 0 | 0.119 | 0.078 | 0 | 0.368 | 0 | 0.008 | 0.349 | 0.128 | 0.124 | 0 | 0.033 | 0.189 | 0.006 | 0.088 | 0.006 | 0.048 | 0.018 | 0.037 | 0.258 | 0.0003 | 0.039 | 0 | 0.266 | 0.005 | 0.061 | 0.251 | 0.102 | 0.087 | 0.009 | 0.217 | 0.013 | 0.072 | 0.116 | 0.013 | 0.08 | 0.128 | 0.053 | 0.067 | 0.01 | 0.06 | 0.211 | 0.06 | 0 | 0.008 | 0.009 | 0.013 | 0.081 | 0.096 | 0 | 0.017 | 0.034 | 0.119 | 0.061 | 0.285 | 0.02 | 0 | 0.159 | 0.082 | 0.073 | 0.161 | 0.074 | 0.196 | 0.013 | 0.062 | 0.108 | 0.141 | 0.158 | 0.118 | 0 | 0.167 | 0.013 | 0.006 | 0.027 | 0.09 | 0.012 | 0.119 | 0.055 | 0.377 | 0.228 | 0.137 | 0.014 | 0.022 | 0.005 | 0.031 | 0.025 | 0.11 | 0.028 | 0.126 | 0.078 | 0.021 | 0.3 | 0.47 | 0.126 | 0.023 | 0.093 | 0.013 | 0.133 | 0.091 | 0.191 | 0.332 | 0.164 | 0.002 | 0.021 | 0.058 | 0.033 | 0.042 | 0.159 | 0.114 | 0.179 | 0.063 | 0.003 | 0.077 | 0.022 | 0.143 | 0.156 | 0.113 | 0.184 | 0.019 | 0 | 0.01 | 0.02 | 0.026 | 0.179 | 0 | 0.06 | 0 | 0.012
10 | 4.5 | 0.09 | 0 | 0.078 | 0 | 0 | 0 | 0 | 0 | 0.149 | 0 | 0 | 0 | 0 | 0 | 0.063 | 0 | 0 | 0 | 0 | 0.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028 | 0 | 0 | 0 | 0.038 | 0 | 0 | 0 | 0 | 0.035 | 0.085 | 0 | 0.037 | 0.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0 | 0 | 0.119 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061 | 0 | 0 | 0.013 | 0 | 0.156 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0.034 | 0.077 | 0 | 0 | 0.018 | 0 | 0 | 0 | 0 | 0 | 0.089 | 0 | 0 | 0 | 0 | 0 | 0.063 | 0.042 | 0 | 0.031 | 0 | 0 | 0.06 | 0.018 | 0 | 0.043 | 0 | 0 | 0 | 0 | 0.074 | 0 | 0 | 0.093 | 0 | 0.217 | 0 | 0 | 0 | 0.024 | 0 | 0.011 | 0 | 0 | 0.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038 | 0.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053 | 0 | 0.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064 | 0.122 | 0 | 0 | 0 | 0 | 0.212 | 0.174 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056 | 0.123 | 0.002 | 0 | 0 | 0 | 0
11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.093 | 0 | 0 | 0.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.089 | 0 | 0.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.358 | 0.014 | 0 | 0 | 0 | 0.192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.138 | 0 | 0 | 0 | 0.092 | 0 | 0 | 0.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.153 | 0 | 0 | 0 | 0 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.159 | 0 | 0 | 0.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.543 | 1.719 | 0 | 0 | 0 | 0 | 0 | 0.335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014 | 0 | 0 | 0 | 0.055 | 0 | 0 | 0.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.739 | 0 | 0 | 0 | 1.455 | 0 | 0 | 0 | 0 | 1.327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063 | 0 | 0 | 0 | 0 | 0.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 9 | 0 | 0 | 0 | 0 | 0 | 1.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41 | 0 | 0 | 1.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.287 | 0 | 0.311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.61 | 0 | 0 | 0 | 0 | 0.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.603 | 0 | 0
21 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.387 | 0 | 0 | 1.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.342 | 0 | 0.986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.366 | 0 | 0
22 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.451 | 0 | 0 | 0 | 0.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.204 | 0 | 0
23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.285 | 0 | 0 | 0 | 0 | 0.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.218 | 0 | 0 | 0 | 0.165 | 0 | 0 | 0 | 0.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.378 | 0 | 0 | 0 | 0 | 0 | 0 | 0.277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38 | 0 | 0 | 0 | 0.497 | 0 | 0 | 0 | 0 | 0.187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053 | 0 | 0 | 0.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.445 | 0 | 0 | 0 | 0.147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.316 | 0 | 0 | 1.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0
34 | 16.5 | 1.019 | 0 | 0 | 0 | 0.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0.348 | 0 | 0 | 0 | 0 | 0.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.383 | 0 | 0 | 0.503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.851 | 0 | 0.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.611 | 0 | 0 | 0 | 0.246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.852 | 0 | 0 | 0 | 0 | 0.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 17 | 0.86 | 0 | 0 | 0 | 0.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.142 | 0 | 1.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0.752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.275 | 0 | 0.044 | 1.461 | 0 | 0 | 0 | 0.056 | 0 | 0 | 2.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.706 | 0 | 0 | 0 | 0 | 0 | 0 | 1.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.198 | 0 | 0
36 | 17.5 | 0 | 0 | 0 | 0.144 | 1.271 | 0 | 0.174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.149 | 0 | 1.183 | 0 | 0.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0 | 0 | 0.238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.108 | 0 | 0 | 2.13 | 0.624 | 0 | 0 | 0 | 0 | 1.231 | 0 | 0 | 0 | 0 | 0 | 2.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019 | 0 | 0 | 0.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.706 | 0 | 1.353 | 1.505 | 0.129 | 0 | 0 | 0 | 1.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.532 | 0 | 0 | 1.323 | 0 | 0 | 0 | 0 | 0.571 | 0 | 1.304 | 0 | 0 | 0 | 0 | 0.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079 | 0 | 0 | 0 | 1.363 | 0 | 0.812 | 0.924 | 1.035 | 0 | 0 | 0 | 0 | 0 | 0.584 | 0 | 0 | 0 | 0 | 0 | 0 | 2.137 | 0 | 0.247 | 0 | 0.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019 | 0 | 0 | 0.009 | 0 | 0 | 0.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.488 | 0 | 0 | 0 | 1.338 | 0 | 1.925
37 | 18 | 0 | 0 | 0 | 0 | 0.473 | 0 | 0 | 0.381 | 0 | 0 | 0 | 0 | 0.249 | 0 | 0 | 0 | 0 | 0 | 0 | 0.932 | 0 | 0 | 0 | 0 | 0.679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.775 | 0 | 0 | 0 | 0 | 0 | 0.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 1.987 | 1.188 | 0.631 | 0 | 0 | 0 | 1.024 | 0 | 0 | 0.517 | 0 | 0 | 2.125 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0.154 | 0 | 0 | 0.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0.244 | 0 | 0 | 0 | 0 | 0 | 0.084 | 0 | 0 | 0 | 0 | 0 | 1.398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.019 | 0 | 0 | 0 | 1.56 | 0 | 0.079 | 0 | 0 | 0 | 0 | 0 | 1.657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.508 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0.557 | 0 | 1.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012 | 0 | 0 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017 | 0 | 0 | 0 | 0.054 | 0 | 2.628
38 | 18.5 | 0.132 | 0 | 0 | 0 | 0.829 | 0 | 0 | 0.372 | 0.114 | 0 | 0 | 0 | 0.753 | 0 | 0 | 0 | 0 | 0 | 0 | 1.933 | 0 | 0.087 | 0 | 0 | 1.203 | 0 | 0 | 1.312 | 0 | 0 | 0 | 0.197 | 0 | 0 | 0.051 | 0 | 0 | 0.266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.808 | 0 | 0 | 0 | 0 | 0.304 | 0 | 0 | 0 | 0.565 | 0.086 | 0.094 | 0.968 | 0 | 0 | 0.017 | 0.006 | 0.972 | 0 | 0 | 0 | 0.147 | 0 | 0 | 0 | 0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0.669 | 0 | 0 | 0 | 0.056 | 0.001 | 0 | 0 | 0 | 0.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022 | 0.281 | 0 | 0 | 0 | 0.294 | 0 | 0.216 | 0.153 | 0 | 0 | 0 | 0 | 1.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065 | 0 | 0 | 0 | 0 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0.023 | 0 | 0 | 0 | 1.37 | 0 | 1.053 | 0 | 0.122 | 0 | 0 | 0.028 | 0 | 0 | 0 | 0.289 | 0 | 0 | 0 | 0 | 0 | 0.031 | 1.461 | 0 | 1.444 | 0 | 1.42 | 0 | 0 | 0 | 0 | 1.651 | 0.962 | 0.31 | 0 | 0 | 0.456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042 | 0 | 0 | 1.23 | 0 | 0 | 0.01 | 0 | 0 | 0.762 | 0 | 0 | 0.284 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.184 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037
39 | 19 | 0.331 | 0 | 0.029 | 0.106 | 0.408 | 0.005 | 0.632 | 0.36 | 0.134 | 0.076 | 0 | 0 | 2.366 | 0 | 0 | 0 | 0 | 0 | 0.061 | 0.569 | 0 | 0.723 | 0 | 0.397 | 0 | 0 | 0 | 0.249 | 0 | 1.049 | 0 | 0.696 | 0 | 0 | 0.185 | 0 | 0 | 1.185 | 0.051 | 0 | 0.176 | 0.02 | 0.233 | 0 | 0.431 | 0 | 0 | 0.306 | 0 | 0 | 0 | 0.097 | 0.162 | 0 | 0 | 0.058 | 0 | 0 | 0.227 | 0.117 | 0.223 | 0.127 | 0.014 | 0 | 0 | 0.074 | 0.13 | 0 | 0.108 | 0 | 0.438 | 0 | 0.19 | 1.105 | 0.472 | 0 | 1.389 | 0 | 0 | 0.042 | 0 | 0.061 | 0 | 0 | 0 | 0.257 | 0.145 | 0.106 | 0 | 1.683 | 0.182 | 0.08 | 0 | 0.061 | 0.233 | 0 | 0.048 | 0 | 0 | 0 | 0.108 | 1.098 | 0 | 0 | 0 | 0.14 | 0.182 | 1.048 | 0 | 0 | 0 | 0.119 | 1.028 | 0 | 0 | 1.249 | 0 | 0 | 0.071 | 0.036 | 0 | 0 | 0.288 | 0 | 0 | 0.518 | 0 | 0.272 | 0 | 0 | 0 | 0.216 | 0.231 | 0.371 | 0 | 0.025 | 0 | 0.672 | 0 | 0 | 0 | 0.758 | 0 | 0 | 0.241 | 0 | 0 | 0 | 0.208 | 0.095 | 0 | 0.346 | 0.012 | 0 | 0.117 | 1.511 | 0 | 0.045 | 0 | 1.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.038 | 0 | 1.256 | 0 | 0 | 0 | 0 | 0.078 | 0.773 | 0.109 | 0.814 | 0.289 | 0.034 | 0.337 | 0 | 0.08 | 0.159 | 0 | 0.368 | 0 | 0 | 0.767 | 0 | 0 | 0.202 | 0.018 | 0 | 0.921 | 0 | 0 | 0 | 0.085 | 0 | 0 | 0 | 0.442 | 0.103 | 0.082 | 0.781 | 0.024 | 0.132 | 0 | 0.044 | 0.306 | 0 | 0 | 0.104
40 | 19.5 | 0.262 | 0.367 | 0.363 | 0.416 | 0.49 | 0.217 | 0.458 | 0.619 | 0.132 | 0.315 | 0.432 | 0 | 0.158 | 0.213 | 0.148 | 0 | 0 | 0 | 0.348 | 0.031 | 0 | 0.506 | 0.028 | 0.485 | 0.108 | 0.129 | 0 | 0.484 | 0.311 | 1.285 | 0 | 0.279 | 0.125 | 0.001 | 0.363 | 0.231 | 0.495 | 0.379 | 0.292 | 0.308 | 0.39 | 0.142 | 0.329 | 0.182 | 0.452 | 0.602 | 0.519 | 0.371 | 0.21 | 0.234 | 0.315 | 0.158 | 0.31 | 0.33 | 0.258 | 0.779 | 0.43 | 0.049 | 0.405 | 0.358 | 0.512 | 0.4 | 0.359 | 0.558 | 0.106 | 0.453 | 0.385 | 0 | 0.421 | 0 | 0.468 | 0.235 | 0.61 | 0.451 | 0.558 | 0.162 | 0.323 | 0.395 | 0.213 | 0.449 | 0 | 1.584 | 0.306 | 1.712 | 0.236 | 0.303 | 0.41 | 0.823 | 0 | 0.572 | 0.504 | 0.29 | 0.39 | 0.461 | 0.082 | 0 | 0.414 | 0.252 | 0.602 | 0.453 | 0.325 | 1.542 | 0.298 | 0 | 0.056 | 0.835 | 0.217 | 0.333 | 0.353 | 0.582 | 0.331 | 0.579 | 0.455 | 0.094 | 0.11 | 0.396 | 0.263 | 0.138 | 0.579 | 0.001 | 0.099 | 0.294 | 0.487 | 0.126 | 1.367 | 0.846 | 0.083 | 0.56 | 0.039 | 0 | 0.84 | 0.178 | 3.041 | 0.426 | 0.178 | 0.411 | 0 | 0.5 | 0.174 | 0.357 | 0.249 | 1.778 | 0.224 | 0 | 0.458 | 0 | 0.037 | 0.317 | 0.586 | 0.178 | 0.053 | 0.352 | 0.18 | 0.039 | 0.094 | 1.373 | 0.603 | 0.287 | 0 | 0.976 | 0.079 | 0.264 | 0.233 | 0.338 | 0.114 | 0.523 | 0.087 | 0.312 | 0.125 | 0.291 | 0 | 0.213 | 0.131 | 0.772 | 0.186 | 1.077 | 0.909 | 0.302 | 0.385 | 0.71 | 0.445 | 0.184 | 0.222 | 0.463 | 0.023 | 0.178 | 0.068 | 0.143 | 0.802 | 0.232 | 0.256 | 0.53 | 0.27 | 0.16 | 0.541 | 0.921 | 0.028 | 0.202 | 0.352 | 0.323 | 0.024 | 0.095 | 0.079 | 0.223 | 0.278 | 0.798 | 0.464 | 0.165 | 0.107 | 0.281 | 2.912 | 0.04 | 0.002 | 0.169
41 | 20 | 0.068 | 0.253 | 0.433 | 0.389 | 0.57 | 0.54 | 0.796 | 1.107 | 0.316 | 0.549 | 0.505 | 0.127 | 0.453 | 0.34 | 0.142 | 0.086 | 0.12 | 0.312 | 0.847 | 0.158 | 0.166 | 0.47 | 0.036 | 0.855 | 0.281 | 0.186 | 0.043 | 0.469 | 0.278 | 1.683 | 0.211 | 0.429 | 0.034 | 0.183 | 0.709 | 0.449 | 0.418 | 0.606 | 0.23 | 0.569 | 0.392 | 0.04 | 0.444 | 0.45 | 0.391 | 0.645 | 0.464 | 0.135 | 0.342 | 0.261 | 0.318 | 0.088 | 0.578 | 0.349 | 0.627 | 1.315 | 0.794 | 0.079 | 0.493 | 0.045 | 0.551 | 1.466 | 0.484 | 0.512 | 0.048 | 0.386 | 0.696 | 0.037 | 0.583 | 0.045 | 0.649 | 0.54 | 1.037 | 0.229 | 0.476 | 0.314 | 0.53 | 0.453 | 0.126 | 0.552 | 0.034 | 1.175 | 0.387 | 0.569 | 0.266 | 0.464 | 0.836 | 0.594 | 0.197 | 0.751 | 0.369 | 0.375 | 0.353 | 0.53 | 0.194 | 0.032 | 0.318 | 0.558 | 0.564 | 0.445 | 0.39 | 0.459 | 1.344 | 0.071 | 0.119 | 0.452 | 0.433 | 0.498 | 0.586 | 0.65 | 1.614 | 0.657 | 0.696 | 0.094 | 0.175 | 0.099 | 0.717 | 0.072 | 0.484 | 0.163 | 0.035 | 0.397 | 0.681 | 0.044 | 0.591 | 0.416 | 0.071 | 0.497 | 0.107 | 0.026 | 0.637 | 0.288 | 2.469 | 0.377 | 0.674 | 0.498 | 0.154 | 0.681 | 0.274 | 0.334 | 0.434 | 1.295 | 0.321 | 0.174 | 0.599 | 0.103 | 0.139 | 0.419 | 0.74 | 0.182 | 0.117 | 0.583 | 0.247 | 0.087 | 0.501 | 0.571 | 0.345 | 0.351 | 0.036 | 0.27 | 0.357 | 0.486 | 0.344 | 0.475 | 0.561 | 0.656 | 0.098 | 0.575 | 0.274 | 0.257 | 0.174 | 0.486 | 0.169 | 0.84 | 0.493 | 0.081 | 0.936 | 0.69 | 0.681 | 0.551 | 0.417 | 0.697 | 0.496 | 0.344 | 0.517 | 0.29 | 0.186 | 0.039 | 0.131 | 0.546 | 0.559 | 0.736 | 0.243 | 0.63 | 0.605 | 0.519 | 0.021 | 0.033 | 0.467 | 0.441 | 0.158 | 0.442 | 0.634 | 0.655 | 0.504 | 0.619 | 0.375 | 1.617 | 0.143 | 0.383 | 1.318 | 0.378 | 0.119 | 0.229
42 | 20.5 | 0.135 | 0.391 | 0.569 | 0.444 | 0.573 | 0.321 | 0.556 | 0.98 | 0.547 | 0.407 | 0.658 | 0.088 | 0.562 | 0.666 | 0.143 | 0.186 | 0.138 | 0.053 | 0.771 | 1.695 | 0.059 | 0.466 | 0.209 | 0.836 | 0.323 | 0.169 | 0.055 | 0.692 | 0.268 | 1.252 | 0.236 | 0.712 | 0.051 | 0.15 | 0.413 | 0.458 | 0.502 | 0.633 | 0.361 | 0.425 | 0.569 | 0.3 | 0.537 | 0.324 | 0.528 | 0.561 | 0.583 | 0.334 | 0.424 | 0.262 | 0.465 | 0.196 | 0.801 | 0.559 | 0.295 | 1.611 | 0.681 | 0.064 | 0.444 | 0.057 | 0.532 | 0.391 | 0.54 | 0.598 | 0.212 | 0.522 | 0.66 | 0.057 | 0.411 | 0.057 | 0.494 | 0.312 | 1.315 | 0.432 | 0.633 | 0.546 | 0.828 | 0.683 | 0.267 | 1.456 | 0.098 | 1.093 | 0.469 | 0.331 | 0.392 | 0.357 | 2.245 | 0.227 | 0.155 | 0.609 | 0.572 | 0.662 | 0.415 | 0.631 | 0.251 | 0.201 | 0.494 | 0.415 | 0.564 | 0.301 | 0.454 | 0.751 | 1.232 | 0.091 | 0.141 | 0.615 | 0.28 | 1.489 | 0.51 | 0.97 | 1.591 | 0.394 | 0.784 | 0.137 | 0.134 | 0.097 | 0.613 | 0.05 | 0.461 | 0.223 | 0.186 | 0.456 | 0.585 | 0.112 | 0.294 | 0.041 | 0.125 | 0.558 | 0.086 | 0.16 | 0.577 | 0.661 | 0.366 | 0.249 | 0.475 | 0.83 | 0.21 | 0.509 | 0.53 | 0.492 | 0.469 | 1.918 | 0.568 | 0.05 | 0.637 | 0.098 | 0.12 | 0.425 | 0.385 | 0.404 | 0.391 | 0.733 | 0.651 | 0.04 | 0.168 | 1.758 | 0.394 | 0.653 | 0.056 | 0.359 | 0.392 | 0.397 | 1.428 | 0.376 | 0.338 | 0.955 | 0.096 | 0.603 | 0.252 | 0.617 | 0.14 | 0.37 | 0.236 | 0.569 | 0.281 | 0.637 | 0.962 | 0.579 | 0.641 | 0.561 | 0.629 | 0.973 | 0.488 | 0.907 | 0.359 | 1.306 | 0.145 | 0.159 | 0.25 | 0.609 | 0.642 | 0.517 | 0.22 | 0.199 | 0.613 | 0.829 | 0.214 | 0.176 | 1.783 | 0.439 | 0.047 | 0.309 | 1.41 | 0.394 | 0.51 | 0.477 | 0.468 | 0.673 | 0.096 | 0.604 | 0.794 | 0.831 | 0.176 | 0.228
43 | 21 | 0.152 | 0.168 | 0.134 | 0.664 | 1.142 | 0.35 | 0.88 | 0.177 | 0.838 | 0.296 | 0.481 | 0.047 | 0.448 | 0.384 | 0.188 | 0.56 | 0.196 | 0.164 | 0.519 | 1.853 | 0.326 | 0.67 | 0.051 | 2.394 | 0.357 | 0.282 | 0.055 | 0.489 | 0.052 | 1.148 | 0.182 | 0.499 | 0.254 | 0.12 | 0.257 | 0.375 | 0.411 | 0.922 | 0.306 | 0.439 | 0.55 | 0.078 | 0.581 | 0.233 | 0.676 | 0.502 | 0.714 | 0.447 | 0.442 | 0.591 | 0.631 | 0.131 | 0.556 | 0.777 | 0.426 | 0.401 | 0.694 | 0.249 | 0.47 | 0.057 | 0.721 | 0.572 | 1.128 | 0.574 | 0.108 | 0.446 | 0.439 | 0.057 | 0.06 | 0.057 | 0.573 | 0.399 | 0.493 | 0.543 | 0.578 | 0.488 | 2.537 | 0.795 | 0.361 | 0.377 | 0.066 | 0.203 | 0.508 | 0.681 | 0.663 | 0.394 | 0.754 | 0.32 | 0.13 | 0.73 | 0.513 | 0.598 | 0.614 | 0.317 | 0.218 | 0.052 | 0.554 | 0.654 | 0.788 | 0.056 | 0.522 | 0.625 | 1.677 | 0.066 | 0.071 | 0.544 | 0.105 | 0 | 0.563 | 0.654 | 0.614 | 0.631 | 0.7 | 0.245 | 0.252 | 0.288 | 0.601 | 0.11 | 0.541 | 0.098 | 0.056 | 0.35 | 0.713 | 0.139 | 0.687 | 0.192 | 0.14 | 0 | 0.172 | 0.573 | 0.992 | 0.466 | 0.749 | 0.229 | 0.736 | 0.86 | 0.534 | 0.577 | 0.372 | 0.52 | 0.654 | 0.549 | 0.51 | 0.05 | 0.52 | 0.041 | 0.238 | 0.508 | 0.611 | 0.283 | 0.608 | 0.973 | 0.973 | 0.04 | 0.179 | 0.363 | 0.497 | 0.597 | 0.056 | 0.394 | 0.472 | 0.402 | 0.68 | 0.464 | 0.417 | 1.132 | 0.169 | 0.19 | 0.394 | 0.266 | 0.081 | 0.422 | 0.113 | 0.88 | 0.161 | 0.285 | 0.967 | 0.371 | 0.487 | 1.051 | 0.102 | 1.1 | 0.468 | 0.613 | 0.316 | 1.315 | 0.05 | 0.102 | 0.43 | 0.549 | 0.584 | 0.546 | 0.134 | 0.117 | 0.711 | 0.961 | 0.036 | 0.053 | 0.903 | 0.473 | 0.122 | 0.342 | 0.599 | 0.494 | 0.674 | 0.458 | 0.352 | 0.656 | 0.162 | 0.496 | 0.905 | 1.341 | 0.049 | 0.314
44 | 21.5 | 0.052 | 0.052 | 0.225 | 0.445 | 0.702 | 0.452 | 0.712 | 0.179 | 0.762 | 0.286 | 0.669 | 0.108 | 0.329 | 0.303 | 0.15 | 0.499 | 0.138 | 0.393 | 0.549 | 0 | 0.347 | 0.48 | 0.18 | 1.121 | 0.273 | 0.229 | 0.132 | 0.541 | 0.354 | 0.573 | 0.467 | 2.235 | 0.232 | 0.307 | 0.227 | 0.423 | 0.531 | 0.86 | 0.482 | 0.287 | 0.61 | 0.208 | 0.839 | 0.181 | 0.888 | 0.373 | 0.483 | 0.844 | 0.448 | 0.133 | 0.376 | 0.044 | 0.116 | 0.514 | 0.625 | 0.58 | 0.633 | 0.312 | 0.619 | 0.057 | 0.518 | 0.701 | 0.64 | 0.51 | 0.147 | 2.018 | 0.898 | 0.057 | 0.237 | 0.057 | 2.864 | 0.523 | 0.443 | 0.381 | 0.71 | 0.372 | 0.723 | 0.562 | 0.39 | 0.529 | 0.046 | 0.202 | 0.356 | 0.248 | 1.61 | 0.653 | 0.651 | 0.877 | 0.166 | 0.606 | 0.63 | 0.665 | 0.438 | 0.445 | 0.239 | 0.126 | 0.809 | 0.744 | 0.818 | 0.056 | 0.645 | 0.531 | 0.453 | 0.108 | 0.257 | 1.751 | 0.147 | 0 | 0.36 | 0.785 | 0.479 | 0.446 | 0.945 | 0.574 | 0.076 | 0.232 | 0.541 | 0.073 | 0.781 | 0.164 | 0.05 | 0.341 | 0.503 | 0.051 | 0.584 | 0.041 | 0.052 | 0 | 0.098 | 0.187 | 0.575 | 0.548 | 0.317 | 0.056 | 0.628 | 0.612 | 0.456 | 0.722 | 0.348 | 0.449 | 0.597 | 0.753 | 0.232 | 0.099 | 1.439 | 0.041 | 0.055 | 0.62 | 0.404 | 0.486 | 0.512 | 0.499 | 1.056 | 0.201 | 0.247 | 0 | 0.293 | 0.292 | 0.056 | 0.436 | 2.054 | 0.657 | 0.545 | 0.715 | 0.543 | 0.855 | 0.053 | 0.092 | 0.559 | 0.326 | 0.26 | 0.602 | 0.186 | 1.052 | 1.08 | 0.106 | 0.928 | 0.335 | 0.537 | 0.709 | 0.093 | 0.621 | 0.728 | 0.705 | 0.711 | 0.488 | 0.05 | 0.051 | 0.414 | 0.503 | 0.688 | 0.9 | 0.467 | 0.148 | 1.31 | 0.806 | 0.125 | 0.149 | 0.953 | 0.589 | 0.139 | 0.379 | 0.542 | 0.464 | 0.321 | 0.594 | 0.427 | 0.548 | 0.135 | 0.441 | 0.937 | 1.427 | 0.198 | 1.237
45 | 22 | 0.361 | 0.614 | 0.048 | 0.36 | 0.157 | 0.52 | 0.993 | 0.079 | 0.068 | 0.085 | 0.35 | 0.122 | 0.31 | 0.262 | 0.045 | 1.654 | 0.257 | 0.483 | 0.586 | 0 | 0.335 | 0.8 | 0.08 | 0.709 | 0.306 | 0.049 | 0.396 | 0.351 | 1.055 | 0.183 | 0.36 | 0.522 | 0.142 | 0.82 | 0.209 | 0.208 | 0.404 | 0.526 | 0.055 | 0.049 | 0.547 | 0.17 | 0.481 | 0.115 | 1.479 | 0.541 | 0.682 | 0.597 | 0.208 | 0.149 | 0.342 | 0.263 | 0 | 0.703 | 0.517 | 0.351 | 0.58 | 0.575 | 0.612 | 0.057 | 0.464 | 0.324 | 0.561 | 0.533 | 0.174 | 0.151 | 0.445 | 0.057 | 0.167 | 0.057 | 0.45 | 0.438 | 0.618 | 0.762 | 0.765 | 0.609 | 0.156 | 0.054 | 0.342 | 0.406 | 0.136 | 0.12 | 1.089 | 0.559 | 0.509 | 0.366 | 0.591 | 0.586 | 0.118 | 0.915 | 0.629 | 0.753 | 0.89 | 0.489 | 0.539 | 0.126 | 0.612 | 0.629 | 0.411 | 0.056 | 0.939 | 0.527 | 0.683 | 0.083 | 0.175 | 0 | 0.05 | 0 | 0.23 | 0.74 | 0.326 | 0.657 | 0.726 | 1.025 | 0.126 | 0.207 | 0.35 | 0.133 | 0.909 | 0.19 | 0.147 | 0.13 | 0.59 | 0.2 | 0.296 | 0.137 | 0.214 | 0 | 0.149 | 0.046 | 0.565 | 0.357 | 0 | 0.183 | 0.651 | 0.773 | 0.29 | 0.545 | 0.541 | 0.217 | 0.27 | 0 | 0.666 | 0.135 | 0.887 | 0.179 | 0.268 | 0.599 | 0.507 | 0.475 | 0.838 | 0.545 | 0.601 | 0.04 | 0.155 | 0 | 0.71 | 0.05 | 0.056 | 0.644 | 0.995 | 0.417 | 0.644 | 0.487 | 0.056 | 0.983 | 0.053 | 0.051 | 0.383 | 0.309 | 0.05 | 0.534 | 0.125 | 0.889 | 0.37 | 0.228 | 0 | 0.642 | 0.49 | 1.011 | 0.159 | 0.82 | 0.383 | 0.504 | 1.047 | 0.479 | 0.2 | 0.051 | 0.233 | 0.652 | 0.777 | 0.805 | 0.345 | 0.048 | 0.532 | 0.979 | 0.125 | 0.079 | 1.142 | 0.789 | 0.047 | 0.139 | 0.941 | 0.872 | 0.491 | 0.453 | 0.351 | 0.591 | 0.179 | 0.482 | 0 | 1.233 | 0.042 | 0.303
46 | 22.5 | 0.564 | 0.152 | 0.183 | 0.23 | 0 | 0.568 | 0.856 | 0.252 | 0.162 | 0.194 | 0.05 | 0.094 | 0.338 | 0.402 | 0.316 | 1.248 | 0.069 | 0.604 | 0.577 | 0 | 0.791 | 0.538 | 0.13 | 0.325 | 0.327 | 0.049 | 0.576 | 0.629 | 0.684 | 0 | 0.331 | 0.526 | 0.264 | 0.635 | 0.244 | 0.147 | 0.296 | 0.731 | 0.055 | 0.049 | 0.483 | 0.052 | 0.371 | 0.287 | 0.951 | 0.608 | 0.729 | 0.522 | 0.112 | 0.293 | 0.27 | 0.044 | 0 | 0.815 | 0.758 | 0.773 | 0.567 | 0.233 | 0.754 | 0.057 | 0.626 | 0.522 | 0.707 | 0.626 | 0.055 | 0.147 | 0.524 | 0.057 | 0.052 | 0.057 | 0.646 | 0.206 | 0.681 | 0.416 | 0.271 | 0.678 | 0.394 | 0.054 | 0.163 | 0.519 | 0.337 | 0.091 | 0.709 | 0.446 | 0.511 | 0.376 | 0.606 | 0.75 | 0.144 | 0.497 | 0.233 | 0.572 | 0.591 | 0.408 | 0.324 | 0.052 | 1.09 | 0.713 | 0.055 | 0.056 | 1.085 | 0.338 | 0.442 | 0.144 | 0.047 | 0 | 0.147 | 0 | 0.361 | 0.666 | 0.223 | 0.591 | 0.789 | 0.373 | 0.267 | 0.206 | 0.535 | 0.074 | 0.642 | 0.177 | 0.095 | 0.134 | 0.197 | 0.051 | 0.382 | 0.096 | 0.052 | 0 | 0.121 | 0.046 | 0.437 | 0.149 | 0 | 0.102 | 1.014 | 0.341 | 0.689 | 1.031 | 0.337 | 0.049 | 0.447 | 0 | 0.549 | 0.05 | 0.913 | 0.041 | 0.09 | 0.711 | 0.673 | 0.23 | 0.639 | 0.524 | 0.405 | 0.56 | 0.141 | 0 | 1.133 | 0.05 | 0.056 | 0.423 | 0.645 | 0.398 | 0.227 | 0.421 | 0.087 | 0.877 | 0.053 | 0.051 | 0.285 | 0.111 | 0.225 | 0.569 | 0.283 | 0.694 | 0.364 | 0.229 | 0 | 0.475 | 0.595 | 0.85 | 0.054 | 1.062 | 0.402 | 0.497 | 0.622 | 0.44 | 0.05 | 0.145 | 0.331 | 0.626 | 0.2 | 0.473 | 0.539 | 0.14 | 0.072 | 0.886 | 0.036 | 0.053 | 0.53 | 0.556 | 0.077 | 0.189 | 0.176 | 0.641 | 0.439 | 0.255 | 0.396 | 0.508 | 0.135 | 0.217 | 0 | 0 | 0.184 | 0
47 | 23 | 0.678 | 0.166 | 0.067 | 0.186 | 0 | 0.657 | 1.106 | 0.082 | 0.226 | 0.085 | 0.311 | 0.135 | 0.149 | 0.748 | 0.12 | 1.311 | 0.117 | 0.166 | 0.366 | 0 | 0.052 | 0.322 | 0.13 | 0.052 | 0.331 | 0.049 | 0.745 | 0.439 | 0.174 | 0 | 0.269 | 0.434 | 0.986 | 0.18 | 0.073 | 0.087 | 0.049 | 0.498 | 0.133 | 0.049 | 0.052 | 0.196 | 0.431 | 0.053 | 0.23 | 2 | 0.203 | 0.721 | 0.179 | 0.1 | 0.264 | 0.044 | 0 | 0.63 | 0.354 | 0.449 | 0.407 | 0.048 | 0.328 | 0.057 | 0.63 | 0.301 | 0.486 | 1.482 | 0.218 | 0.106 | 0.12 | 0.057 | 0.167 | 0.057 | 0.188 | 0.077 | 0.34 | 0.562 | 0.669 | 0.246 | 0.291 | 0.054 | 0.052 | 0.416 | 0.448 | 0.247 | 0.776 | 0.452 | 0.041 | 0.544 | 0.668 | 0.529 | 0.218 | 0.157 | 0.198 | 0.965 | 0.592 | 0.633 | 0.373 | 0.052 | 0.939 | 0.716 | 0.247 | 0.305 | 0.615 | 0 | 0.455 | 0.295 | 0.297 | 0 | 0.105 | 0 | 0.25 | 0.241 | 0.258 | 0.549 | 0 | 0 | 0.07 | 0.04 | 0.322 | 0.285 | 0.705 | 0.22 | 0.05 | 0.224 | 0.121 | 0.193 | 0.087 | 0.062 | 0.431 | 0 | 0.04 | 0.046 | 0.968 | 0.108 | 0 | 0.075 | 1.495 | 0.052 | 0.522 | 0.18 | 0.144 | 0.049 | 0.192 | 0 | 0.036 | 0.184 | 0.896 | 0.041 | 0.079 | 0.523 | 0.253 | 0.05 | 0.079 | 0.224 | 0.612 | 0.317 | 0.331 | 0 | 0.632 | 0.05 | 0.056 | 0 | 0.783 | 0.575 | 0.365 | 0.049 | 0.197 | 0.343 | 0.212 | 0.23 | 0.101 | 0.143 | 0.116 | 0.207 | 0.122 | 0.903 | 0.337 | 0.173 | 0 | 0.625 | 0.586 | 0.87 | 0.199 | 0.689 | 2.674 | 1.345 | 0.301 | 0.575 | 0.072 | 0.116 | 0.5 | 0.589 | 0.215 | 0.124 | 0.515 | 0.125 | 0.139 | 0.561 | 0.117 | 0.213 | 0.133 | 0.383 | 0.148 | 0.118 | 0.22 | 0.41 | 0.557 | 0.041 | 0.3 | 0.582 | 0.127 | 0.18 | 0 | 0 | 0.131 | 0
48 | 23.5 | 0.684 | 0.216 | 0.243 | 0.136 | 0 | 0.724 | 0.182 | 0.247 | 0.132 | 0.328 | 0.057 | 0.047 | 0.051 | 0.294 | 0.127 | 0.053 | 0.132 | 0.144 | 0.052 | 0 | 0.105 | 0.494 | 0.051 | 0 | 0.272 | 0.049 | 1.022 | 0.053 | 0.273 | 0 | 0.586 | 0.398 | 0.174 | 0.171 | 0.452 | 0.051 | 0.049 | 0.141 | 0.055 | 0.157 | 0.215 | 0.182 | 0.11 | 0.053 | 0.07 | 0.849 | 0.067 | 1.286 | 0.186 | 0.194 | 0.37 | 0.272 | 0 | 0.341 | 0.208 | 0.285 | 0.185 | 0.227 | 0 | 0.057 | 0.601 | 0.229 | 0.216 | 0.313 | 0.103 | 0.662 | 0.148 | 0.057 | 0.052 | 0.057 | 0.256 | 0.132 | 0.447 | 0.147 | 0.317 | 0.05 | 0 | 0.059 | 0.052 | 0.426 | 0.526 | 0.065 | 0.475 | 0.623 | 0.175 | 0.156 | 0.186 | 0.371 | 0.052 | 0.052 | 0.119 | 0.472 | 0.138 | 0.59 | 0.048 | 0.201 | 0.453 | 0.649 | 0.15 | 0.443 | 0.551 | 0 | 0.197 | 0.125 | 0.047 | 0 | 0.05 | 0 | 0.159 | 0.098 | 0.172 | 0.231 | 0 | 0 | 0.07 | 0.177 | 0.584 | 0.584 | 0.389 | 0.055 | 0.193 | 0.051 | 0.215 | 0.058 | 0.219 | 0.172 | 0.757 | 0 | 0.04 | 0.046 | 0.861 | 0.053 | 0 | 0.209 | 0 | 0.131 | 0.342 | 0.196 | 0.067 | 0.144 | 0.288 | 0 | 0.036 | 0.05 | 0.49 | 0.179 | 0.228 | 0.113 | 0.238 | 0.176 | 0.222 | 0.144 | 0.839 | 0.103 | 0.302 | 0 | 0.377 | 0.105 | 0.056 | 0 | 0.682 | 0.493 | 0.736 | 0.136 | 0.434 | 0 | 0.053 | 0.051 | 0.119 | 0.225 | 0.119 | 0.153 | 0.073 | 0.575 | 0.498 | 0.233 | 0 | 0.349 | 0.251 | 0.729 | 0.054 | 0.812 | 0 | 1.119 | 0.06 | 0.388 | 0.204 | 0.087 | 0.052 | 0.297 | 0.102 | 0.183 | 0.326 | 0.048 | 0 | 0.218 | 0.133 | 0.053 | 0.149 | 0.178 | 0.134 | 0.047 | 0.395 | 0.486 | 0.203 | 0.128 | 0.299 | 0.147 | 0.145 | 0.059 | 0 | 0 | 0.042 | 0

## 7. PV allocation (per period)
TR5 PV allocation — per half-hour
VIOLET = aggregated live from the raw sheets 3–6 (SUM / SUMIF). AMBER = priority split (MIN formulas): PV → prosumer load → battery → customer load → export.
period | hour (h) | PV (kW) | prosumer load (kW) | customer load (kW) | batt charge (kW) | batt discharge (kW) | batt net =chg−dis | PV→ prosumer | PV→ battery | PV→ customer | PV→ export | customer ←grid
1 | 0 | 0 | 49.0309 | 38.4642 | 0 | 48.491 | -48.491 | 0 | 0 | 0 | 0 | 38.4642
2 | 0.5 | 0 | 41.7251 | 34.2905 | 0 | 39.064 | -39.064 | 0 | 0 | 0 | 0 | 34.2905
3 | 1 | 0 | 34.2645 | 29.3959 | 0 | 31.068 | -31.068 | 0 | 0 | 0 | 0 | 29.3959
4 | 1.5 | 0 | 32.8201 | 27.8328 | 0 | 28.306 | -28.306 | 0 | 0 | 0 | 0 | 27.8328
5 | 2 | 0 | 28.1255 | 25.6442 | 0 | 25.165 | -25.165 | 0 | 0 | 0 | 0 | 25.6442
6 | 2.5 | 0 | 24.2629 | 26.2106 | 0 | 22.204 | -22.204 | 0 | 0 | 0 | 0 | 26.2106
7 | 3 | 0 | 28.3195 | 25.9671 | 0 | 26.816 | -26.816 | 0 | 0 | 0 | 0 | 25.9671
8 | 3.5 | 0.5423 | 26.7174 | 27.0733 | 0 | 23.918 | -23.918 | 0.5423 | 0 | 0 | 0 | 27.0733
9 | 4 | 7.8519 | 28.6731 | 23.5818 | 0.074 | 18.4529 | -18.3789 | 7.8519 | 0 | 0 | 0 | 23.5818
10 | 4.5 | 36.7197 | 27.6939 | 25.3155 | 13.551 | 3.855 | 9.696 | 27.6939 | 9.0258 | 0 | 0 | 25.3155
11 | 5 | 72.8314 | 25.1948 | 24.3968 | 49.093 | 1.43 | 47.663 | 25.1948 | 47.6366 | 0 | 0 | 24.3968
12 | 5.5 | 117.1238 | 27.2143 | 28.0436 | 90.231 | 0.317 | 89.914 | 27.2143 | 89.9095 | 0 | 0 | 28.0436
13 | 6 | 165.4373 | 29.7664 | 27.146 | 136.528 | 0.846 | 135.682 | 29.7664 | 135.6709 | 0 | 0 | 27.146
14 | 6.5 | 214.3524 | 31.9989 | 27.1402 | 183.498 | 1.144 | 182.354 | 31.9989 | 182.3535 | 0 | 0 | 27.1402
15 | 7 | 263.0158 | 39.4021 | 43.7893 | 224.606 | 0.99 | 223.616 | 39.4021 | 223.6137 | 0 | 0 | 43.7893
16 | 7.5 | 311.742 | 49.4352 | 44.6622 | 245.82 | 1.801 | 244.019 | 49.4352 | 244.019 | 18.2878 | 0 | 26.3744
17 | 8 | 357.4781 | 71.4731 | 56.1988 | 178.158 | 6.284 | 171.874 | 71.4731 | 171.874 | 56.1988 | 57.9322 | 0
18 | 8.5 | 400.476 | 89.5682 | 56.6794 | 101.927 | 7.948 | 93.979 | 89.5682 | 93.979 | 56.6794 | 160.2494 | 0
19 | 9 | 437.0907 | 88.0418 | 62.8276 | 68.425 | 4.544 | 63.881 | 88.0418 | 63.881 | 62.8276 | 222.3403 | 0
20 | 9.5 | 468.3204 | 88.3828 | 72.5772 | 50.508 | 5.909 | 44.599 | 88.3828 | 44.599 | 72.5772 | 262.7614 | 0
21 | 10 | 495.7275 | 87.6033 | 67.1486 | 29.587 | 6.888 | 22.699 | 87.6033 | 22.699 | 67.1486 | 318.2766 | 0
22 | 10.5 | 518.3542 | 74.0468 | 73.8219 | 29.148 | 4.955 | 24.193 | 74.0468 | 24.193 | 73.8219 | 346.2925 | 0
23 | 11 | 534.4053 | 75.0566 | 80.7739 | 24.151 | 1.22 | 22.931 | 75.0566 | 22.931 | 80.7739 | 355.6438 | 0
24 | 11.5 | 541.4481 | 71.2602 | 81.9383 | 17.691 | 1.87 | 15.821 | 71.2602 | 15.821 | 81.9383 | 372.4286 | 0
25 | 12 | 543.4846 | 90.7108 | 72.5805 | 7.879 | 0.83 | 7.049 | 90.7108 | 7.049 | 72.5805 | 373.1443 | 0
26 | 12.5 | 539.6677 | 88.3963 | 59.0206 | 5.95 | 2.772 | 3.178 | 88.3963 | 3.178 | 59.0206 | 389.0728 | 0
27 | 13 | 526.8565 | 97.7962 | 62.9153 | 5.405 | 2.811 | 2.594 | 97.7962 | 2.594 | 62.9153 | 363.551 | 0
28 | 13.5 | 507.3034 | 82.0746 | 64.3104 | 5.686 | 2.937 | 2.749 | 82.0746 | 2.749 | 64.3104 | 358.1694 | 0
29 | 14 | 483.9659 | 74.2282 | 66.0108 | 5.227 | 4.84 | 0.387 | 74.2282 | 0.387 | 66.0108 | 343.3399 | 0
30 | 14.5 | 454.3938 | 64.0548 | 60.8718 | 4.149 | 0.578 | 3.571 | 64.0548 | 3.571 | 60.8718 | 325.8962 | 0
31 | 15 | 422.9665 | 57.1949 | 61.7916 | 5.315 | 0.728 | 4.587 | 57.1949 | 4.587 | 61.7916 | 299.393 | 0
32 | 15.5 | 385.1479 | 60.0611 | 62.2149 | 3.886 | 0.473 | 3.413 | 60.0611 | 3.413 | 62.2149 | 259.4589 | 0
33 | 16 | 342.5592 | 77.4095 | 61.3645 | 3.541 | 5.35 | -1.809 | 77.4095 | 0 | 61.3645 | 203.7852 | 0
34 | 16.5 | 291.1337 | 83.3525 | 72.1707 | 4.997 | 8.61 | -3.613 | 83.3525 | 0 | 72.1707 | 135.6105 | 0
35 | 17 | 243.0012 | 85.1087 | 74.8727 | 4.959 | 13.158 | -8.199 | 85.1087 | 0 | 74.8727 | 83.0198 | 0
36 | 17.5 | 193.5442 | 105.4768 | 86.3476 | 3.349 | 32.402 | -29.053 | 105.4768 | 0 | 86.3476 | 1.7198 | 0
37 | 18 | 145.7065 | 86.1861 | 87.7474 | 7.806 | 25.63 | -17.824 | 86.1861 | 0 | 59.5204 | 0 | 28.227
38 | 18.5 | 99.5836 | 83.4958 | 79.6544 | 5.13 | 28.65 | -23.52 | 83.4958 | 0 | 16.0878 | 0 | 63.5666
39 | 19 | 58.1471 | 84.2011 | 80.0919 | 1.913 | 40.004 | -38.091 | 58.1471 | 0 | 0 | 0 | 80.0919
40 | 19.5 | 16.9242 | 94.7603 | 90.9889 | 0.01 | 78.361 | -78.351 | 16.9242 | 0 | 0 | 0 | 90.9889
41 | 20 | 3.1239 | 97.7223 | 96.8479 | 0 | 94.604 | -94.604 | 3.1239 | 0 | 0 | 0 | 96.8479
42 | 20.5 | 0 | 107.6506 | 104.0495 | 0 | 106.876 | -106.876 | 0 | 0 | 0 | 0 | 104.0495
43 | 21 | 0 | 105.7056 | 102.6549 | 0 | 101.094 | -101.094 | 0 | 0 | 0 | 0 | 102.6549
44 | 21.5 | 0 | 111.7599 | 102.5327 | 0 | 104.6 | -104.6 | 0 | 0 | 0 | 0 | 102.5327
45 | 22 | 0 | 99.2192 | 95.3542 | 0 | 88.26 | -88.26 | 0 | 0 | 0 | 0 | 95.3542
46 | 22.5 | 0 | 86.6616 | 80.6818 | 0 | 77.262 | -77.262 | 0 | 0 | 0 | 0 | 80.6818
47 | 23 | 0 | 77.5417 | 69.4409 | 0 | 67.538 | -67.538 | 0 | 0 | 0 | 0 | 69.4409
48 | 23.5 | 0 | 59.3887 | 54.099 | 0 | 47.473 | -47.473 | 0 | 0 | 0 | 0 | 54.099
TOTAL | kWh/day | 5100.2134 | 1615.1173 | 1439.7673 | 759.099 | 624.6634 | 134.4355 | 1049.137 | 709.867 | 725.1666 | 2616.0428 | 714.6007
Each half-hour is 0.5 h, so daily energy (kWh) = Σ(power in kW) × 0.5.
Trace any input: e.g. cell C5 = SUM of column C on sheet 3 (PV of all 417 connections at 00:00). Click it to see the formula.

## 8. Results & charts
TR5 PV allocation — results
Where the day's PV goes |  |  | How the customers (203) are supplied
Destination | kWh/day | % of PV | Source | kWh/day | % of cust. load
PV → prosumers' own load | 1049.137 | 20.57% | From prosumer PV (day) | 725.1666 | 50.37%
PV → battery storage | 709.867 | 13.92% | From grid import (night) | 714.6007 | 49.63%
PV → customers | 725.1666 | 14.22% | TOTAL customer load | 1439.7673 | 100%
PV → export to grid | 2616.0428 | 51.29%
TOTAL (= PV) | 5100.2134 | 100%
Charts read live from sheet 7, which reads live from raw sheets 3–6.